| NPRR Number | 1144 | NPRR Title | Station Service Backup Power Metering |
| --- | --- | --- | --- |
| Date of Decision |  | January 24, 2023 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | April 1, 2023 |  |
| Priority and Rank Assigned |  | Not Applicable |  |
| Nodal Protocol Sections Requiring Revision |  | 10.3.2.3, Generation Netting for ERCOT-Polled Settlement Meters |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) provides a limited exception to the requirement that all Loads included in the netting arrangement for an ERCOT-Polled Settlement (EPS) Metering Facility only be connected to the ERCOT Transmission Grid through the EPS metering point(s) for the Facility. The exception allows no more than 500kW of auxiliary Load connected to a station service transformer to be connected to a Transmission Service Provider’s (TSP’s) or Distribution Service Provider’s (DSP’s) Facilities through a separately metered point using an open transition Load transfer switch listed for emergency use. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | - Allowing the relatively insignificant Load of backup station service in emergency and maintenance situations to be provided and metered by the DSP and/or alternate connection to the TSP would allow generators to eliminate the need for an on-site backup generator which has initial high costs and continued maintenance costs. It also requires a fuel source that would likely require further local permitting. Eliminating fuel storage also makes the site inherently safer. A meter that has the capability to function as an EPS Meter is also not a standard meter for most local distribution companies and the requirement of an EPS Meter would mean additional infrastructure to support the backup service. |  |
| PRS Decision |  | On 8/11/22, PRS voted unanimously to table NPRR1144 and refer the issue to WMS. All Market Segments participated in the vote. On 11/11/22, PRS voted to recommend approval of NPRR1144 as amended by the 8/29/22 Joint Commenters comments. There were three abstentions from the Consumer (Occidental), Cooperative (LCRA), and Investor Owned Utility (IOU) (CNP) Market Segments. All Market Segments participated in the vote. On 12/8/22, PRS voted to endorse and forward to TAC the 11/11/22 PRS Report and 11/22/22 Impact Analysis for NPRR1144. There was one abstention from the IOU (CNP) Market Segment. All Market Segments participated in the vote. |  |
| Summary of PRS Discussion |  | On 8/11/22, Plus Power revoked its request for Urgent status and requested that NPRR1144 be tabled in anticipation of further discussion at the August 25, 2022 Metering Working Group (MWG) meeting and pending comments. On 11/11/22, participants expressed that their abstentions for NPRR1144 were due to its conflict with company service standards. On 12/8/22, participants reviewed NPRR1144’s 11/22/22 Impact Analysis. |  |
| TAC Decision |  | On 1/24/23, TAC voted to recommend approval of NPRR1144 as recommended by PRS in the 12/8/22 PRS Report. There was one abstention from the IOU (CNP) Market Segment. All Market Segments participated in the vote. |  |
| Summary of TAC Discussion |  | On 1/24/23, TAC reviewed the ERCOT Opinion, ERCOT Market Impact Statement, and Independent Market Monitor (IMM) Opinion for NPRR1144. |  |

| Opinions |  |
| --- | --- |
| Credit Review | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR1144 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |
| Independent Market Monitor Opinion | IMM has no opinion on NPRR1144. |
| ERCOT Opinion | ERCOT supports approval of NPRR1144. |
| ERCOT Market Impact Statement | ERCOT Staff has reviewed NPRR1144 and believes NPRR1144 provides a defined and limited exception to EPS metering requirements for generation site auxiliary Loads, not exceeding 500kW, to be isolated and connected to an alternate feed through a TDSP read metering point. |

| - Sponsor |  |
| --- | --- |
| - Name | - Ravi Beeravalli |
| - E-mail Address | - rbeeravalli@pluspower.com |
| - Company | - Plus Power |
| - Phone Number | - 218-387-4538 |
| - Market Segment | - Not Applicable |

| - Market Rules Staff Contact |  |
| --- | --- |
| - Name | - Jordan Troublefield |
| - E-Mail Address | - Jordan.Troublefield@ercot.com |
| - Phone Number | - 512-248-6521 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 080422 | Expressed confusion regarding NPRR1144’s intent and suggested that additional guidance may be required in regard to how DSPs, TSPs, and Resources will be electrically connected; ERCOT also recommended that NPRR1144 be discussed at the August 25, 2022 MWG Meeting |
| Joint Commenters 081722 | Proposed alternative language to clarify that NPRR1144 is not intended to change or impact the metering requirements or determination of Wholesale Storage Load (WSL) |
| Joint Commenters 082922 | Proposed a requirement in paragraph (6) that the Resource Entity provide notice of the proposed connection to all DSPs that are certificated to serve the area in which the backup connection is proposed |
| WMS 091422 | Requested PRS continue to table NPRR1144 |
| WMS 110922 | Endorsed NPRR1144 as amended by the 8/29/22 Joint Commenters comments |

Market Rules Notes

None

Proposed Protocol Language Revision

- 10.3.2.3	Generation Netting for ERCOT-Polled Settlement Meters

(1)	Each Generation Resource and Settlement Only Generator (SOG) and each Load that is designated to be netted with that Generation Resource or SOG, including construction and maintenance Load that is netted with existing generation auxiliaries, must be physically metered at its POI to the ERCOT Transmission Grid or Service Delivery Point, or, in accordance with Section 10.3.2.2, Loss Compensation of EPS Meter Data, loss-compensated to its POI to the ERCOT Transmission Grid.  Interval Data Recorders (IDRs) must be used to determine generator output or Load usage.  In the intervals where the generation output exceeds the Load, the net must be settled as generation.  In the intervals where the Load exceeds the generation output, the net must be settled as Load, and carry any applicable Load shared charges and credits.

(2)	For Settlement purposes, netting is not allowed except under the configurations described in paragraphs (2)(a) through (2)(e) below, and only if the service arrangement is otherwise lawful.  ERCOT has no obligation to independently determine whether a site configuration that includes both Loads and Generation Resource(s) or SOGs complies with Public Utility Regulatory Act (PURA) or the Public Utility Commission of Texas (PUCT) Substantive Rules, and ERCOT’s approval of a metering proposal for such a site is not a verification of the legality of that arrangement:

(a)	Single POI or Service Delivery Point;

(b)	Transmission-level interconnections where all POIs are located at the same substation, at the same voltage, and under normal operating conditions, are interconnected through common electrical equipment such as circuit breakers, connecting cables, bus bars, switches/isolators.  Qualifying station arrangements include, but are not limited to, Generation and Load connected in a line bus, ring bus, double-breaker, or breaker-and-a-half configuration;

(c)	Multiple POIs where the Loads and generator output are electrically connected to a common switchyard, as defined in paragraph (7) below.  In addition, there must be sufficient generator capacity to serve all plant Loads for netting to occur;

(d)	A Qualifying Facility (QF) with POIs, where the QF is selling energy to a thermal host, may net the Load meters of the thermal host with the QF’s generation meters when the Load and generation are electrically connected to a common switchyard.  In instances in which Load is served by new on-site generation through a common switchyard, the TSP or DSP may install monitoring equipment necessary for measuring Load to determine stranded cost charges, if any are applicable, as determined under the PURA and applicable PUCT rules.  For purposes of this Section, new on-site generation has the meaning as contained in Public Utility Regulatory Act, Tex. Util. Code Ann. §§ 39.252 and 39.262(k) (Vernon 1998 & Supp. 2007) (PURA); or

(e)	For Generation Resources and/or Load with flow-through on a private, contiguous transmission system (not included in a TSP or DSP rate base) and in a configuration existing as of October 1, 2000, the meters at the interconnections with the ERCOT Transmission Grid may be netted for the purpose of determining Generation Resources or Load.  For Settlement purposes, when the net is a Load, the metered interconnection points must be assigned to the same Load Zone and Unaccounted for Energy (UFE) zone.

(3)	For Energy Storage Resource (ESR) sites, Wholesale Storage Load (WSL) must be separately metered from all other Loads and generation, and must be metered using EPS Metering Facilities.

(a)	For configurations where the Resource Entity telemeters an auxiliary Load value to the EPS Meter:

(i)	The total energy into the ESR must be separately metered from all other Loads and generation, and must be metered using EPS Metering Facilities; and

(ii)	The auxiliary Load energy shall be stored in the EPS Meter’s IDR, per channel assignments defined in the SMOG.

(b)	For configurations where the WSL is not at a POI, it must be metered behind a single POI metering point, per the requirements in paragraph (3) or (3)(a) above; and

(c)	WSL for a compressed air energy storage Load Resource is exempt from the requirement to be electrically connected to a common switchyard, as defined in paragraph (7) below.

[NPRR995: Replace paragraph (3) above with the following upon system implementation:] (3) For Energy Storage Resource (ESR), Settlement Only Distribution Energy Storage System (SODESS), or Settlement Only Transmission Energy Storage System (SOTESS) sites, Wholesale Storage Load (WSL) must be separately metered from all other Loads and generation, and must be metered using EPS Metering Facilities. (a) For configurations where the Resource Entity telemeters an auxiliary Load value to the EPS Meter: (i) The total energy into the ESR, SODESS, or SOTESS must be separately metered from all other Loads and generation, and must be metered using EPS Metering Facilities; and (ii) The auxiliary Load energy shall be stored in the EPS Meter’s IDR, per channel assignments defined in the SMOG. (b) For configurations where the WSL is not at a POI, it must be metered behind a single POI metering point, per the requirements in paragraph (3) or (3)(a) above; and (c) WSL for a compressed air energy storage Load Resource is exempt from the requirement to be electrically connected to a common switchyard, as defined in paragraph (7) below.

(4)	ERCOT shall maintain descriptions of the Metering Facilities of all common switchyards that contain multiple POIs of Loads (ESI IDs) and generation meters (EPS).  The description is limited to identifying the Entities within a common switchyard and a simplified diagram showing the metering configuration of all Supervisory Control and Data Acquisition (SCADA) and Settlement Metering points.

(5)	All Load(s) included in the netting arrangement for an EPS Metering Facility shall only be electrically connected to the ERCOT Transmission Grid through the EPS metering point(s) for such Facility.  Such Loads shall not be electrically connected to the ERCOT Transmission Grid through electrical connections that are not metered by the EPS metering point(s) for the Facility.

(6)	Notwithstanding the requirements of paragraph (5) above, auxiliary Load(s) connected to the station service transformer not to exceed 500 kW in aggregate shall be permitted an additional electrical connection to a TSP’s or DSP’s Facilities through a separately metered Transmission and/or Distribution Service Provider (TDSP) read metering point.  In locations subject to multiple certificated service areas, the Resource Entity shall notify each DSP that has the right to serve in the service area of the proposed connection.  This configuration requires mutual agreement between the connecting TSP, DSP, and Resource Entity, and the connection shall be achieved through an open transition load transfer switch listed for emergency service and shall only be used in emergency and maintenance situations.

(7)	For purposes of this Section, a common switchyard is defined as an electric substation Facility where the POI for Load and Generation Resources are located at the same Facility but where the interconnection points are physically not greater than 400 yards apart.  The physical connections of the Load to its POI and the Generation Resource to its POI cannot be Facilities that have been placed in a TSP’s or DSP’s rate base.

(8)	Notwithstanding any other provision in this Section, for any Generation Resource or ESR that is configured to serve a Customer Load as part of a Private Microgrid Island (PMI), the connection to the Customer Load in the PMI configuration shall be located behind the EPS metering point at the Resource’s POI.  For a PMI configuration that includes an ESR that is receiving WSL treatment for charging Load, an EPS Meter shall be located to measure the ESR’s gross output net of any internal telemetered auxiliary Load, and a separate TDSP ESI ID (for nodal Settlement) with a Load Serving Entity (LSE) association must be established for the site prior to service of any Load.

[NPRR945: Insert paragraph (9) below upon system implementation:] (9) ERCOT shall post on the ERCOT website a report listing all Generation Resources or Settlement Only Generators (SOGs) that have achieved commercial operations, excluding Decommissioned Generation Resources, Mothballed Generation Resources, and decommissioned SOGs, whose Resource Registration data indicates that the Generation Resource or SOG is part of a Private Use Network. The report must identify the name of the Generation Resource or SOG site, its nameplate capacity, and the date the Generation Resource or SOG was added to the report. The report shall not identify any confidential, customer-specific information regarding netted loads. ERCOT shall update the list at least monthly.