## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS
Vice Chair: Vacant
ROS
March 2nd, 2023

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs and IMFR
    2 FMEs in the month of Jan
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 2/15/2023
  Spring/Summer Implementation Refresher – Including ECRS
  ERCOT Reports
  TRE Report

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 2 FMEs in January
  1/2/2023 04:35:53
    Reduction of 537 MW of load
    Interconnection Frequency Response: 1,041 MW/0.1 Hz
    288 Resources were evaluated. These includes,
      253 Generation Resources
      0 Controllable Load Resources
      35 Energy Storage Resources
    138 of 288 Evaluated Resources had less than 75% of their expected Initial Primary Frequency Response.
    118 of 288 Evaluated Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  1/24/2023 14:27:10
    Loss of 966 MW of generation
    Interconnection Frequency Response: 1,725 MW/0.1 Hz
    117 Resources were evaluated. These includes,
      60 Generation Resources
      1 Controllable Load Resource
      56 Energy Storage Resources
    14 of 117 Evaluated Resources had less than 75% of their expected Initial Primary Frequency Response.
    10 of 117 Evaluated Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 463 MW/0.1 Hz
IMFR Performance currently
1468.17 MW/0.1HZ

## Slide 8
Questions?

## Slide 9: Frequency Control Report
Jan 2023

## Slide 10: CPS1 Performance

## Slide 11: RMS1 Performance of ERCOT Frequency
Notes: 14.46Mhz on avg for Jan 2023

## Slide 12: Frequency Profile Analysis

## Slide 13: Time Error Corrections

## Slide 14: ERCOT Total Energy
Notes: 32,277,477 MWh

## Slide 15: ERCOT Total Energy from Wind Generation
Notes:   10,909,355 MWH

## Slide 16: ERCOT % Energy from Wind Generation
Notes: 33.80%
of total energy was provided by wind generation

## Slide 17: ERCOT Total Energy from Solar Generation
Notes: 1,516,586 MWh

## Slide 18: ERCOT % Energy from Solar Generation
Notes: 4.70%

## Slide 19: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia =135,268 MW*s on 1/15/2023
Absolute Minimum remains 109,029 MW*s on 3/22/2021
Data:
Mean: 178,997 MW*s
Max: 348,505 MW*s on Jan 31st
Min: 135,268 MW*s on Jan 15th

## Slide 20: ERCOT Inertia Trend
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.