## Summary
Release Date: March 8, 2023
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Spring 2023
SUMMARY
Assuming that the ERCOT Region experiences typical spring grid conditions, ERCOT anticipates that there will be sufficient installed generating capacity available to serve the system-wide forecasted peak demand for the upcoming spring season, March - May 2023.
The forecasted April and May peak demands are 59,505 MW and 69,921 MW, respectively. These forecasts are based on average weather conditions at the time of the spring peaks for years 2007 through 2021. This report does not contain a weather forecast for the spring season. The forecasts also incorporate expected load increases during the peak demand hour due to interconnection of Large Loads (such as crypto-mining facilities) to Transmission Service Provider networks.
Almost 99,800 MW of spring-rated resource capacity is expected to be available for the spring peak demand. One thermal generation resource—a coal-fired unit with a 610 MW spring rating—is out of service for the duration of the spring season. Also, a gas-fired unit with a spring capacity rating of 568 MW has changed its operating period to summer-only. The total resource amount also includes 844 MW of battery storage capability assumed to be available for dispatch prior to the highest spring net load hours. (Net load is total load minus wind and solar generation, and represents the demand that must be met with other available resources.) This capacity estimate serves as a proxy for the amount expected during a tight reserve hour for the upcoming spring and is an interim availability assumption to be used until a formal capacity contribution method is adopted for future SARA reports.
This report also identifies the aggregate amount of installed generation capacity where Large Loads, such as crypto-mining facilities, are directly interconnected, and the expected peak reduction in available generation capacity attributable to these loads during spring hours with the highest risk of insufficient reserve capacity. The background tab includes a detailed description of the methodology used to estimate the expected generator capacity reductions.
The spring SARA includes a typical thermal generating unit outage assumption of 19,536 MW for the spring generator maintenance window (March-April) and 15,979 MW at the time of the forecasted spring peak load in May. These outage assumptions are based on historical outage data for the last three spring seasons excluding 2021 (2019, 2020, 2022). Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages that extended into the spring season.
The spring SARA includes two Risk Scenario tabs: Base & Moderate Risk Scenarios, and Extreme Risk Scenarios. The most severe Risk Scenario assumes a forecasted May peak load with extreme unplanned thermal plant outages based on historic observations, combined with extreme low wind power production.

## Forecasted Capacity
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2023
Release Date: March 8, 2023
Installed and Spring Capacity Ratings, MW
| Resources, MW | Installed Capacity Rating 1/ | Expected Capacity for Spring Peak Demand
| Thermal Resources, Installed Spring-rated Capacity | 70022.13 | 63431.18 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
| Hydroelectric, Peak Average Capacity Contribution | 563.3 | 437.4037 | Based on 77% of installed capacity for hydro resources (Spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Switchable Capacity Total | 3840.12 | 3691 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
| Less Switchable Capacity Unavailable to ERCOT | -572.12 | -558 | Based on survey responses of Switchable Resource owners
| Available Mothballed Capacity | 126 | 118 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
| Capacity from Private Use Networks | 9575 | 3013 | Average grid injection during the top 20 Spring peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocols Section 10.3.2.4.
| Operational Co-located Resources with Large Flexible Loads (LFLs) | 3074.45 | 1559.1 | Forecasted capacity of generation units with a co-located large load at the site. The methodology for calculating the capacity contribution is outlined on the Background tab.
| Coastal Wind, Peak Average Capacity Contribution | 5436.37 | 3475.296 | Based on 64% of installed capacity for coastal wind resources (Spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Panhandle Wind, Peak Average Capacity Contribution | 4247.23 | 1655.238 | Based on 39% of installed capacity for panhandle wind resources (Spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Other Wind, Peak Average Capacity Contribution | 27439.49 | 10699.8957 | Based on 39% of installed capacity for other wind resources (Spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Solar Utility-Scale, Peak Average Capacity Contribution | 14964.51 | 10687.1472 | Based on 72% of rated capacity for solar resources (Spring season) per Nodal Protocols Section 3.2.6.2.2
| Storage, Peak Average Capacity Contribution | 3013.31 | 844 | Based on the amount of battery storage capability assumed to be available for dispatch prior to the highest spring net load hours. (Net load is total load minus wind and solar generation, and represents the demand that must be met with other available resources. This is an interim availability assumption for use until a formal capacity contribution method is adopted for future SARA reports
| RMR Capacity to be under Contract | 0 | 0
| Capacity Pending Retirement | 0 | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocols Section 3.14.1.2
| Non-Synchronous Ties, Capacity Contribution | 1220 | 719.8 | Based on net imports during Winter 2020/2021 (Winter Storm Uri) Energy Emergency Alert (EEA) intervals
| Planned Thermal Resources with Signed IA, Air Permits and Adequate Water Supplies | 0 | 0 | Based on in-service dates provided by developers
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 64% Spring capacity contribution for coastal wind resources
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 39% Spring capacity contribution for panhandle wind resources
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 39% Spring capacity contribution for other wind resources
| Planned Solar Utility-Scale, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 72% Spring capacity contribution for solar resources
| Planned Storage, Peak Average Capacity Contribution | 0 | 0 | Installed capacity based on in-service dates provided by developers. The capacity contribution is considered to be incorporated with the 947 MW aggregate contribution value reported in the operational Storage line item
[a] Total Resources, MW |  | 142949.79 | 99773.0606
1/ Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer.

## Base & Moderate Risk Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2023
Release Date: March 8, 2023
Base & Moderate Reserve Capacity Risk Scenarios, MW
Spring Maintenance Season, March - April
| Forecasted April Peak Load / Typical Unplanned Outages / Typical Wind and Solar | High April Peak Load / Typical Unplanned Outages / Typical Wind and Solar | Forecasted April Peak Load / High Unplanned Outages / Typical Wind and Solar | Forecasted April Peak Load / Typical Unplanned Outages / Low Wind and Solar
Scenario Assumptions
[a] Peak Load Forecast (Baseline) | 59943 | 59943 | 59943 | 59943
[b] Rooftop PV Forecast Reduction, MW | -438 | -438 | -438 | -438
[c] Adjusted Peak Load Forecast, [a+b] | 59505 | 59505 | 59505 | 59505
[d] Total Resources (from Forecast Capacity tab) | 99773.0606 | 99773.0606 | 99773.0606 | 99773.0606
Uses of Reserve Capacity
Peak Load Increase, High | 0 | 9216 | 0 | 0
Typical Planned Outages, Thermal | 5931 | 5931 | 5931 | 5931
Typical Unplanned Outages, Thermal | 13605 | 13605 | 13605 | 13605
High Unplanned Outage Adjustment, Thermal | 0 | 0 | 4941 | 0
Low Wind Output Reduction to 5,277 MW | 0 | 0 | 0 | 10553.4297
Low Solar Output Reduction to 5,123 MW | 0 | 0 | 0 | 5564.1472
[e] Total Uses of Reserve Capacity | 19536 | 28752 | 24477 | 35653.5769
Capacity Available For Operating Reserves
[f] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d-f), MW | 20732.0606 | 11516.0606 | 15791.0606 | 4614.4837
Less than 2,300 MW indicates risk of EEA1
[g] Pre-EEA Resources available for ERCOT deployment (Emergency Response Service, distribution voltage reduction, LFL curtailment) | 0 | 0 | 0 | 0
[h] EEA Resources available for ERCOT deployment | 0 | 0 | 0 | 0
[i] Capacity Available for Operating Reserves, Emergency Conditions (f+g+h), MW | 20732.0606 | 11516.0606 | 15791.0606 | 4614.4837
Less than 1,000 MW indicates risk of EEA3 Load Shed
Spring Peak Load Month, May
| Forecasted May Peak Load / Typical Unplanned Outages / Typical Wind and Solar | High May Peak Load / Typical Unplanned Outages / Typical Wind and Solar | Forecasted May Peak Load / High Unplanned Outages / Typical Wind and Solar | Forecasted May Peak Load / Typical Unplanned Outages / Low Wind and Solar
Scenario Assumptions
[a] Peak Load Forecast (Baseline) | 70459 | 70459 | 70459 | 70459
[b] Rooftop PV Forecast Reduction, MW | -538 | -538 | -538 | -538
[c] Adjusted Peak Load Forecast, [a+b] | 69921 | 69921 | 69921 | 69921
[d] Total Resources (from Forecast Capacity tab) | 99773.0606 | 99773.0606 | 99773.0606 | 99773.0606
Uses of Reserve Capacity
Peak Load Increase, High | 0 | 7263 | 0 | 0
Typical Planned Outages, Thermal | 2374 | 2374 | 2374 | 2374
Typical Unplanned Outages, Thermal | 13605 | 13605 | 13605 | 13605
High Unplanned Outage Adjustment, Thermal | 0 | 0 | 4941 | 0
Low Wind Output Adjustment to 4,735 MW | 0 | 0 | 0 | 11095.4297
Low Solar Output Adjustment to 8,036 MW | 0 | 0 | 0 | 2651.1472
[e] Total Uses of Reserve Capacity | 15979 | 23242 | 20920 | 29725.5769
Capacity Available For Operating Reserves
[f] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d-f), MW | 13873.0606 | 6610.0606 | 8932.0606 | 126.4837
Less than 2,300 MW indicates risk of EEA1
[g] Pre-EEA Resources available for ERCOT deployment (Emergency Response Service, distribution voltage reduction, LFL curtailment) | 0 | 0 | 0 | 2115
[h] EEA Resources available for ERCOT deployment | 0 | 0 | 0 | 1377
[i] Capacity Available for Operating Reserves, Emergency Conditions (f+g+h), MW | 13873.0606 | 6610.0606 | 8932.0606 | 3618.4837
Less than 1,000 MW indicates risk of EEA3 Load Shed

## Extreme Risk Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2023
Release Date: March 8, 2023
Extreme Reserve Capacity Risk Scenarios, MW (One or a combination of extreme risk assumptions resulting in low probability, high impact outcomes)
Spring Maintenance Season, March - April
| Extreme April Peak Load / Typical Unplanned Outages / Typical Renewable Output | Extreme April Peak Load / Extreme Unplanned Outages / Typical Renewable Output | Forecasted April Peak Load / Extreme Unplanned Outages / Extreme Low Wind Output
Scenario Assumptions
[a] Peak Load Forecast (Baseline) | 59943 | 59943 | 59943
[b] Rooftop PV Forecast Reduction, MW | -438 | -438 | -438
[c] Adjusted Peak Load Forecast, [a+b] | 59505 | 59505 | 59505
[d] Total Resources (from Forecast Capacity tab) | 99773.0606 | 99773.0606 | 99773.0606
Uses of Reserve Capacity
April Extreme Load Increase | 15696 | 15696 | 0
Typical Planned Outages, Thermal | 5931 | 5931 | 5931
Typical Unplanned Outages, Thermal | 13605 | 13605 | 13605
Extreme Unplanned Outage Adjustment, Thermal | 0 | 7396 | 7396
Extreme Low Wind Output Adjustment to 107 MW | 0 | 0 | 15723.4297
[e] Total Uses of Reserve Capacity | 35232 | 42628 | 42655.4297
Capacity Available For Operating Reserves
[f] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d-f), MW | 5036.0606 | -2359.9394 | -2387.3691
Less than 2,300 MW indicates risk of EEA1
[g] Pre-EEA Resources available for ERCOT deployment (Emergency Response Service, distribution voltage reduction, LFL curtailment) | 0 | 2115 | 2115
[h] EEA Resources available for ERCOT deployment | 0 | 1377 | 1377
[i] Capacity Available for Operating Reserves, Emergency Conditions (f+g+h), MW | 5036.0606 | 1132.0606 | 1104.6309
Less than 1,000 MW indicates risk of EEA3 Load Shed
Spring Peak Load Month, May
| Extreme May Peak Load / Typical Unplanned Outages / Typical Wind and Solar | Extreme May Peak Load / Extreme Unplanned Outages / Typical Wind and Solar | Forecasted May Peak Load / Extreme Unplanned Outages / Extreme Low Wind
Scenario Assumptions
[a] Peak Load Forecast (Baseline) | 70459 | 70459 | 70459
[b] Rooftop PV Forecast Reduction, MW | -538 | -538 | -538
[c] Adjusted Peak Load Forecast, [a]+[b] | 69921 | 69921 | 69921
[d] Total Resources (from Forecast Capacity tab) | 99773.0606 | 99773.0606 | 99773.0606
Uses of Reserve Capacity
May Extreme Load Increase | 13128 | 13128 | 0
Typical Planned Outages, Thermal | 2374 | 2374 | 2374
Typical Unplanned Outages, Thermal | 13605 | 13605 | 13605
Extreme Unplanned Outage Adjustment, Thermal | 0 | 7396 | 7396
Extreme Low Wind Output Adjustment to 364 MW | 0 | 0 | 15466.4297
[e] Total Uses of Reserve Capacity | 29107 | 36503 | 38841.4297
Capacity Available For Operating Reserves
[f] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d-f), MW | 745.0606 | -6650.9394 | -8989.3691
Less than 2,300 MW indicates risk of EEA1
[g] Pre-EEA Resources available for ERCOT deployment (Emergency Response Service, distribution voltage reduction, LFL curtailment) | 2115 | 2115 | 2115
[h] EEA Resources available for ERCOT deployment | 0 | 1377 | 1377
[i] Capacity Available for Operating Reserves, Emergency Conditions (f+g+h), MW | 2860.0606 | -3158.9394 | -5497.3691
Less than 1,000 MW indicates risk of EEA3 Load Shed

## Planning Reserve Margins
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2023
Release Date: March 8, 2023
Planning Reserve Margins
|  | March-April | May
| Peak Demand Forecast, MW | 59943 | 70459
| Rooftop PV Forecast Reduction, MW | -438 | -538
| Adjusted Peak Load Forecast, MW | 59505 | 69921
| Total Resources, MW | 99773.0606 | 99773.0606
| Emergency Resources Deployed by ERCOT, MW 1 | 3492 | 3492
| Planning Reserve Margin 2 | 78.12% | 50.2%
Formula: PRM = ((Total Resources / (Adjusted Peak Demand - Emergency Resources)) - 1, expressed as a percentage
1 The derivation of the emergency resource amount is described in the Scenario Assumptions Details tab.
2 The Planning Reserve Margin (PRM) is the forecasted capacity reserve that can cover higher-than-expected peak demand and lower-than-expected resource availability when looking at months or longer in the future. This is in contrast to operating reserve measures that focus on actual available capacity during real-time and hour-ahead operating periods. Consequently, the PRM is not an appropriate measure of capacity reserves when operations timeframes are being considered.

## SpringCapacities
Unit Megawatt Capacities - Spring
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | INSTALLED CAPACITY RATING | SPRING CAPACITY (MW) | NEW PLANNED PROJECT ADDITIONS TO REPORT
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1269 | 1227
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1269 | 1214
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1365 | 1323.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1365 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 650 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 615 | 608
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 615 | 608
11 | FAYETTE POWER U2 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 460 | 448
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 555 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 922 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 893 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 956.8 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 893 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 893 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 893 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 916.8 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 916.8 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 430 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 1008 | 932.61
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 174.6 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 174.6 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 734.1 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 734.1 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 614.6 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 653.99 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 164
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 164
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 222 | 190
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 21 | 19
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
35 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 352.8 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 351 | 322
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 178
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 178
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 242 | 236
40 | BEACHWOOD POWER STATION U1 |  | BCH_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.1
41 | BEACHWOOD POWER STATION U2 |  | BCH_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.1
42 | BEACHWOOD POWER STATION U3 |  | BCH_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.1
43 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 161.83
44 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 161.83
45 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 188.7 | 160.58
46 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 94.95 | 83.56
47 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 254.15 | 222.39
48 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 169
49 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 169
50 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 275.57 | 270
51 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-CC | WEST | 1987 | 75 | 75
52 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-CC | WEST | 1987 | 75 | 75
53 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 62 | 62
54 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 46.7
55 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 46.7
56 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 46.7
57 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 46.7
58 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 168
59 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 168
60 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 182
61 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 765 | 745
62 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 765 | 749
63 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 83.2
64 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 76.2
65 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 83.6
66 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 77.1
67 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 105 | 103.7
68 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 108.8 | 107.9
69 | COLORADO BEND II CTG 7 |  | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 332.08
70 | COLORADO BEND II CTG 8 |  | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 337.8
71 | COLORADO BEND II STG 9 |  | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 508.5 | 482.27
72 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 181
73 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 178
74 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 178
75 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2002 | 150 | 144
76 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 48 | 46.5
77 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 50 | 48.5
78 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 120 | 108.5
79 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 50
80 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 50
81 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 50
82 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 50
83 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 71
84 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 70
85 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 70
86 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 71
87 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 190
88 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 202
89 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 190
90 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 202
91 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 199 | 174
92 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 274.5 | 290
93 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
94 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
95 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
96 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
97 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 153.58
98 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 153.58
99 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 202 | 195
100 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 209
101 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 140 | 116
102 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36
103 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36
104 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36
105 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36
106 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 176
107 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 176
108 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 204 | 189
109 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 167
110 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 159
111 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 159
112 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 167
113 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 159
114 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 159
115 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 408
116 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 408
117 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 156.2
118 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 156.2
119 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 156.46
120 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 156.46
121 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 178.03
122 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 177.11
123 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 129 | 119
124 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 225 | 239
125 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 387 | 390
126 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 57
127 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 57
128 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 57
129 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 50
130 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 57
131 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 57
132 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
133 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
134 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
135 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 152
136 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 151
137 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 100 | 75
138 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
139 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
140 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
141 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
142 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 200
143 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 200
144 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395 | 375
145 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435 | 435
146 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435 | 435
147 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 213
148 | HAYS ENERGY FACILITY CSG 2 | 21INR0527 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 214
149 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 213
150 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 216
151 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 143
152 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 143
153 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 198.05 | 172
154 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150
155 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150
156 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 165
157 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 165
158 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 320.6 | 275
159 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 320.6 | 294
160 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 185 | 163
161 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 107 | 106
162 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 397 | 392
163 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 531 | 523
164 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 161
165 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153
166 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153
167 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 161
168 | LAMAR ENERGY CENTER STG 1 | 23INR0486 | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
169 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
170 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 92.9
171 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 90.1
172 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
173 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
174 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
175 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
176 | LIGNIN (CHAMON 2) U1 |  | LIG_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 42.5
177 | LIGNIN (CHAMON 2) U2 |  | LIG_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 42.5
178 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 183
179 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 175
180 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 204 | 192
181 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 213.64
182 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 213.64
183 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 258.4 | 255.45
184 | MIDLOTHIAN ENERGY FACILITY CTG 1 | 23INR0489 | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 232
185 | MIDLOTHIAN ENERGY FACILITY CTG 2 | 21INR0534 | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 230
186 | MIDLOTHIAN ENERGY FACILITY CTG 3 | 22INR0543 | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 229
187 | MIDLOTHIAN ENERGY FACILITY CTG 4 | 22INR0523 | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 232
188 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 244
189 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 246
190 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
191 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 66
192 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 66
193 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
194 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 68
195 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 68
196 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122 | 122
197 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118 | 118
198 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
199 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
200 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 351 | 322
201 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 445 | 420
202 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 435 | 410
203 | OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 46.7
204 | OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 46.7
205 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 218
206 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 217
207 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1 | 308
208 | PANDA TEMPLE I POWER CTG 1 | 22INR0533 | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 232 | 220
209 | PANDA TEMPLE I POWER CTG 2 | 22INR0533 | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 232 | 207
210 | PANDA TEMPLE I POWER STG 1 | 22INR0533 | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1 | 324
211 | PANDA TEMPLE II POWER CTG 1 | 23INR0524 | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.45
212 | PANDA TEMPLE II POWER CTG 2 | 23INR0524 | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.45
213 | PANDA TEMPLE II POWER STG 1 | 23INR0524 | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1 | 353.1
214 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 86
215 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 86
216 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 90 | 87
217 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 170
218 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 170
219 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 195.5 | 168
220 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.64
221 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.64
222 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.64
223 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.64
224 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64
225 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64
226 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64
227 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 89.4 | 64
228 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 89.4 | 65
229 | PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
230 | PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
231 | PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
232 | PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
233 | PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
234 | PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
235 | PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
236 | PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
237 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 61
238 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 62
239 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 52
240 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 56
241 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 56
242 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 54
243 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 25 | 21.5
244 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 43.2 | 36
245 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 80
246 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 80
247 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 80
248 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 80
249 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98.1 | 98
250 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98.1 | 98
251 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 104
252 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 104
253 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 74.98 | 75
254 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 113.61 | 120
255 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 216.01 | 208
256 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 88.4 | 90
257 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 113.64 | 107
258 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 156.6 | 146
259 | RABBS POWER STATION U1 |  | RAB_UNIT1 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.1
260 | RABBS POWER STATION U2 |  | RAB_UNIT2 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.1
261 | RABBS POWER STATION U3 |  | RAB_UNIT3 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.1
262 | RABBS POWER STATION U4 |  | RAB_UNIT4 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.1
263 | RABBS POWER STATION U5 |  | RAB_UNIT5 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.1
264 | RABBS POWER STATION U6 |  | RAB_UNIT6 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.1
265 | RABBS POWER STATION U7 |  | RAB_UNIT7 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.1
266 | RABBS POWER STATION U8 |  | RAB_UNIT8 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.1
267 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.28
268 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.28
269 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.28
270 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.28
271 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 162
272 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 162
273 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 162
274 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 373.16 | 306
275 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
276 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 51
277 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
278 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 41.98 | 40
279 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 83
280 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 83
281 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
282 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
283 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
284 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
285 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 198.9 | 151
286 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47
287 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47
288 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 191 | 148
289 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 60.5 | 46
290 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 50 | 40
291 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 25 | 20
292 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 136 | 130
293 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 136 | 133
294 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 351 | 336
295 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 25.71 | 26.7
296 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 25.71 | 26.7
297 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 177 | 167
298 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 479 | 502
299 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 16.32 | 14
300 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 56
301 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 56
302 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 56
303 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 56
304 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 56
305 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 56
306 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 56
307 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 56
308 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
309 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
310 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
311 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
312 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
313 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
314 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 109
315 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 109
316 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 100.62
317 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 100.62
318 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 100.62
319 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 143.65 | 131.52
320 | TEXAS GULF SULPHUR CTG 1 |  | TGS_GT01 | WHARTON | GAS-GT | SOUTH | 1985 | 94 | 68.5
321 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 239 | 235
322 | TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
323 | TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
324 | TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
325 | TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
326 | TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
327 | TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
328 | TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
329 | TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
330 | TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
331 | TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.09
332 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
333 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
334 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
335 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 47
336 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 225 | 217
337 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 240 | 230
338 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 420 | 412
339 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 46.7
340 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 46.7
341 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 46.7
342 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 46.7
343 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 196.86 | 171
344 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 180.2 | 132
345 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 16.32 | 13
346 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
347 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
348 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 299.2 | 246
349 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 580.5 | 536
350 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
351 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
352 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
353 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 20 | 17
354 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
355 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
356 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
357 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
358 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 275 | 244.4
359 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 275 | 244.4
360 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 290 | 298
361 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 240.4
362 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 234.4
363 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 300 | 270
364 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 116.45 | 105
365 | BIOENERGY AUSTIN-WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8
366 | BIOENERGY TEXAS-COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6
367 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2
368 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4
369 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2
370 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4
371 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2
372 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4
373 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2
374 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8
375 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 70242.13 | 63702.88
376
377 | Operational Resources - Synchronized but not Approved for Commercial Operations (Thermal)
378 | BRANDON (LP&L) (DGR) | 21INR0201 | BRANDON_UNIT1 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 25 | 20
379 | BEACHWOOD POWER STATION U4 | 22INR0607 | BCH_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.1
380 | BEACHWOOD POWER STATION U5 | 22INR0607 | BCH_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.1
381 | BEACHWOOD POWER STATION U6 | 22INR0607 | BCH_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.1
382 | COLORADO BEND ENERGY CENTER CTG 11 | 21INR0512 | CBEC_GT11 | WHARTON | GAS-GT | HOUSTON | 2023 | 41.65 | 39
383 | COLORADO BEND ENERGY CENTER CTG 12 | 21INR0512 | CBEC_GT12 | WHARTON | GAS-GT | HOUSTON | 2023 | 41.65 | 39
384 | R MASSENGALE CTG 1 (LP&L) | 21INR0202 | MASSENGL_G6 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
385 | R MASSENGALE CTG 2 (LP&L) | 21INR0202 | MASSENGL_G7 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
386 | R MASSENGALE STG (LP&L) | 21INR0202 | MASSENGL_G8 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 58.9 | 38
387 | TY COOKE CTG 1 (LP&L) | 21INR0506 | TY_COOKE_GT2 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 18.7 | 14
388 | TY COOKE CTG 2 (LP&L) | 21INR0506 | TY_COOKE_GT3 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 26.6 | 17
389 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 434 | 338.3
390
391 | Operational Capacity Thermal Unavailable due to Extended Outage or Derate |  | THERMAL_UNAVAIL |  |  |  |  | -654 | -610
392 | Operational Capacity Thermal Total |  | THERMAL_OPERATIONAL |  |  |  |  | 70022.13 | 63431.18
393
394 | Operational Resources (Hydro)
395 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 34.7 | 37.9
396 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 34.7 | 37.9
397 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 8
398 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9
399 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
400 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
401 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 18.3 | 17
402 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 50.8 | 49.5
403 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 50.8 | 49.5
404 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6
405 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12
406 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12
407 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12
408 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 27 | 29
409 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 27 | 29
410 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6
411 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 15 | 14
412 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 21
413 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 20
414 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
415 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
416 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
417 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 21 | 22
418 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 21 | 22
419 | Operational Capacity Total (Hydro) | [6 empty] | 549.6 | 557.4
420 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 549.6 | 427
421
422 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
423 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4 | 1.4
424 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDTP_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8
425 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7
426 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6
427 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2
428 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7 | 19.7
429 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  |  |  |  | 19.7 | 15
430
431 | Operational Capacity Hydroelectric Unavailable due to Extended Outage or Derate |  | HYDRO_UNAVAIL |  |  |  |  | -6 | -4.5963
432 | Operational Capacity Hydroelectric Total |  | HYDRO_OPERATIONAL |  |  |  |  | 563.3 | 437.4037
433
434 | Operational Resources (Switchable)
435 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
436 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
437 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
438 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 195
439 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 195
440 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
441 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
442 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
443 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400 | 400
444 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 179 | 162
445 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 179
446 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 179 | 178
447 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 389
448 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 162
449 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 158
450 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 322
451 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 159
452 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 161
453 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 323
454 | Switchable Capacity Total | [6 empty] | 3840.12 | 3691
455
456 | Switchable Capacity Unavailable to ERCOT
457 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56.04 | -56
458 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56.04 | -56
459 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56.04 | -56
460 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -202 | -195
461 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -202 | -195
462 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -572.12 | -558
463
464 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 126 | 118
465
466 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  |  |  |  | 9575 | 3131
467 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST | [5 empty] | -118
468
469 | Operational Co-located Resources with Large Flexible Loads (LFLs) Total | [6 empty] | 3074.45 | 1559.1
470
471 | Operational Resources (Wind)
472 | WESTERN TRAIL WIND (AJAX WIND) U1 |  | AJAXWIND_UNIT1 | WILBARGER | WIND-O | WEST | 2022 | 225.6 | 225.6
473 | WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WILBARGER | WIND-O | WEST | 2022 | 141 | 141
474 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7 | 36.7
475 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8 | 35.8
476 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7 | 177.7
477 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.83 | 99.8
478 | AQUILLA LAKE WIND U1 |  | AQUILLA_U1_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 13.9 | 13.9
479 | AQUILLA LAKE WIND U2 |  | AQUILLA_U1_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 135.4 | 135.4
480 | AQUILLA LAKE 2 WIND U1 |  | AQUILLA_U2_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 7 | 7
481 | AQUILLA LAKE 2 WIND U2 |  | AQUILLA_U2_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 143.8 | 143.8
482 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.12 | 180.12
483 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.64 | 145.64
484 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.26 | 199.26
485 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100
486 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102
487 | BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | ANDREWS | WIND-O | WEST | 2021 | 90.2 | 90.2
488 | BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | ANDREWS | WIND-O | WEST | 2021 | 70.5 | 70.5
489 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120 | 120
490 | BLUE SUMMIT WIND 1 A | 22INR0550 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 132.84 | 132.8
491 | BLUE SUMMIT WIND 1 B | 22INR0550 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 6.96 | 6.9
492 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 92.5 | 92.5
493 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.86 | 6.9
494 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.7 | 13.4
495 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 186.5 | 182.4
496 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162 | 162
497 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.85 | 149.8
498 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120
499 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108
500 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9 | 44.9
501 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7 | 55.7
502 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6 | 120.6
503 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5 | 115.5
504 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117 | 117
505 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2 | 170.2
506 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 89 | 88
507 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 91 | 90
508 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2 | 115.2
509 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4 | 122.4
510 | CACTUS FLATS WIND U1 |  | CFLATS_U1 | CONCHO | WIND-O | WEST | 2022 | 148.4 | 148.4
511 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1 | 123.1
512 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165
513 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 134.42 | 130.5
514 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 123.6 | 120
515 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1 | 210.1
516 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7 | 231.7
517 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5 | 149.5
518 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9 | 200.9
519 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | STERLING | WIND-O | WEST | 2008 | 121.5 | 121.5
520 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75
521 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75
522 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.25 | 173.25
523 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5 | 126.5
524 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6
525 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4
526 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4 | 50.4
527 | CRANELL WIND |  | CRANELL_UNIT1 | REFUGIO | WIND-C | COASTAL | 2022 | 220 | 220
528 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
529 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
530 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
531 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
532 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 101.2 | 98
533 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 99 | 96
534 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 121.9 | 121.9
535 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 101.31 | 98.9
536 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 134.29 | 131.1
537 | EL ALGODON ALTO W U1 |  | ALGODON_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 171.6 | 171.6
538 | EL ALGODON ALTO W U2 |  | ALGODON_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 28.6 | 28.6
539 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2 | 25.2
540 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200 | 200
541 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8 | 79.8
542 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6 | 75.6
543 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.48 | 186.5
544 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8 | 163.8
545 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2 | 124.2
546 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80 | 80
547 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6 | 69.6
548 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6 | 148.6
549 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82 | 82
550 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76 | 76
551 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4 | 107.4
552 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8 | 103.8
553 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 21INR0532 | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99 | 99
554 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 21INR0532 | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61 | 61
555 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
556 | GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 98.7 | 98.7
557 | GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 126.9 | 126.9
558 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
559 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
560 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.93 | 119.93
561 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 165.6 | 163.5
562 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9 | 99.9
563 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100 | 100
564 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5 | 152.5
565 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5 | 147.5
566 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52 | 52
567 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98 | 98
568 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100 | 100
569 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4 | 50.4
570 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46 | 46
571 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 51.9 | 52
572 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
573 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.4 | 122.5
574 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
575 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.5 | 127.6
576 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.5 | 101.6
577 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 134.81 | 131.1
578 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 101.69 | 98.9
579 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230 | 230
580 | HORSE HOLLOW WIND 2 | 17INR0053 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184 | 184
581 | HORSE HOLLOW WIND 3 | 17INR0053 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4 | 241.4
582 | HORSE HOLLOW WIND 4 | 17INR0053 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115 | 115
583 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95 | 95
584 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102 | 102
585 | INDIAN MESA WIND | 18INR0069 | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8 | 91.8
586 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.69 | 19.7
587 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230 | 230
588 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96 | 96
589 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74 | 74
590 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30 | 30
591 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.15 | 146.15
592 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.55 | 153.55
593 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
594 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
595 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.42 | 100.4
596 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110 | 110
597 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 159.96 | 159.96
598 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7 | 183.7
599 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.26 | 106.3
600 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.85 | 103.8
601 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194 | 194
602 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98 | 98
603 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100 | 100
604 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
605 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
606 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48 | 48
607 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51 | 51
608 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5 | 25.5
609 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24 | 24
610 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200 | 200
611 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200 | 200
612 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110 | 110
613 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1
614 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6
615 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.83 | 99.8
616 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.46 | 103.5
617 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
618 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
619 | MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | CONCHO | WIND-O | WEST | 2022 | 201.6 | 201.6
620 | MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | CONCHO | WIND-O | WEST | 2022 | 11.1 | 11.1
621 | MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | CONCHO | WIND-O | WEST | 2022 | 33.6 | 33.6
622 | MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | CONCHO | WIND-O | WEST | 2022 | 22.2 | 22.2
623 | MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | CONCHO | WIND-O | WEST | 2022 | 71.4 | 71.4
624 | MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | CONCHO | WIND-O | WEST | 2022 | 33.3 | 33.3
625 | MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | CONCHO | WIND-O | WEST | 2022 | 22 | 22
626 | MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | CONCHO | WIND-O | WEST | 2022 | 20 | 20
627 | MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | CONCHO | WIND-O | WEST | 2022 | 76.8 | 76.8
628 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150 | 150
629 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
630 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
631 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
632 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
633 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8 | 162.8
634 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6 | 196.6
635 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.61 | 92.6
636 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60 | 60
637 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 58.8 | 58.8
638 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2 | 151.2
639 | OVEJA WIND U1 |  | OVEJA_G1 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
640 | OVEJA WIND U2 |  | OVEJA_G2 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
641 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9 | 144.9
642 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.15
643 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.15
644 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.19 | 94.19
645 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6 | 96.6
646 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5 | 142.5
647 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5 | 115.5
648 | PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | HOWARD | WIND-O | WEST | 2022 | 106.92 | 106.92
649 | PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | HOWARD | WIND-O | WEST | 2022 | 108.54 | 108.54
650 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.85 | 179.9
651 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.12 | 200.1
652 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7 | 91.7
653 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86 | 85.8
654 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8
655 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6
656 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8
657 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2 | 151.2
658 | PYRON WIND 1 | 23INR0525 | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5 | 121.5
659 | PYRON WIND 2 | 23INR0525 | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5 | 127.5
660 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
661 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
662 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 104.26 | 104.3
663 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 102.99 | 103
664 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6 | 89.6
665 | RELOJ DEL SOL WIND U1 |  | RELOJ_UNIT1 | ZAPATA | WIND-O | SOUTH | 2022 | 55.4 | 55.4
666 | RELOJ DEL SOL WIND U2 |  | RELOJ_UNIT2 | ZAPATA | WIND-O | SOUTH | 2022 | 48 | 48
667 | RELOJ DEL SOL WIND U3 |  | RELOJ_UNIT3 | ZAPATA | WIND-O | SOUTH | 2022 | 83.1 | 83.1
668 | RELOJ DEL SOL WIND U4 |  | RELOJ_UNIT4 | ZAPATA | WIND-O | SOUTH | 2022 | 22.8 | 22.8
669 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9 | 121.9
670 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.44 | 27.4
671 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114 | 114
672 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95 | 95
673 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150 | 150
674 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
675 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
676 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160 | 160
677 | SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
678 | SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
679 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64 | 64
680 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110 | 110
681 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.25 | 95.2
682 | SAND BLUFF WIND U1 | 20INR0296 | MCDLD_SB1_2 | GLASSCOCK | WIND-O | WEST | 2022 | 71.4 | 71.4
683 | SAND BLUFF WIND U2 | 20INR0296 | MCDLD_SB3_282 | GLASSCOCK | WIND-O | WEST | 2022 | 14.1 | 14.1
684 | SAND BLUFF WIND U3 | 20INR0296 | MCDLD_SB4_G87 | GLASSCOCK | WIND-O | WEST | 2022 | 4 | 4
685 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150 | 150
686 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78 | 78
687 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.24 | 30.24
688 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.05 | 226.1
689 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1 | 204.1
690 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132 | 132
691 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8 | 52.8
692 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102 | 102
693 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98 | 98
694 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5 | 148.5
695 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8 | 151.8
696 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 101.2 | 98.2
697 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 160.95 | 160.95
698 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98 | 98
699 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96 | 96
700 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 123.6 | 120
701 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201 | 201
702 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 213.82 | 211.2
703 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 166.52 | 164.68
704 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 37.5 | 42.5
705 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16 | 16.8
706 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 105.3 | 110.8
707 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 30.78 | 33.6
708 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 108.54 | 118.6
709 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 119 | 125
710 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 105.8 | 112
711 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 80.5 | 85
712 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150 | 150
713 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150 | 150
714 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.72 | 27.7
715 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6 | 6.6
716 | TG EAST WIND U1 |  | TRUSGILL_UNIT1 | KNOX | WIND-O | WEST | 2022 | 42 | 42
717 | TG EAST WIND U2 |  | TRUSGILL_UNIT2 | KNOX | WIND-O | WEST | 2022 | 44.8 | 44.8
718 | TG EAST WIND U3 |  | TRUSGILL_UNIT3 | KNOX | WIND-O | WEST | 2022 | 42 | 42
719 | TG EAST WIND U4 |  | TRUSGILL_UNIT4 | KNOX | WIND-O | WEST | 2022 | 207.2 | 207.2
720 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150 | 150
721 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23 | 23
722 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5 | 127.5
723 | TRENT WIND 1 A | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 38.25 | 38.3
724 | TRENT WIND 1 B |  | TRENT_UNIT_1B | NOLAN | WIND-O | WEST | 2018 | 15.59 | 15.6
725 | TRENT WIND 2 |  | TRENT_UNIT_2 | NOLAN | WIND-O | WEST | 2018 | 50.49 | 50.5
726 | TRENT WIND 3 A |  | TRENT_UNIT_3A | NOLAN | WIND-O | WEST | 2018 | 38.25 | 38.3
727 | TRENT WIND 3 B |  | TRENT_UNIT_3B | NOLAN | WIND-O | WEST | 2018 | 13.79 | 13.8
728 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4 | 103.4
729 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6 | 94.6
730 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2 | 2
731 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 174.6 | 169.5
732 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6 | 125.6
733 | VENADO WIND U1 |  | VENADO_UNIT1 | ZAPATA | WIND-O | SOUTH | 2021 | 105 | 105
734 | VENADO WIND U2 |  | VENADO_UNIT2 | ZAPATA | WIND-O | SOUTH | 2021 | 96.6 | 96.6
735 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12 | 12
736 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2 | 7.2
737 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
738 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22 | 22
739 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
740 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
741 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.91 | 114.9
742 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.35 | 142.3
743 | WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 116.6 | 116.6
744 | WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 123.2 | 123.2
745 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 59.8 | 56.96
746 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.34 | 92.3
747 | WHITE MESA WIND U1 |  | WHMESA_UNIT1 | CROCKETT | WIND-O | WEST | 2022 | 152.3 | 152.3
748 | WHITE MESA 2 WIND U1 |  | WHMESA_UNIT2_23 | CROCKETT | WIND-O | WEST | 2022 | 13.92 | 13.9
749 | WHITE MESA 2 WIND U2 |  | WHMESA_UNIT2_28 | CROCKETT | WIND-O | WEST | 2022 | 183.3 | 183.3
750 | WHITE MESA 2 WIND U3 |  | WHMESA_UNIT3_23 | CROCKETT | WIND-O | WEST | 2022 | 18.56 | 18.6
751 | WHITE MESA 2 WIND U4 |  | WHMESA_UNIT3_28 | CROCKETT | WIND-O | WEST | 2022 | 132.54 | 132.5
752 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
753 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
754 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5 | 199.5
755 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.62 | 67.62
756 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30 | 30
757 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5 | 112.5
758 | Operational Capacity Total (Wind) | [6 empty] | 30938.15 | 30925.66
759
760 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 4862.27 | 4856.05
761 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 100 | 64
762
763 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4247.23 | 4244.2
764 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 100 | 39
765
766 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 21828.65 | 21825.41
767 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 100 | 39
768
769 | Operational Resources (Wind) - Synchronized but not Approved for Commercial Operations
770 | AGUAYO WIND | 20INR0250 | AGUAYO_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 193.5 | 192.9
771 | ANCHOR WIND U1 | 21INR0546 | ANCHOR_WIND1 | CALLAHAN | WIND-O | WEST | 2023 | 16 | 16
772 | ANCHOR WIND U2 | 21INR0387 | ANCHOR_WIND2 | CALLAHAN | WIND-O | WEST | 2023 | 98.9 | 98.9
773 | ANCHOR WIND II B | 21INR0539 | ANCHOR_WIND3 | CALLAHAN | WIND-O | WEST | 2023 | 90 | 90
774 | ANCHOR WIND U4 | 21INR0539 | ANCHOR_WIND4 | CALLAHAN | WIND-O | WEST | 2023 | 38.7 | 38.7
775 | ANCHOR WIND U5 | 22INR0562 | ANCHOR_WIND5 | CALLAHAN | WIND-O | WEST | 2022 | 19.3 | 19.3
776 | APPALOOSA RUN WIND U2 | 20INR0249 | APPALOSA_UNIT1 | UPTON | WIND-O | WEST | 2023 | 157.9 | 157.9
777 | APPALOOSA RUN WIND U2 | 20INR0249 | APPALOSA_UNIT2 | UPTON | WIND-O | WEST | 2023 | 13.9 | 13.9
778 | APOGEE WIND U1 | 21INR0467 | APOGEE_UNIT1 | THROCKMORTON | WIND-O | WEST | 2023 | 25 | 25
779 | APOGEE WIND U2 | 21INR0467 | APOGEE_UNIT2 | THROCKMORTON | WIND-O | WEST | 2023 | 14 | 14
780 | APOGEE WIND U3 | 21INR0467 | APOGEE_UNIT3 | THROCKMORTON | WIND-O | WEST | 2023 | 30.2 | 30.2
781 | APOGEE WIND U4 | 21INR0467 | APOGEE_UNIT4 | THROCKMORTON | WIND-O | WEST | 2023 | 115 | 115
782 | APOGEE WIND U5 | 21INR0467 | APOGEE_UNIT5 | THROCKMORTON | WIND-O | WEST | 2023 | 110 | 110
783 | APOGEE WIND U6 | 21INR0467 | APOGEE_UNIT6 | THROCKMORTON | WIND-O | WEST | 2023 | 24 | 24
784 | APOGEE WIND U7 | 21INR0467 | APOGEE_UNIT7 | THROCKMORTON | WIND-O | WEST | 2023 | 75 | 75
785 | BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | CALLAHAN | WIND-O | WEST | 2023 | 195 | 195
786 | BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | CALLAHAN | WIND-O | WEST | 2023 | 145 | 145
787 | BLACKJACK CREEK WIND U1 | 20INR0068 | BLACKJAK_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 120 | 120
788 | BLACKJACK CREEK WIND U2 | 20INR0068 | BLACKJAK_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 120 | 120
789 | BOARD CREEK WP U1 | 21INR0324 | BOARDCRK_UNIT1 | NAVARRO | WIND-O | NORTH | 2023 | 108.8 | 108.8
790 | BOARD CREEK WP U2 | 21INR0324 | BOARDCRK_UNIT2 | NAVARRO | WIND-O | NORTH | 2023 | 190.4 | 190.4
791 | COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | SCURRY | WIND-O | WEST | 2023 | 90 | 90
792 | COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | SCURRY | WIND-O | WEST | 2023 | 26.6 | 26.6
793 | COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | SCURRY | WIND-O | WEST | 2023 | 126 | 126
794 | EL SUAZ RANCH U1 | 20INR0097 | ELSAUZ_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 153 | 153
795 | EL SUAZ RANCH U2 | 20INR0097 | ELSAUZ_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 148.5 | 148.5
796 | FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 130.2 | 130.2
797 | FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 84 | 84
798 | FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | BEE | WIND-O | SOUTH | 2023 | 54 | 54
799 | HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | GLASSCOCK | WIND-O | WEST | 2023 | 162.1 | 162.1
800 | INERTIA WIND U1 | 22INR0326 | INRT_W_UNIT1 | HASKELL | WIND-O | WEST | 2023 | 67.7 | 67.7
801 | INERTIA WIND U2 | 22INR0326 | INRT_W_UNIT2 | HASKELL | WIND-O | WEST | 2023 | 27.7 | 27.7
802 | INERTIA WIND U3 | 22INR0326 | INRT_W_UNIT3 | HASKELL | WIND-O | WEST | 2023 | 205.9 | 205.9
803 | LACY CREEK WIND U1 | 18INR0043 | LACY_CRK_UNIT1 | GLASSCOCK | WIND-O | WEST | 2023 | 135.4 | 135.4
804 | LACY CREEK WIND U2 | 18INR0043 | LACY_CRK_UNIT2 | GLASSCOCK | WIND-O | WEST | 2023 | 15.12 | 15.1
805 | LACY CREEK WIND U3 | 18INR0043 | LACY_CRK_UNIT3 | GLASSCOCK | WIND-O | WEST | 2023 | 138.2 | 138.18
806 | LACY CREEK WIND U4 | 18INR0043 | LACY_CRK_UNIT4 | GLASSCOCK | WIND-O | WEST | 2023 | 12.6 | 12.6
807 | LAS MAJADAS WIND U1 | 17INR0035 | LMAJADAS_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 110 | 110
808 | LAS MAJADAS WIND U2 | 17INR0035 | LMAJADAS_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 24 | 24
809 | LAS MAJADAS WIND U3 | 17INR0035 | LMAJADAS_UNIT3 | WILLACY | WIND-C | COASTAL | 2023 | 138.6 | 138.6
810 | MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | NOLAN | WIND-O | WEST | 2022 | 182.4 | 182.4
811 | MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | STARR | WIND-O | SOUTH | 2022 | 201.6 | 201.6
812 | PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | LIMESTONE | WIND-O | NORTH | 2023 | 153 | 153
813 | PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | LIMESTONE | WIND-O | NORTH | 2023 | 147 | 147
814 | PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 187.2 | 187.2
815 | PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | MILLS | WIND-O | NORTH | 2023 | 115.2 | 115.2
816 | VORTEX WIND U1 | 20INR0120 | VORTEX_WIND1 | THROCKMORTON | WIND-O | WEST | 2023 | 153.6 | 153.6
817 | VORTEX WIND U2 | 20INR0120 | VORTEX_WIND2 | THROCKMORTON | WIND-O | WEST | 2023 | 24.2 | 24.2
818 | VORTEX WIND U3 | 20INR0120 | VORTEX_WIND3 | THROCKMORTON | WIND-O | WEST | 2023 | 158.4 | 158.4
819 | VORTEX WIND U4 | 20INR0120 | VORTEX_WIND4 | THROCKMORTON | WIND-O | WEST | 2023 | 14 | 14
820 | WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | FISHER | WIND-O | WEST | 2023 | 209.4 | 209.4
821 | WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | FISHER | WIND-O | WEST | 2023 | 209.5 | 209.5
822 | WILDWIND U1 | 20INR0033 | WILDWIND_UNIT1 | COOKE | WIND-O | NORTH | 2023 | 18.38 | 18.4
823 | WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | COOKE | WIND-O | NORTH | 2023 | 48 | 48
824 | WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | COOKE | WIND-O | NORTH | 2023 | 6.3 | 6.3
825 | WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | COOKE | WIND-O | NORTH | 2023 | 54.6 | 54.6
826 | WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | COOKE | WIND-O | NORTH | 2023 | 52.8 | 52.8
827 | YOUNG WIND U3 | 21INR0401 | YNG_WND_UNIT1 | YOUNG | WIND-O | WEST | 2023 | 197.4 | 197.4
828 | YOUNG WIND U2 | 21INR0401 | YNG_WND_UNIT2 | YOUNG | WIND-O | WEST | 2023 | 152.28 | 152.28
829 | YOUNG WIND U3 | 21INR0401 | YNG_WND_UNIT3 | YOUNG | WIND-O | WEST | 2023 | 149.46 | 149.46
830 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 6184.94 | 6184.32
831
832 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Coastal Counties) |  | WIND_SYNCHRONIZED_C |  |  |  |  | 574.1 | 574.1
833 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_SYNC_PEAK_PCT_C | % |  |  |  | 100 | 64
834
835 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Panhandle Counties) |  | WIND_SYNCHRONIZED_P |  |  |  |  | 0 | 0
836 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_SYNC_PEAK_PCT_P | % |  |  |  | 100 | 39
837
838 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Other Counties) |  | WIND_SYNCHRONIZED_O |  |  |  |  | 5610.84 | 5610.22
839 | Wind Peak Average Capacity Percentage (Other) |  | WIND_SYNC_PEAK_PCT_O | % |  |  |  | 100 | 39
840
841 | Operational Resources (Solar)
842 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 9.99
843 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10 | 10
844 | ANSON SOLAR U1 |  | ANSON1_UNIT1 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
845 | ANSON SOLAR U2 |  | ANSON1_UNIT2 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
846 | ARAGORN SOLAR |  | ARAGORN_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 188.2 | 187.2
847 | AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | HASKELL | SOLAR | WEST | 2021 | 74.9 | 74.9
848 | AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | HASKELL | SOLAR | WEST | 2021 | 153.5 | 153.5
849 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1 | 1
850 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 50 | 49.1
851 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6
852 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3
853 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30 | 30
854 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100 | 100
855 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15 | 15
856 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6
857 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50 | 50
858 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
859 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
860 | BRIGHTSIDE SOLAR |  | BRIGHTSD_UNIT1 | BEE | SOLAR | SOUTH | 2022 | 53.4 | 50
861 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
862 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
863 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
864 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
865 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180
866 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10 | 10
867 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10 | 10
868 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5 | 5
869 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7 | 125.7
870 | CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | WEBB | SOLAR | SOUTH | 2021 | 202.6 | 202.6
871 | DANCIGER SOLAR U1 |  | DAG_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100
872 | DANCIGER SOLAR U2 |  | DAG_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100
873 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144 | 144
874 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10 | 10
875 | ELARA SOLAR |  | ELARA_SL_UNIT1 | FRIO | SOLAR | SOUTH | 2022 | 132.4 | 132.4
876 | EUNICE SOLAR U1 |  | EUNICE_PV1 | ANDREWS | SOLAR | WEST | 2021 | 189.6 | 189.6
877 | EUNICE SOLAR U2 |  | EUNICE_PV2 | ANDREWS | SOLAR | WEST | 2021 | 237.1 | 237.1
878 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6 | 1.6
879 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 152.5 | 150
880 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22
881 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 126 | 121.1
882 | GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | CONCHO | SOLAR | WEST | 2021 | 251.4 | 250
883 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 126.3 | 124.6
884 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 132.2 | 130.4
885 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5 | 5
886 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3 | 5.3
887 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6
888 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2 | 102.2
889 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3 | 102.3
890 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5 | 198.5
891 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1 | 162.1
892 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5 | 143.5
893 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8 | 59.8
894 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5 | 7.5
895 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7 | 100.7
896 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10 | 10
897 | LILY SOLAR |  | LILY_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2021 | 147.6 | 147.6
898 | LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | BORDEN | SOLAR | WEST | 2021 | 98.5 | 98.5
899 | LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | BORDEN | SOLAR | WEST | 2021 | 128.3 | 128.3
900 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3 | 5.3
901 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10 | 10
902 | MISAE SOLAR U1 |  | MISAE_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 121.4 | 121.4
903 | MISAE SOLAR U2 |  | MISAE_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 118.6 | 118.6
904 | NEBULA SOLAR (RAYOS DEL SOL) U1 |  | NEBULA_UNIT1 | CAMERON | SOLAR | COASTAL | 2022 | 137.5 | 137.5
905 | NOBLE SOLAR U1 |  | NOBLESLR_SOLAR1 | DENTON | SOLAR | NORTH | 2022 | 148.8 | 146.7
906 | NOBLE SOLAR U2 |  | NOBLESLR_SOLAR2 | DENTON | SOLAR | NORTH | 2022 | 130.2 | 128.3
907 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2 | 5.2
908 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180 | 180
909 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.18 | 39.18
910 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4
911 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5
912 | OCI ALAMO 4 SOLAR-BRACKETVILLE | 22INR0600 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.62 | 37.6
913 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100 | 100
914 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2 | 110.2
915 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112 | 112
916 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.04 | 125.14
917 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 127.95 | 128.05
918 | PHOENIX SOLAR |  | PHOENIX_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 83.9 | 83.9
919 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6 | 2.6
920 | PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6 | 153.6
921 | PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150 | 150
922 | PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | ANDREWS | SOLAR | WEST | 2021 | 126.5 | 126.5
923 | PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | ANDREWS | SOLAR | WEST | 2021 | 126.4 | 126.4
924 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
925 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
926 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5 | 97.5
927 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5 | 107.5
928 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 211.19 | 200
929 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.75
930 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.75
931 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PECOS | SOLAR | WEST | 2021 | 222 | 222
932 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PECOS | SOLAR | WEST | 2021 | 28 | 28
933 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2
934 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 155.44 | 150
935 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8 | 59.8
936 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50
937 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5
938 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10 | 10
939 | STRATEGIC SOLAR 1 |  | STRATEGC_UNIT1 | ELLIS | SOLAR | NORTH | 2022 | 135 | 135
940 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
941 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
942 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6
943 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5
944 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9 | 125.9
945 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9 | 128.9
946 | TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 136.8 | 136.8
947 | TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | CULBERSON | SOLAR | WEST | 2021 | 131.1 | 131.1
948 | TPE ERATH SOLAR |  | DG_ERATH_ERATH21 | ERATH | SOLAR | NORTH | 2021 | 10 | 10
949 | VANCOURT SOLAR |  | VANCOURT_UNIT1 | CAMERON | SOLAR | COASTAL | 2023 | 45.7 | 45.7
950 | VISION SOLAR 1 |  | VISION_UNIT1 | NAVARRO | SOLAR | NORTH | 2022 | 129.2 | 127
951 | WAGYU SOLAR |  | WGU_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2021 | 120 | 120
952 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10
953 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182 | 182
954 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7
955 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5 | 5
956 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100 | 100
957 | WESTORIA SOLAR U1 |  | WES_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6
958 | WESTORIA SOLAR U2 |  | WES_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6
959 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
960 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
961 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10 | 10
962 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10 | 10
963 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5 | 5
964 | Operational Capacity Total (Solar) | [6 empty] | 9798.42 | 9753.76
965 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 100 | 72
966
967 | Operational Resources (Solar) - Synchronized but not Approved for Commercial Operations
968 | BIG STAR SOLAR U1 | 21INR0413 | BIG_STAR_UNIT1 | BASTROP | SOLAR | SOUTH | 2023 | 132.27 | 130
969 | BIG STAR SOLAR U2 | 21INR0413 | BIG_STAR_UNIT2 | BASTROP | SOLAR | SOUTH | 2023 | 70.83 | 70
970 | BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | GRIMES | SOLAR | NORTH | 2023 | 69 | 69
971 | BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | GRIMES | SOLAR | NORTH | 2023 | 141 | 141
972 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 217.5 | 217.5
973 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 221.3 | 221.3
974 | CROWN SOLAR | 21INR0323 | CRWN_SLR_UNIT1 | FALLS | SOLAR | NORTH | 2023 | 101.3 | 100.7
975 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 | EGROVESL_UNIT1 | CRANE | SOLAR | WEST | 2023 | 109.5 | 108
976 | FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 179.5 | 179.6
977 | FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 171.8 | 171.9
978 | GOLINDA SOLAR | 21INR0434 | GOLINDA_UNIT1 | FALLS | SOLAR | NORTH | 2023 | 101.1 | 100.5
979 | GRIZZLY RIDGE SOLAR | 21INR0375 | GRIZZLY_SOLAR1 | HAMILTON | SOLAR | NORTH | 2023 | 101.7 | 100
980 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b | HOVEY_UNIT2 | PECOS | SOLAR | WEST | 2023 | 7.41 | 7.4
981 | MCLEAN (SHAKES) SOLAR | 19INR0073 | MCLNSLR_UNIT1 | DIMMIT | SOLAR | SOUTH | 2023 | 207.4 | 200
982 | MUSTANG CREEK SOLAR U1 | 18INR0050 | MUSTNGCK_SOLAR1 | JACKSON | SOLAR | SOUTH | 2023 | 60.2 | 60
983 | MUSTANG CREEK SOLAR U2 | 18INR0050 | MUSTNGCK_SOLAR2 | JACKSON | SOLAR | SOUTH | 2023 | 90.3 | 90
984 | MYRTLE SOLAR U1 | 19INR0041 | MYR_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 171.6 | 171.6
985 | MYRTLE SOLAR U2 | 19INR0041 | MYR_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 149.6 | 149.6
986 | PISGAH RIDGE SOLAR U1 | 22INR0254 | PISGAH_SOLAR1 | NAVARRO | SOLAR | NORTH | 2023 | 189.4 | 186.5
987 | PISGAH RIDGE SOLAR U2 | 22INR0254 | PISGAH_SOLAR2 | NAVARRO | SOLAR | NORTH | 2023 | 64.4 | 63.5
988 | PLAINVIEW SOLAR (RAMSEY SOLAR) U1 | 20INR0130 | PLN_UNIT1 | WHARTON | SOLAR | SOUTH | 2023 | 270 | 257
989 | PLAINVIEW SOLAR (RAMSEY SOLAR) U2 | 20INR0130 | PLN_UNIT2 | WHARTON | SOLAR | SOUTH | 2023 | 270 | 257
990 | RADIAN SOLAR U1 | 21INR0205 | RADN_SLR_UNIT1 | BROWN | SOLAR | NORTH | 2023 | 161.41 | 158.9
991 | RADIAN SOLAR U2 | 21INR0205 | RADN_SLR_UNIT2 | BROWN | SOLAR | NORTH | 2023 | 166.02 | 162.9
992 | RATLIFF SOLAR (CONCHO VALLEY SOLAR) | 21INR0384 | RATLIFF_SOLAR1 | TOM GREEN | SOLAR | WEST | 2023 | 162.43 | 159.8
993 | ROSELAND SOLAR U1 | 20INR0205 | ROSELAND_SOLAR1 | FALLS | SOLAR | NORTH | 2023 | 254 | 250
994 | ROSELAND SOLAR U2 | 20INR0205 | ROSELAND_SOLAR2 | FALLS | SOLAR | NORTH | 2023 | 167.9 | 165.3
995 | ROSELAND SOLAR U3 | 22INR0506 | ROSELAND_SOLAR3 | FALLS | SOLAR | NORTH | 2023 | 86.1 | 84.7
996 | ROWLAND SOLAR I | 19INR0131 | ROW_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 101.7 | 100
997 | TAYGETE II SOLAR U1 | 21INR0233 | TAYGETE2_UNIT1 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9
998 | TAYGETE II SOLAR U2 | 21INR0233 | TAYGETE2_UNIT2 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9
999 | SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125
1000 | SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125
1001 | SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125
1002 | SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125
1003 | SUN VALLEY U1 | 19INR0169 | SUNVASLR_UNIT1 | HILL | SOLAR | NORTH | 2023 | 165.75 | 165.8
1004 | SUN VALLEY U2 | 19INR0169 | SUNVASLR_UNIT2 | HILL | SOLAR | NORTH | 2023 | 86.19 | 86.2
1005 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Solar) | [6 empty] | 5166.09 | 5089.5
1006 | Solar Peak Average Capacity Percentage |  | SOLAR_SYNC_PEAK_PCT | % |  |  |  | 100 | 72
1007
1008 | Operational Resources (Storage)
1009 | AZURE SKY BESS |  | AZURE_BESS1 | HASKELL | STORAGE | WEST | 2022 | 77.6 | 77.6
1010 | BAT CAVE |  | BATCAVE_BES1 | MASON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
1011 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30
1012 | BRP ALVIN (DGR) |  | ALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 9.95
1013 | BRP ANGELTON (DGR) |  | ANGLETON_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 9.95
1014 | BRP BRAZORIA |  | BRAZORIA_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 9.95
1015 | BRP DICKINSON (DGR) |  | DICKNSON_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 9.95
1016 | BRP HEIGHTS (DGR) |  | HEIGHTTN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 9.95
1017 | BRP LOOP 463 (DGR) |  | L_463S_UNIT1 | VICTORIA | STORAGE | SOUTH | 2023 | 9.95 | 9.95
1018 | BRP LOPENO (DGR) |  | BRP_LOP1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.95
1019 | BRP MAGNOLIA (DGR) |  | MAGNO_TN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 9.95
1020 | BRP ODESSA SW (DGR) |  | ODESW_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 9.95 | 9.95
1021 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.95 | 9.95
1022 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.95 | 9.95
1023 | BRP RANCHTOWN (DGR) |  | BRP_RNC1_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 9.95 | 9.95
1024 | BRP SWEENY (DGR) |  | SWEENY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 9.95
1025 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.95
1026 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.95
1027 | BYRD RANCH STORAGE |  | BYRDR_ES_BESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 50.6 | 50
1028 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2018 | 9.9 | 9.9
1029 | CATARINA BESS (DGR) |  | CATARINA_BESS | DIMMIT | STORAGE | SOUTH | 2022 | 9.95 | 9.9
1030 | CEDARVALE BESS (DGR) |  | CEDRVALE_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1031 | CHISHOLM GRID |  | CHISMGRD_BES1 | TARRANT | STORAGE | NORTH | 2021 | 101.7 | 100
1032 | COMMERCE ST ESS (DGR) |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10 | 10
1033 | COYOTE SPRINGS BESS (DGR) |  | COYOTSPR_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1034 | CROSSETT POWER U1 |  | CROSSETT_BES1 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100
1035 | CROSSETT POWER U2 |  | CROSSETT_BES2 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100
1036 | DECORDOVA BESS U1 |  | DCSES_BES1 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1037 | DECORDOVA BESS U2 |  | DCSES_BES2 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1038 | DECORDOVA BESS U3 |  | DCSES_BES3 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1039 | DECORDOVA BESS U4 |  | DCSES_BES4 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1040 | ENDURANCE PARK STORAGE |  | ENDPARKS_ESS1 | SCURRY | STORAGE | WEST | 2022 | 51.5 | 50
1041 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2021 | 40.3 | 40.3
1042 | FAULKNER BESS (DGR) |  | FAULKNER_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1043 | FLAT TOP BATTERY (DGR) |  | FLAT_TOP_BESS1 | REEVES | STORAGE | WEST | 2023 | 9.9 | 9.9
1044 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2021 | 9.9 | 9.9
1045 | FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | REEVES | STORAGE | WEST | 2022 | 101.5 | 100
1046 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 102.4 | 100
1047 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2020 | 2 | 2
1048 | HOLCOMB BESS (DGR) |  | HOLCOMB_BESS | LA SALLE | STORAGE | SOUTH | 2023 | 9.95 | 9.9
1049 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9 | 9.9
1050 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.25 | 2.25
1051 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5 | 1.5
1052 | LILY STORAGE |  | LILY_BESS1 | KAUFMAN | STORAGE | NORTH | 2021 | 51.7 | 51.7
1053 | LONESTAR BESS (DGR) |  | LONESTAR_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9
1054 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5 | 1.5
1055 | NOBLE STORAGE U1 |  | NOBLESLR_BESS1 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5
1056 | NOBLE STORAGE U2 |  | NOBLESLR_BESS2 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5
1057 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 36 | 33.7
1058 | NORTH COLUMBIA (ROUGHNECK STORAGE) |  | NCO_ESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 51.75 | 50
1059 | NORTH FORK |  | NF_BRP_BES1 | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
1060 | PORT LAVACA BATTERY (DGR) |  | PTLBES_BESS1 | CALHOUN | STORAGE | COASTAL | 2020 | 9.9 | 9.9
1061 | PROSPECT STORAGE (DGR) |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.9 | 9.9
1062 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9 | 9.9
1063 | RABBIT HILL ENERGY STORAGE PROJECT (DGR) |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9 | 9.9
1064 | RATTLESNAKE BESS (DGR) |  | RTLSNAKE_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9
1065 | REPUBLIC ROAD STORAGE |  | RPUBRDS_ESS1 | ROBERTSON | STORAGE | NORTH | 2022 | 51.75 | 50
1066 | SADDLEBACK BESS (DGR) |  | SADLBACK_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1067 | SARAGOSA BESS (DGR) |  | SGSA_BESS1 | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1068 | SCREWBEAN BESS (DGR) |  | SBEAN_BESS | CULBERSON | STORAGE | WEST | 2023 | 10 | 9.9
1069 | SNYDER (DGR) |  | SNY_BESS_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 9.95 | 9.95
1070 | SWEETWATER BESS (DGR) |  | SWT_BESS_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.95 | 9.95
1071 | SWOOSE BATTERY (PYOTE) (DGR) |  | SWOOSE1_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9 | 9.9
1072 | SWOOSE II |  | SWOOSEII_BESS1 | WARD | STORAGE | WEST | 2022 | 101.5 | 100
1073 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2 | 2
1074 | TOYAH POWER STATION (DGR) |  | TOYAH_BESS | REEVES | STORAGE | WEST | 2021 | 9.95 | 9.9
1075 | TRIPLE BUTTE (DGR) |  | TRIPBUT1_BELU1 | PECOS | STORAGE | WEST | 2021 | 9.18 | 7.5
1076 | WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 9.95 | 9.95
1077 | WORSHAM BATTERY (DGR) |  | WORSHAM_BESS1 | REEVES | STORAGE | WEST | 2023 | 9.9 | 9.9
1078 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2 | 2
1079 | Operational Capacity Total (Storage) | [6 empty] | 2060.33 | 2035.05
1080 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 100 | 0
1081
1082 | Operational Resources (Storage) - Synchronized but not Approved for Commercial Operations
1083 | ANCHOR BESS U1 | 21INR0474 | ANCHOR_BESS1 | CALLAHAN | STORAGE | WEST | 2023 | 35.2 | 35.2
1084 | ANCHOR BESS U2 | 21INR0474 | ANCHOR_BESS2 | CALLAHAN | STORAGE | WEST | 2023 | 36.3 | 36.3
1085 | BLUE JAY BESS | 23INR0019 | BLUEJAY_BESS1 | GRIMES | STORAGE | NORTH | 2023 | 51.6 | 50
1086 | HIGH LONESOME BESS | 20INR0280 | HI_LONEB_BESS1 | CROCKETT | STORAGE | WEST | 2023 | 51.1 | 50
1087 | MADERO GRID U1 | 21INR0244 | MADERO_UNIT1 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100
1088 | MADERO GRID U2 (IGNACIO GRID) | 21INR0522 | MADERO_UNIT2 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100
1089 | PYRON BESS 2A | 20INR0268 | PYR_ESS2A | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1
1090 | PYRON BESS 2B | 20INR0268 | PYR_ESS2B | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1
1091 | QUEEN BESS | 20INR0281 | QUEEN_BA_BESS1 | UPTON | STORAGE | WEST | 2023 | 51.1 | 50
1092 | ROSELAND STORAGE | 22INR0280 | ROSELAND_BESS1 | FALLS | STORAGE | NORTH | 2023 | 51.6 | 50
1093 | SILICON HILL STORAGE U1 | 20INR0291 | SLCNHLS_ESS1 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50
1094 | SILICON HILL STORAGE U2 | 20INR0291 | SLCNHLS_ESS2 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50
1095 | SP TX-12B BESS | 21INR0357 | SPTX12B_BES1 | UPTON | STORAGE | WEST | 2023 | 22.7 | 22.7
1096 | TURQUOISE STORAGE | 22INR0509 | TURQBESS_BESS1 | HUNT | STORAGE | NORTH | 2023 | 196.2 | 190
1097 | VORTEX BESS | 21INR0473 | VORTEX_BESS1 | THROCKMORTON | STORAGE | WEST | 2023 | 121.8 | 121.8
1098 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Storage) | [6 empty] | 952.98 | 936.2
1099 | Storage Peak Average Capacity Percentage |  | STORAGE_SYNC_PEAK_PCT | % |  |  |  | 100 | 0
1100
1101 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0 | 0
1102
1103 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0
1104
1105 | Non-Synchronous Tie Resources
1106 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600 | 600
1107 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220 | 220
1108 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100 | 100
1109 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300 | 300
1110 | Non-Synchronous Ties Total | [6 empty] | 1220 | 1220
1111 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 100 | 59
1112
1113 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
1114 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2023 | 0 | 0
1115 | BEACHWOOD II POWER STATION (U7-U8) | 23INR0506 |  | BRAZORIA | GAS-GT | COASTAL | 2024 | 0 | 0
1116 | BROTMAN POWER STATION (U1 - U6) | 23INR0095 |  | BRAZORIA | GAS-GT | COASTAL | 2023 | 0 | 0
1117 | BROTMAN II POWER STATION (U7- U8) | 23INR0551 |  | BRAZORIA | GAS-GT | COASTAL | 2023 | 0 | 0 | New
1118 | FRONTERA ENERGY CENTER | 23INR0472 |  | HIDALGO | GAS-CC | SOUTH | 2023 | 0 | 0
1119 | MIRAGE CTG 1 | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2023 | 0 | 0
1120 | REMY JADE POWER STATION | 23INR0339 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 0 | 0
1121 | TECO GTG2 | 23INR0408 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 0 | 0 | New
1122 | Planned Thermal Resources Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 0 | 0
1123
1124 | Planned Wind Resources with Executed SGIA
1125 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2024 | 0 | 0
1126 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2024 | 0 | 0
1127 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2023 | 0 | 0
1128 | CRAWFISH | 19INR0177 |  | WHARTON | WIND-O | SOUTH | 2023 | 0 | 0
1129 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2023 | 0 | 0
1130 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2024 | 0 | 0
1131 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2024 | 0 | 0
1132 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2025 | 0 | 0
1133 | MONTE ALTO 2 WIND | 19INR0023 |  | WILLACY | WIND-C | COASTAL | 2024 | 0 | 0
1134 | MONTE ALTO I WIND | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2024 | 0 | 0
1135 | MONTGOMERY RANCH WIND | 20INR0040 |  | FOARD | WIND-O | WEST | 2023 | 0 | 0
1136 | RAY GULF WIND | 22INR0517 |  | WHARTON | WIND-O | SOUTH | 2023 | 0 | 0
1137 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2024 | 0 | 0
1138 | SHAMROCK | 22INR0502 |  | CROCKETT | WIND-O | WEST | 2024 | 0 | 0
1139 | SHEEP CREEK WIND | 21INR0325 |  | CALLAHAN | WIND-O | WEST | 2023 | 0 | 0
1140 | SIETE | 20INR0047 |  | WEBB | WIND-O | SOUTH | 2024 | 0 | 0
1141 | Planned Capacity Total (Wind) | [6 empty] | 0 | 0
1142
1143 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 0 | 0
1144 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 100 | 64
1145
1146 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0 | 0
1147 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 100 | 39
1148
1149 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 0 | 0
1150 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 100 | 39
1151
1152 | Planned Solar Resources with Executed SGIA
1153 | 7V SOLAR | 21INR0351 |  | FAYETTE | SOLAR | SOUTH | 2024 | 0 | 0
1154 | ADAMSTOWN SOLAR | 21INR0210 |  | WICHITA | SOLAR | WEST | 2025 | 0 | 0
1155 | ALILA SOLAR | 23INR0093 |  | SAN PATRICIO | SOLAR | COASTAL | 2024 | 0 | 0 | New
1156 | AMSTERDAM SOLAR | 21INR0256 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1157 | ANDROMEDA SOLAR | 22INR0412 |  | SCURRY | SOLAR | WEST | 2023 | 0 | 0
1158 | ANGELO SOLAR | 19INR0203 |  | TOM GREEN | SOLAR | WEST | 2024 | 0 | 0
1159 | ANGUS SOLAR | 20INR0035 |  | BOSQUE | SOLAR | NORTH | 2024 | 0 | 0
1160 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2024 | 0 | 0
1161 | ARROYO SOLAR | 20INR0086 |  | CAMERON | SOLAR | COASTAL | 2024 | 0 | 0
1162 | ASH CREEK SOLAR | 21INR0379 |  | HILL | SOLAR | NORTH | 2024 | 0 | 0 | New
1163 | BAKER BRANCH SOLAR | 23INR0026 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1164 | BIG ELM SOLAR | 21INR0353 |  | BELL | SOLAR | NORTH | 2024 | 0 | 0
1165 | BLUE SKY SOL | 22INR0455 |  | CROCKETT | SOLAR | WEST | 2024 | 0 | 0
1166 | BPL FILES SOLAR | 20INR0164 |  | HILL | SOLAR | NORTH | 2023 | 0 | 0
1167 | BRASS FORK SOLAR | 22INR0270 |  | HASKELL | SOLAR | WEST | 2025 | 0 | 0
1168 | BRIGHT ARROW SOLAR | 22INR0242 |  | HOPKINS | SOLAR | NORTH | 2023 | 0 | 0
1169 | BUCKEYE CORPUS FUELS SOLAR | 22INR0397 |  | NUECES | SOLAR | COASTAL | 2025 | 0 | 0
1170 | CACHENA SOLAR | 23INR0027 |  | WILSON | SOLAR | SOUTH | 2025 | 0 | 0
1171 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2025 | 0 | 0
1172 | CASTRO SOLAR | 20INR0050 |  | CASTRO | SOLAR | PANHANDLE | 2024 | 0 | 0
1173 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2024 | 0 | 0
1174 | CHILLINGHAM SOLAR | 23INR0070 |  | BELL | SOLAR | NORTH | 2023 | 0 | 0
1175 | CLUTCH CITY SOLAR | 22INR0279 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1176 | COMPADRE SOLAR | 24INR0023 |  | HILL | SOLAR | NORTH | 2024 | 0 | 0 | New
1177 | CORAL SOLAR | 22INR0295 |  | FALLS | SOLAR | NORTH | 2023 | 0 | 0
1178 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2025 | 0 | 0
1179 | COTTONWOOD BAYOU SOLAR I | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1180 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2024 | 0 | 0
1181 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2025 | 0 | 0
1182 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1183 | DAWN SOLAR | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2024 | 0 | 0
1184 | DELILAH SOLAR 1 | 22INR0202 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1185 | DELILAH SOLAR 2 | 22INR0203 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1186 | DELILAH SOLAR 3 | 23INR0042 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1187 | DELILAH SOLAR 4 | 23INR0060 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1188 | DESERT VINE SOLAR | 22INR0307 |  | ZAPATA | SOLAR | SOUTH | 2024 | 0 | 0 | New
1189 | DILEO SOLAR | 22INR0359 |  | BOSQUE | SOLAR | NORTH | 2023 | 0 | 0
1190 | DR SOLAR | 22INR0454 |  | CULBERSON | SOLAR | WEST | 2024 | 0 | 0
1191 | EASTBELL MILAM SOLAR | 21INR0203 |  | MILAM | SOLAR | SOUTH | 2023 | 0 | 0
1192 | EIFFEL SOLAR | 22INR0223 |  | LAMAR | SOLAR | NORTH | 2023 | 0 | 0
1193 | ELIZA SOLAR | 21INR0368 |  | KAUFMAN | SOLAR | NORTH | 2024 | 0 | 0
1194 | ELLIS SOLAR | 21INR0493 |  | ELLIS | SOLAR | NORTH | 2023 | 0 | 0
1195 | EQUINOX SOLAR 1 | 21INR0226 |  | STARR | SOLAR | SOUTH | 2025 | 0 | 0
1196 | ESTONIAN SOLAR FARM | 22INR0335 |  | DELTA | SOLAR | NORTH | 2024 | 0 | 0
1197 | FAGUS SOLAR PARK (MISAE SOLAR II) | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2024 | 0 | 0
1198 | FENCE POST SOLAR | 22INR0404 |  | NAVARRO | SOLAR | NORTH | 2023 | 0 | 0
1199 | FIVE WELLS SOLAR | 24INR0015 |  | BELL | SOLAR | NORTH | 2023 | 0 | 0
1200 | FRYE SOLAR | 20INR0080 |  | SWISHER | SOLAR | PANHANDLE | 2024 | 0 | 0
1201 | GALACTIC SOLAR | 23INR0144 |  | GRAYSON | SOLAR | NORTH | 2024 | 0 | 0
1202 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2023 | 0 | 0
1203 | GARCITAS CREEK SOLAR | 23INR0223 |  | JACKSON | SOLAR | SOUTH | 2024 | 0 | 0
1204 | GP SOLAR | 23INR0045 |  | VAN ZANDT | SOLAR | NORTH | 2024 | 0 | 0
1205 | GRANDSLAM SOLAR | 21INR0391 |  | ATASCOSA | SOLAR | SOUTH | 2024 | 0 | 0
1206 | GRANSOLAR TEXAS ONE | 22INR0511 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0
1207 | GREATER BRYANT G SOLAR | 23INR0300 |  | MIDLAND | SOLAR | WEST | 2024 | 0 | 0
1208 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2024 | 0 | 0
1209 | GREYHOUND SOLAR | 21INR0268 |  | ECTOR | SOLAR | WEST | 2025 | 0 | 0
1210 | GRIMES COUNTY SOLAR | 23INR0160 |  | GRIMES | SOLAR | NORTH | 2024 | 0 | 0
1211 | GULF STAR SOLAR SLF (G-STAR SOLAR) | 23INR0111 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1212 | HALO SOLAR | 21INR0304 |  | BELL | SOLAR | NORTH | 2023 | 0 | 0
1213 | HAYHURST TEXAS SOLAR | 22INR0363 |  | CULBERSON | SOLAR | WEST | 2023 | 0 | 0
1214 | HOPKINS SOLAR | 20INR0210 |  | HOPKINS | SOLAR | NORTH | 2023 | 0 | 0
1215 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2023 | 0 | 0
1216 | HORNET SOLAR | 23INR0021 |  | SWISHER | SOLAR | PANHANDLE | 2024 | 0 | 0
1217 | HOWLE SOLAR | 20INR0075 |  | ELLIS | SOLAR | NORTH | 2024 | 0 | 0
1218 | HOYTE SOLAR | 23INR0235 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0
1219 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2023 | 0 | 0
1220 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2025 | 0 | 0
1221 | JACKALOPE SOLAR | 23INR0180 |  | SAN PATRICIO | SOLAR | COASTAL | 2024 | 0 | 0
1222 | JADE SOLAR | 22INR0360 |  | SCURRY | SOLAR | WEST | 2023 | 0 | 0
1223 | JUNGMANN SOLAR | 22INR0356 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0
1224 | LAVACA BAY SOLAR | 23INR0084 |  | MATAGORDA | SOLAR | COASTAL | 2024 | 0 | 0
1225 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1226 | LUNIS CREEK SOLAR 1 | 21INR0344 |  | JACKSON | SOLAR | SOUTH | 2024 | 0 | 0
1227 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1228 | MARKUM SOLAR | 20INR0230 |  | MCLENNAN | SOLAR | NORTH | 2024 | 0 | 0
1229 | MATAGORDA SOLAR | 22INR0342 |  | MATAGORDA | SOLAR | COASTAL | 2023 | 0 | 0
1230 | MERCURY I SOLAR | 21INR0257 |  | HILL | SOLAR | NORTH | 2024 | 0 | 0
1231 | MERCURY II SOLAR | 23INR0153 |  | HILL | SOLAR | NORTH | 2024 | 0 | 0
1232 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2024 | 0 | 0
1233 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2025 | 0 | 0
1234 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2025 | 0 | 0
1235 | NEPTUNE SOLAR | 21INR0499 |  | JACKSON | SOLAR | SOUTH | 2023 | 0 | 0
1236 | NORIA SOLAR DCC | 23INR0061 |  | NUECES | SOLAR | COASTAL | 2024 | 0 | 0
1237 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2024 | 0 | 0
1238 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2025 | 0 | 0
1239 | ORIANA SOLAR | 24INR0093 |  | VICTORIA | SOLAR | SOUTH | 2024 | 0 | 0 | New
1240 | OUTPOST SOLAR | 23INR0007 |  | WEBB | SOLAR | SOUTH | 2024 | 0 | 0
1241 | OYSTERCATCHER SOLAR | 21INR0362 |  | ELLIS | SOLAR | NORTH | 2024 | 0 | 0
1242 | PARLIAMENT SOLAR | 23INR0044 |  | WALLER | SOLAR | HOUSTON | 2023 | 0 | 0
1243 | PEREGRINE SOLAR | 22INR0283 |  | GOLIAD | SOLAR | SOUTH | 2024 | 0 | 0
1244 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2024 | 0 | 0
1245 | PINK SOLAR | 22INR0281 |  | HUNT | SOLAR | NORTH | 2023 | 0 | 0
1246 | PITTS DUDIK SOLAR | 20INR0074 |  | HILL | SOLAR | NORTH | 2023 | 0 | 0
1247 | PORTER SOLAR | 21INR0458 |  | DENTON | SOLAR | NORTH | 2024 | 0 | 0
1248 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2024 | 0 | 0
1249 | REDONDA SOLAR | 23INR0162 |  | ZAPATA | SOLAR | SOUTH | 2024 | 0 | 0
1250 | RED-TAILED HAWK SOLAR | 21INR0389 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1251 | ROCINANTE SOLAR | 23INR0231 |  | GONZALES | SOLAR | SOUTH | 2024 | 0 | 0
1252 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2024 | 0 | 0
1253 | ROWLAND SOLAR II | 22INR0482 |  | FORT BEND | SOLAR | HOUSTON | 2024 | 0 | 0
1254 | SAMSON SOLAR 2 | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1255 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2023 | 0 | 0
1256 | SCHOOLHOUSE SOLAR | 22INR0211 |  | LEE | SOLAR | SOUTH | 2025 | 0 | 0
1257 | SECOND DIVISION SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1258 | SHAULA I SOLAR | 22INR0251 |  | DEWITT | SOLAR | SOUTH | 2024 | 0 | 0
1259 | SHAULA II SOLAR | 22INR0267 |  | DEWITT | SOLAR | SOUTH | 2024 | 0 | 0
1260 | SIGNAL SOLAR | 20INR0208 |  | HUNT | SOLAR | NORTH | 2024 | 0 | 0
1261 | SODA LAKE SOLAR 1 SLF | 23INR0080 |  | CRANE | SOLAR | WEST | 2023 | 0 | 0
1262 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2024 | 0 | 0
1263 | SP JAGUAR SOLAR | 24INR0038 |  | MCLENNAN | SOLAR | NORTH | 2024 | 0 | 0 | New
1264 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2025 | 0 | 0
1265 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2023 | 0 | 0
1266 | STAMPEDE SOLAR | 22INR0409 |  | HOPKINS | SOLAR | NORTH | 2023 | 0 | 0
1267 | STARLING SOLAR | 23INR0035 |  | GONZALES | SOLAR | SOUTH | 2024 | 0 | 0
1268 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2024 | 0 | 0
1269 | SUNRAY | 21INR0395 |  | UVALDE | SOLAR | SOUTH | 2024 | 0 | 0
1270 | TALITHA SOLAR | 21INR0393 |  | JIM WELLS | SOLAR | SOUTH | 2024 | 0 | 0
1271 | TANGLEWOOD SOLAR | 23INR0054 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1272 | TAVNER (FORT BEND SOLAR) | 18INR0053 |  | FORT BEND | SOLAR | HOUSTON | 2023 | 0 | 0
1273 | TEXANA SOLAR | 18INR0058 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1274 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2023 | 0 | 0
1275 | TEXAS SOLAR NOVA 2 | 20INR0269 |  | KENT | SOLAR | WEST | 2023 | 0 | 0
1276 | TIERRA BONITA SOLAR | 21INR0424 |  | PECOS | SOLAR | WEST | 2024 | 0 | 0
1277 | TRES BAHIAS SOLAR | 20INR0266 |  | CALHOUN | SOLAR | COASTAL | 2023 | 0 | 0
1278 | TROJAN SOLAR | 23INR0296 |  | COOKE | SOLAR | NORTH | 2024 | 0 | 0
1279 | TULSITA SOLAR | 21INR0223 |  | GOLIAD | SOLAR | SOUTH | 2024 | 0 | 0
1280 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1281 | ULYSSES SOLAR | 21INR0253 |  | COKE | SOLAR | WEST | 2024 | 0 | 0
1282 | UMBRA (STOCKYARD) SOLAR | 23INR0155 |  | FRANKLIN | SOLAR | NORTH | 2024 | 0 | 0
1283 | XE MURAT SOLAR | 22INR0354 |  | HARRIS | SOLAR | HOUSTON | 2024 | 0 | 0
1284 | ZIER SOLAR | 21INR0019 |  | KINNEY | SOLAR | SOUTH | 2023 | 0 | 0
1285 | Planned Capacity Total (Solar) | [6 empty] | 0 | 0
1286 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 100 | 72
1287
1288 | Planned Storage Resources with Executed SGIA
1289 | ADAMSTOWN STORAGE | 21INR0209 |  | WICHITA | STORAGE | WEST | 2025 | 0 | 0
1290 | AEP_N_ALAMO_LD02(SMT ALAMO) | 23INR0477 |  | HIDALGO | STORAGE | SOUTH | 2023 | 0 | 0 | New
1291 | AL PASTOR BESS | 24INR0273 |  | DAWSON | STORAGE | WEST | 2024 | 0 | 0 | New
1292 | AMSTERDAM STORAGE | 22INR0417 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 0 | 0
1293 | ANEMOI ENERGY STORAGE | 23INR0369 |  | HIDALGO | STORAGE | SOUTH | 2023 | 0 | 0
1294 | ARROYO STORAGE SLF | 24INR0306 |  | CAMERON | STORAGE | COASTAL | 2024 | 0 | 0
1295 | BIG STAR STORAGE | 21INR0469 |  | BASTROP | STORAGE | SOUTH | 2023 | 0 | 0
1296 | BOCO BESS | 23INR0470 |  | BORDEN | STORAGE | WEST | 2023 | 0 | 0 | New
1297 | BORDERTOWN BESS | 23INR0354 |  | STARR | STORAGE | SOUTH | 2025 | 0 | 0
1298 | BRAZOS BEND BESS | 23INR0363 |  | FORT BEND | STORAGE | HOUSTON | 2024 | 0 | 0
1299 | BRIGHT ARROW STORAGE | 22INR0302 |  | HOPKINS | STORAGE | NORTH | 2023 | 0 | 0
1300 | BRP ANTLIA BESS | 22INR0349 |  | VAL VERDE | STORAGE | WEST | 2023 | 0 | 0
1301 | BRP AVILA BESS | 23INR0287 |  | PECOS | STORAGE | WEST | 2023 | 0 | 0 | New
1302 | BRP CACHI BESS | 22INR0388 |  | GUADALUPE | STORAGE | SOUTH | 2023 | 0 | 0
1303 | BRP CARINA BESS | 22INR0353 |  | NUECES | STORAGE | COASTAL | 2023 | 0 | 0
1304 | BRP DICKENS BESS | 22INR0325 |  | DICKENS | STORAGE | PANHANDLE | 2023 | 0 | 0
1305 | BRP HYDRA BESS | 22INR0372 |  | PECOS | STORAGE | WEST | 2023 | 0 | 0
1306 | BRP LIBRA BESS | 22INR0366 |  | GUADALUPE | STORAGE | SOUTH | 2023 | 0 | 0
1307 | BRP PALEO BESS | 22INR0322 |  | HALE | STORAGE | PANHANDLE | 2024 | 0 | 0
1308 | BRP PAVO BESS | 22INR0384 |  | PECOS | STORAGE | WEST | 2024 | 0 | 0
1309 | BRP TORTOLAS BESS | 23INR0072 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 0 | 0
1310 | BRP ZEYA BESS | 23INR0290 |  | GALVESTON | STORAGE | HOUSTON | 2023 | 0 | 0 | New
1311 | CALLISTO I ENERGY CENTER | 22INR0490 |  | HARRIS | STORAGE | HOUSTON | 2024 | 0 | 0
1312 | CHILLINGHAM STORAGE | 23INR0079 |  | BELL | STORAGE | NORTH | 2023 | 0 | 0
1313 | CITADEL BESS | 24INR0147 |  | HARRIS | STORAGE | HOUSTON | 2024 | 0 | 0
1314 | CORAL STORAGE | 23INR0124 |  | FALLS | STORAGE | NORTH | 2023 | 0 | 0
1315 | COTTONWOOD BAYOU STORAGE | 21INR0443 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 0 | 0
1316 | DAMON STORAGE | 23INR0523 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 0 | 0 | New
1317 | DANISH FIELDS STORAGE | 21INR0450 |  | WHARTON | STORAGE | SOUTH | 2023 | 0 | 0
1318 | DIBOLL BESS (DGR) | 23INR0522 |  | ANGELINA | STORAGE | NORTH | 2023 | 0 | 0
1319 | DONEGAL BESS | 23INR0103 |  | DICKENS | STORAGE | PANHANDLE | 2024 | 0 | 0
1320 | EBONY ENERGY STORAGE | 23INR0154 |  | COMAL | STORAGE | SOUTH | 2024 | 0 | 0
1321 | ELIZA STORAGE | 22INR0260 |  | KAUFMAN | STORAGE | NORTH | 2024 | 0 | 0
1322 | ESTONIAN ENERGY STORAGE | 22INR0336 |  | DELTA | STORAGE | NORTH | 2023 | 0 | 0
1323 | EVAL STORAGE | 22INR0401 |  | CAMERON | STORAGE | COASTAL | 2024 | 0 | 0
1324 | FENCE POST BESS | 22INR0405 |  | NAVARRO | STORAGE | NORTH | 2023 | 0 | 0
1325 | FERDINAND GRID BESS | 22INR0422 |  | BEXAR | STORAGE | SOUTH | 2025 | 0 | 0 | New
1326 | FIVE WELLS STORAGE | 23INR0159 |  | BELL | STORAGE | NORTH | 2023 | 0 | 0 | New
1327 | GIGA TEXAS ENERGY STORAGE | 23INR0239 |  | TRAVIS | STORAGE | SOUTH | 2023 | 0 | 0
1328 | GOMEZ BESS (DGR) | 23INR0519 |  | PECOS | STORAGE | WEST | 2023 | 0 | 0
1329 | GREAT KISKADEE STORAGE | 23INR0166 |  | HIDALGO | STORAGE | SOUTH | 2024 | 0 | 0
1330 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2024 | 0 | 0
1331 | GRIZZLY RIDGE BESS (DGR) | 22INR0596 |  | HAMILTON | STORAGE | NORTH | 2023 | 0 | 0
1332 | GUAJILLO ENERGY STORAGE | 23INR0343 |  | WEBB | STORAGE | SOUTH | 2024 | 0 | 0
1333 | HOUSE MOUNTAIN 2 BATT | 22INR0485 |  | BREWSTER | STORAGE | WEST | 2023 | 0 | 0
1334 | HUMMINGBIRD STORAGE | 22INR0327 |  | DENTON | STORAGE | NORTH | 2023 | 0 | 0
1335 | INERTIA BESS | 22INR0328 |  | HASKELL | STORAGE | WEST | 2023 | 0 | 0
1336 | INERTIA BESS 2 | 22INR0375 |  | HASKELL | STORAGE | WEST | 2025 | 0 | 0
1337 | IRON BELT ENERGY STORAGE | 25INR0208 |  | DAWSON | STORAGE | WEST | 2025 | 0 | 0 | New
1338 | JUNCTION BESS (DGR) | 23INR0521 |  | KIMBLE | STORAGE | SOUTH | 2023 | 0 | 0
1339 | LARKSPUR ENERGY STORAGE | 23INR0340 |  | UPTON | STORAGE | WEST | 2025 | 0 | 0
1340 | LIMOUSIN OAK STORAGE | 22INR0338 |  | GRIMES | STORAGE | NORTH | 2023 | 0 | 0
1341 | MUSTANG CREEK STORAGE | 21INR0484 |  | JACKSON | STORAGE | SOUTH | 2023 | 0 | 0
1342 | MYRTLE STORAGE | 21INR0442 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 0 | 0 | New
1343 | NORIA STORAGE | 23INR0062 |  | NUECES | STORAGE | COASTAL | 2024 | 0 | 0
1344 | OLNEY BESS | 22INR0603 |  | YOUNG | STORAGE | WEST | 2023 | 0 | 0 | New
1345 | ORIANA BESS | 24INR0109 |  | VICTORIA | STORAGE | SOUTH | 2024 | 0 | 0 | New
1346 | PADUA GRID BESS | 22INR0368 |  | BEXAR | STORAGE | SOUTH | 2024 | 0 | 0
1347 | RAMSEY STORAGE | 21INR0505 |  | WHARTON | STORAGE | SOUTH | 2024 | 0 | 0
1348 | RED HOLLY STORAGE | 21INR0033 |  | DAWSON | STORAGE | WEST | 2024 | 0 | 0
1349 | RIVER VALLEY STORAGE 1 | 20INR0290 |  | WILLIAMSON | STORAGE | SOUTH | 2023 | 0 | 0
1350 | RIVER VALLEY STORAGE 2 | 20INR0293 |  | WILLIAMSON | STORAGE | SOUTH | 2023 | 0 | 0
1351 | ROCINANTE BESS | 23INR0232 |  | GONZALES | STORAGE | SOUTH | 2024 | 0 | 0
1352 | RODEO RANCH ENERGY STORAGE | 23INR0371 |  | REEVES | STORAGE | WEST | 2023 | 0 | 0
1353 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2024 | 0 | 0
1354 | SABAL STORAGE | 22INR0398 |  | CAMERON | STORAGE | COASTAL | 2023 | 0 | 0
1355 | SOHO BESS | 23INR0419 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 0 | 0 | New
1356 | SOWERS STORAGE | 22INR0552 |  | KAUFMAN | STORAGE | NORTH | 2024 | 0 | 0
1357 | SP JAGUAR BESS | 24INR0039 |  | MCLENNAN | STORAGE | NORTH | 2024 | 0 | 0 | New
1358 | ST. GALL I ENERGY STORAGE | 22INR0524 |  | PECOS | STORAGE | WEST | 2023 | 0 | 0 | New
1359 | STAMPEDE BESS | 22INR0410 |  | HOPKINS | STORAGE | NORTH | 2023 | 0 | 0
1360 | STOCKYARD GRID BATT | 21INR0492 |  | TARRANT | STORAGE | NORTH | 2023 | 0 | 0
1361 | SUN VALLEY BESS | 22INR0429 |  | HILL | STORAGE | NORTH | 2023 | 0 | 0 | New
1362 | TALITHA BESS | 23INR0331 |  | JIM WELLS | STORAGE | SOUTH | 2024 | 0 | 0 | New
1363 | TANZANITE STORAGE | 22INR0549 |  | HENDERSON | STORAGE | NORTH | 2024 | 0 | 0
1364 | TIDWELL PRAIRIE STORAGE 1 | 21INR0517 |  | ROBERTSON | STORAGE | NORTH | 2024 | 0 | 0
1365 | TIMBERWOLF BESS 2 | 22INR0495 |  | CRANE | STORAGE | WEST | 2023 | 0 | 0
1366 | UMBRA (STOCKYARD) BESS | 23INR0156 |  | FRANKLIN | STORAGE | NORTH | 2024 | 0 | 0
1367 | WOLF TANK STORAGE | 22INR0551 |  | WEBB | STORAGE | SOUTH | 2023 | 0 | 0
1368 | ZIER STORAGE | 21INR0027 |  | KINNEY | STORAGE | SOUTH | 2023 | 0 | 0
1369 | SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * | [6 empty] | 0 | 0
1370 | Planned Capacity Total (Storage) | [6 empty] | 0 | 0
1371 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 100 | 0
1372
1373 | Inactive Planned Resources
1374 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60 | 60
1375 | DONEGAL SOLAR | 23INR0089 |  | DICKENS | SOLAR | PANHANDLE | 2024 | 0 | 0
1376 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2026 | 0 | 0
1377 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1
1378 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1
1379 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5 | 152.5
1380 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150 | 150
1381 | PLEASANTON BESS (DGR) | 23INR0520 |  | ATASCOSA | STORAGE | SOUTH | 2023 | 9.9 | 9.9
1382 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2025 | 0 | 0
1383 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2024 | 0 | 0
1384 | Inactive Planned Capacity Total | [6 empty] | 872.6 | 872.6
1385
1386 | Seasonal Mothballed Resources
1387 | MOUNTAIN CREEK STG 8 (AS OF 3/1/2023, AVAILABLE 6/1 THROUGH 9/30) |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568 | 568
1388 | POWERLANE PLANT STG 1 (AS OF 10/1/2022, AVAILABLE 6/1 THROUGH 9/30) |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 18.75 | 17.5
1389 | SPENCER STG U4 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 61 | 57
1390 | SPENCER STG U5 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 65 | 61
1391 | Total Seasonal Mothballed Capacity | [6 empty] | 712.75 | 703.5
1392
1393 | Mothballed Resources
1394 | RAY OLINGER STG 1 (AS OF 4/5/22) |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78 | 78
1395 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 415 | 420
1396 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 415 | 420
1397 | Total Mothballed Capacity | [6 empty] | 908 | 918
1398
1399 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
1400 | Total Retiring Capacity | [6 empty] | 0 | 0
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide Ancillary Services rather than sustained capacity available to meet system peak loads.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Reources Services (RIOO-RS) system.
Note on J391: W A PARISH U8 (WAP_WAP_G8), -610 MW, on extended outage from 5/8/22 to 5/7/23
Note on J431: Extended outages: GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE (3.6 MW) and 2.4 MW of the 4.8 MW GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP Hydro unit.
Note on J469: The methodology for calculating the capacity contribution is outlined on the Background tab.

## Scenario Assumption Details
| Base & Moderate Risk Scenarios | Extreme Risk Scenarios
Adjusted Peak Load Forecast | Based on average weather conditions from 2007 – 2021 at the time of the April and May peaks. Data for spring 2021 is not used in the forecast model because the model estimation process depends on using full calendar-year data. These baseline forecasts are adjusted downwards to account for peak load reductions from rooftop solar installations that are not already accounted for in the baseline forecasts. The rooftop solar load reductions for March/April and May are 438 MW and 538 MW, respectively.
April High Load Adjustment | Based on the average weather conditions at the time of a May peak meaning it assumes average May peak weather occuring in April. | Based on the 90th percentile weather conditions at the time of a May peak; in other words, that 90th percentile May peak weather conditions occur in April. Note that for the 2022 Spring SARA, ERCOT used 90th percentile weather occurring at the time of the April peak. The higher scenario amount assumed for this SARA recognizes that Texas is recently experiencing extreme weather more frequently than represented in the historical data.
May High Load Adjustment | Based on the average weather conditions at the time of a June peak meaning it assumes average June peak weather occuring in May. | Based on the 90th percentile weather conditions at the time of a June peak; in other words, that 90th percentile June peak weather conditions occur in May. Note that for the 2022 Spring SARA, ERCOT used 90th percentile weather occurring at the time of the May peak. The higher scenario amount assumed for this SARA recognizes that Texas is recently experiencing extreme weather more frequently than represented in the historical data.
Typical Planned Outages, Thermal | Based on the historical average of planned outages for March through May weekdays, hours ending 15 - 22 (3 pm - 10 pm), for the last three spring seasons excluding 2021 (2019, 2020, 2022). Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages that extended into the spring season. Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
Typical Unplanned Outages, Thermal | Based on historical average of Unplanned outages for March through May weekdays, hours ending 15 - 22 (3 pm - 10 pm), for the last three spring seasons excluding 2021 (2019, 2020, 2022). Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages that extended into the spring season. Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
Unplanned Outage Adjustments, Thermal | Based on the 95th percentile of historical Unplanned outages for March through May weekdays, hours ending 15 - 22 (3 pm - 10 pm), for last five spring seasons excluding 2021 (2017 -2022); the adjustment is the 95th percentile value, 18,546 MW, less the typical Unplanned outage amount of 13,605 MW. The outages include those from Private Use Network (PUN) generators. See the Background tab for more information on the treatment of PUN capacity. Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages in this calculation. | Based on the Maximum historical Unplanned outages for March through May weekdays, hours ending 15 - 22 (3 pm - 10 pm), for the last five spring seasons excluding 2021 (2017 -2022); the adjustment is the Maximum value of 21,001 MW, less the typical Unplanned outage amount of 13,605 MW. The outages include those from PUN generators. See the Background tab for more information on the treatment of PUN capacity. Spring 2021 outages were excluded to avoid including Winter Storm Uri-related outages that extended into the spring season.
Wind Output Adjustments | The adjustments are based on the 10th percentile of hourly wind capacity factors (output as a percentage of installed capacity) for the daily period hour-ending 13 - 20 (1 pm - 8 pm). The capacity factors are derived from annual hourly simulated wind output profiles for the period 1980 - 2021. The profiles reflect hourly weather conditions for each of the 42 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the Final 2021 Summer SARA. For the March/April period, hourly capacity factors are developed for all days in March and April, resulting in 17,934 capacity factors from which the 10th percentile is computed (42 profiles x 61 days x 7 hours). For the May period, hourly capacity factors are developed for all days in May, resulting in 9,114 capacity factors from which the 5th percentile is computed (42 profiles x 31 days x 7 hours). For the March/April period, this low wind output level is 5,277 MW, while the low output level for May is 4,735 MW. The adjustments are the Peak Average Capacity Contribution, 15,637 MW, less 5,277 MW and 4,735 MW, respectively. The methodology report for profile development is available at: https://www.ercot.com/files/docs/2021/12/07/Report_ERCOT_1980-2020_WindSolarDGPVGenProfiles.pdf | The adjustments are based on the minimum wind capacity factors (output as a percentage of installed capacity) for the daily period hour-ending 13 - 20 (1 pm - 9 pm). The capacity factors are derived from annual hourly simulated wind output profiles for the period 1980 - 2021 as described to the left. For the March/April period, this extreme-low wind output level is 107 MW, while the extreme-low output level for May is 364 MW. The adjustments are the Peak Average Capacity Contribution, 15,637 MW, less 107 MW and 364 MW, respectively. Note that a scenario with a combined extreme peak load and extreme-low renewables output is not provided because an extreme peak load is associated with high solar output due to minimal cloud cover serving as a driver for both system conditions.
Solar Output Adjustments | The adjustments are based on the 10th percentile of hourly solar photovoltaic capacity factors (output as a percentage of installed capacity) for the daily period hour-ending 13 - 18 (1 pm - 7 pm). The capacity factors are derived from annual hourly simulated solar output profiles for the period 1980 - 2021 as described above. For the March/April period, this low solar PV output level is 5,123 MW, while the low output level for May is 8,036 MW. The adjustments are the Peak Average Capacity Contribution, 10,687 MW, less 5,123 MW and 8,036 MW respectively. | N/A
Emergency Resources Deployed by ERCOT prior to EEA Declaration | An amount is only shown if Capacity Available for Operating Reserves, line item [g], is at or below 3,000 MW. Consists of the sum of (1) expected Emergency Response Service (1,050 MW) and TDSP Distribution Voltage Reduction (562 MW), and (2) the expected peak consumption by operational LFLs at co-located and standalone sites (333 MW and 170 MW respectively), which is assumed to be available for curtailment based on ERCOT requests to address an imminent capacity reserve shortage. The ERS, Distribution Voltage Reduction, and co-located LFL amounts reflect a 2% gross-up to account for avoided transmission losses. Other resources that may be available, but not factored into this estimate, include voluntary customer Demand Response (including customer installation of backup generators), switchable generation resources currently serving the Eastern Interconnection, and additional DC tie imports.
Emergency Resources deployed by ERCOT | An amount is only shown if the sum of Capacity Available for Operating Reserves (line item [f]) and line item [g] is at or below 2,300 MW. Consists of the sum of expected Load Resources Available for Responsive Reserves for the spring season (1,377 MW). This amount reflects a 2% gross-up to account for avoided transmission losses. Other resources that may be available include voluntary customer Demand Response (including customer installation of backup generators), switchable generation resources currently serving the Eastern Interconnection, and additional DC tie imports provided via an emergency support request.

## Background
Release Date: March 8, 2023
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (for example, an anticipated common-mode event such as a system-wide heat wave) which can be used to consider the range of resource adequacy outcomes in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses operating reserve thresholds of 2,300 and 1,000 MW, respectively, to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) and Level 3 (EEA3) may be triggered during the time of the forecasted seasonal peak load. These threshold levels are intended to be roughly analogous to the 2,300 and 1,000 MW Physical Responsive Capability (PRC) thresholds for EEA1 and EEA3 with controlled outages ordered by ERCOT, respectively. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 and 1,000 MW reserve capacity thresholds are reasonable indicators for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variations in these parameters are based on historic ranges of the parameter values, known changes expected in the near-term, or reasonable assumptions regarding potential future events.
Thermal Outage Accounting
Directly comparing SARA thermal unplanned (previously "forced") outage scenario capacity with outage amounts listed in ERCOT outage reports — such as the Unplanned Resource Outages Report — will yield misleading results. The reason is that the SARA report consists of multiple resource availability line items, and thermal outages for certain resource types are reflected elsewhere in the SARA reports rather than the thermal outage scenario line items. As a result, the SARA thermal outage scenario amounts will always be less than what is typically shown in other outage reports. The main differences include the following:
• Outages for Private Use Network (PUN) generators are incorporated in the line item called “Capacity from Private Use Networks.” This is an aggregate estimate of the amount of capacity available for the ERCOT grid during the highest 20 seasonal hourly demands for the last three years and incorporates average generator outage amounts over those hourly intervals. Additionally, the aggregate estimate reflects PUN owner decisions to supply power to their industrial loads versus export to the grid. PUN outages are thus already reflected in the SARA available resource capacity estimate.
• Extended outages are reported in the SARA Capacities tab in a line item called “Operational Capacity Unavailable due to Extended Outage or Derate.” Extended Outages are those forced outages that are expected to last a minimum of 180 days as reported by the resource owner via submission of a Notice of Suspension of Operations (NSO) form. These outages are thus already reflected in the SARA available resource capacity estimate.
• The capacity of Switchable Generation Resources (SWGRs) that are assumed to serve a neighboring grid for the season is deducted from available resource capacity, so outages associated with these SWGRs are not reflected anywhere in the SARA report.
To more closely align the SARA with other outage reports based on ERCOT Outage Scheduler data, a modification was made to the treatment of outages classified as Unavoidable Extensions, or UEs. UEs are defined as "a Planned or Maintenance Outage that is not completed within the ERCOT-approved timeframe and extended." For past SARA reports, if the original outage was classified as Planned in the Outage Scheduler, then the UE would continue to be classified as Planned. If the original outage was classified as Forced, then the UE would continue to be classified as Forced. In contrast, for other ERCOT outage reports, UE outages are all classified as Forced (Unplanned). SARA reports now treat all UEs as Unplanned. While this category change does not impact the total base outage amount, it does increase the high and extreme unplanned thermal adjustments used in several risk scenarios.
Operational Co-located Resources with Large Loads
Due to a new influx of Large Flexible Loads (LFLs) co-located with operational generation resources, an interim solution was implemented to better account for the peak contributions of these resources. The new interim methodology utilizes the 20 hours over each of the past three years with the lowest average Physical Responsive Capability. The methodology compares historical load zone prices to an ERCOT determined (and industry backed) estimate of the bitcoin mining breakeven cost. This breakeven cost was estimated at $86/MWh and is based on the economics of an Antminer S19 bitcoin mining rig for the average of January 2023. If the historical load zone price for the generating unit's respective load zone was below the breakeven threshold then the generator's peak spring capacity contribution was netted with the total expected co-located load at the site according to internal tracking of LFL projects. If the historical load zone price was greater than the breakeven threshold then the co-located load was assumed to be fully curtailed and consuming only 3% of the load's maximum capability. The 3% assumption accounts for the idle power draw of ASIC miners and necessary auxiliary cooling on site. In the case of a generation resource outage, the co-located load was assumed to be a net consumer on the grid if the price was below the cutoff. However, instances of these sites behaving as net loads are captured in the load forecast and is thus not accounted for in the co-located peak contribution calculation as to avoid double counting. In cases of a co-located site acting as a net load for any hour analyzed within the calculation procedure, the peak contribution of the generation resource was recorded as 0 MW. The estimated contributions for each co-located resource were summed for all 20 hours and then averaged to calculate the total contribution. This value is reflected in the Operational Co-located Resources with Large Flexible Loads (LFLs) item on the Spring Capacities tab (cell J469).