## Slide 1
Review of Potential Price Correction for Feb. 5, 2023 – Generic Transmission Constraint (GTC) Error Impacting Real-Time
David Maggio
Sr. Director, Market Design & Analytics
Technical Advisory Committee (TAC)
March 21, 2023

## Slide 2: Background
On February 7, 2023, ERCOT discovered an error related to the value of the Valley Export GTC (VALEXP) flow that was being passed to the RTM for Operating Days February 5 and 6, 2023.
The VALEXP definition (interface constraint) consists of six transmission lines in the region (three 345 kV transmission lines and three 138 kV transmission lines).
The constraint represents a stability limit for transient voltage instability associated with large power exports out of the Greater Valley area.
Limits on the amount of power that can flow across this interface constraint are highly dependent on transmission outage conditions with limits for the GTC ranging between 145 and 705 MW.

## Slide 3: Background
A typical thermal constraint is non-directional, meaning flow on the transmission element must be managed in either direction.
  The Transmission Constraint Manager (TCM) sends the absolute value of the flow to the Security-Constrained Economic Dispatch (SCED) engine and the sign of the shift factors are adjusted to account for direction.
GTCs and the associated phenomenon that result in these transmission limitations are directional in nature.
  The constraint should only be limiting when the flow is in a specific direction and signs of the shift factors are not adjusted.
However, TCM was not designed to recognize this distinction in constraint type when providing flow information and was sending the absolute value for GTCs.
  There has been a dependency on these constraints being deactivated from consideration in SCED before the flow reversed direction.
Station A
Station B
Thermal constraint: managed in both directions
GTC: managed in a single direction

## Slide 4: Background
On the given Operating Days, there were specific outages that resulted in the limits for the VALEXP GTC being on the lower end of the possible range. This lower limit combined with wind conditions in the region resulted in increased potential for the constraint flow to change directions prior to it being deactivated from consideration in SCED.
For certain intervals on these days, the misalignment between constraint shift factors and constraint flow for the GTC resulted in incorrect congestion management including incorrect prices in Real-Time.
Upon learning of the issue, ERCOT issued an Operations Message on the afternoon of February 7, 2023, noting that there was an investigation of SCED prices underway.

## Slide 5: Background
Upon completion of the investigation, an updated message was provided on the afternoon of February 8, 2023. ERCOT found that both Operating Days met the initial criteria for price correction, according to Protocols Section 6.3(5).
However, because the initial deadline for February 5, 2023, had passed, further analysis was performed and it was determined that the Settlements impact met the criteria for seeking review by the ERCOT Board of Directors (Board), as specified in Protocol Section 6.3(7)(b).
  Protocol Section 6.3(7)(b) defines the two possible criteria for seeking Board review as the impact to any single Counter Party RTM Settlement Statement being:
    2% and also greater than $20,000; or
    20% and also greater than $2,000
Operating Day | Counter-Parties meeting criteria in Protocol Section 6.3(7)(b)(i)* | Counter-Parties meeting criteria in Protocol Section 6.3(7)(b)(ii)*
02/05/2023 | 2 | 3

## Slide 6: Background
ERCOT issued Market Notice M-A022123-01 on February 21, 2023, notifying Market Participants that ERCOT would seek correction of Real-Time prices for February 5, 2023, in accordance with Protocol Section 6.3(7)(a).
A fix was implemented on March 2, 2023, that allows TCM to pass a negative flow to SCED for GTCs, ensuring that the flow is managed in the correct direction and that shift factors and flow information for the constraint are in alignment for the SCED engine.
  The flow for all thermal constraints are still passed as an absolute value.

## Slide 7: Estimated Settlement Impacts
Operating Day | Increase in Statement Charges Due to ERCOT | 
2/5/2023 | $83,356 | 2.1%
A positive value in this table represents an increase in statement charge amount due to ERCOT.
The percent amount is the absolute value of the percent of impact to the previously settled net amount due to/from ERCOT.
Operating Day | Absolute Value Impact to Counter-Parties |  | 
 | Maximum Amount | Maximum Percentage for Criteria (i)* | Maximum Percentage for Criteria (ii)**
2/5/2023 | $60,156 | 16.5% | 33.1%
* The maximum of percentage change to any single Counter party with impact more than $20,000.
** The maximum of percentage change to any single Counter party with impact more than $2,000.

## Slide 8: Next Steps
ERCOT will request that the Board review and approve the correction of Real-Time prices for Operating Day February 5, 2023, at their next meeting in April. A presentation will be provided to the Reliability and Markets Committee during their meeting on April 17, 2023.