## Slide 1
Mid-Term Load Forecast
Winter Storm Elliott Review
Jeff Billo
Operations Planning
TAC
March 21, 2023

## Slide 2: Background: MTLF Models
The Mid-Term Load Forecast (MTLF) is a 168-hour, forward-looking operational forecast
ERCOT uses two independent forecasting systems for the MTLF
  Internally-developed forecast using Itron software (creates the E, E1, E2, and E3 forecasts)
  Vendor-provided forecast through the legacy Areva system (GE) (creates the A3, A6, and M forecasts)
  Residing on separate computer systems provides redundancy in case one system is unavailable
The internally-developed forecast has more flexibility to select between different weather models

## Slide 3: MTLF Performance for December 23, 2022
Chart: ERCOT Forecasts for 12/23 created 12/17
A3 | 57628.5195 | 56905.1172 | 56610.9375 | 57059.6172 | 57875.0859 | 59866.4844 | 62824.8438 | 65335.9102 | 67237.8984 | 68318.5547 | 67902.9688 | 66703.6562 | 64484.457 | 62797.6211 | 60537.9844 | 59329.3633 | 59073.0625 | 60677.8438 | 62419.7422 | 62679.8164 | 62338.0508 | 61831.0117 | 60136.9844 | 58353.7969
A6 | 56957.5586 | 56071.1211 | 55530.0117 | 55877.1641 | 56549.5078 | 58858.1797 | 62179.0742 | 64290.2266 | 65134.4141 | 66090.2812 | 66198.8281 | 65449.4883 | 63363.5312 | 61786.1641 | 60102.4062 | 59393.7695 | 59058.9453 | 60516.4883 | 61555.4141 | 61380.1172 | 60840.5117 | 59717.4688 | 58219.8867 | 56563.1445
E | 50198.1016 | 49148.5 | 48065.8008 | 48036.8008 | 48081.3008 | 48306.3008 | 48494.6992 | 48503.1016 | 48250.3008 | 48096.3984 | 47957.3984 | 47883.1992 | 47858.5 | 47525.6992 | 47267.6992 | 47477.1016 | 47111.1016 | 46932.8008 | 46839.5 | 47186.5 | 47468.3008 | 47749.3008 | 46989.3984 | 46400.8984
E1 | 51224.8008 | 49690.5 | 48125.8008 | 48025.3008 | 48130 | 48134.1016 | 48321.1016 | 48403 | 48302.8008 | 48191.5 | 48249.8984 | 48226.6016 | 48195.6992 | 48066.6016 | 48041.3008 | 48151.3984 | 47907.6016 | 47786.3008 | 47753.3984 | 48000.6016 | 48114.5 | 48297.1992 | 47575.1992 | 47009
E2 | 50820.3008 | 49289.1016 | 47727.6992 | 47627.8008 | 47732.1992 | 47735.5 | 47919.1992 | 48001.6016 | 47904.3984 | 47794.3984 | 47852.3008 | 47825.6016 | 47793.1992 | 47662.3008 | 47634.6992 | 47742.3008 | 47498.6992 | 47377.8984 | 47344.8008 | 47591 | 47704.8008 | 47887.6016 | 47172.1992 | 46612.8984
E3 | 48764.8984 | 47837.1016 | 46910.6992 | 46893.5 | 47138.8984 | 47300 | 47646.6016 | 47998.3984 | 48129.5 | 48123.8984 | 48155.3984 | 47994.8008 | 47684.3008 | 47240 | 46926 | 46833.5 | 46535 | 46555.6992 | 46790.6016 | 47153.3008 | 47338.1992 | 47603.6016 | 46708.3008 | 45968.3984
Actual | 70982.2422 | 70528.7812 | 70171.4062 | 70325.4219 | 70852.2344 | 71776.9688 | 72992.125 | 73962.6016 | 73910.4609 | 73687.8984 | 72242.3125 | 70034.1328 | 67487.0781 | 65539.2266 | 63850.8125 | 63395.7031 | 64255.1758 | 66505.4922 | 67948.1875 | 67977.6875 | 67856.9141 | 67342.5078 | 66338.4531 | 64822.7148

## Slide 4: Forecast Error Sources During Elliott - Summary
Due to a software change, ERCOT could not use the internally-developed MTLF models and had to rely on vendor-provided MTLF. The vendor-provided MTLF under-forecast the load
ERCOT has limited historical data on actual loads during cold weather events. This makes model training challenging
  Uri data after 2/14/21 was of no value due to system outages
The global weather forecast models and vendor-supplied weather forecasts were off on the timing and intensity of the cold front
Load forecasting model error

## Slide 5: Corrective Actions Currently Planned
Objective 1 – Reduce forecast errors from the alternative load forecasting source
  Add an external load forecast that will complement ERCOT’s Itron models
Objective 2 – Develop an innovative process for developing extreme cold weather forecasts
  Develop a process for creating specialized extreme cold weather models
  Based on a robust set of historical cold weather data

## Slide 6: Corrective Actions Currently Planned
Objective 3 – Reduce weather forecast error
  Add more raw weather forecasting models
    If the Canadian forecast was available, the day(s) ahead forecast would have been better
    If the HRRR forecast was available, the intraday forecast would have been better
Objective 4 – Improve Itron software upgrade testing process
  Create a more robust testing environment
  Update testing procedures to include holidays and other outlier phenomena

## Slide 7: Wrap-Up
The under-forecast had no impact on reliability because ERCOT intentionally prepared for higher demand than what the forecast models were projecting
For more details, see Operations Working Group presentation: https://www.ercot.com/files/docs/2023/02/15/MTLF%20Winter%20Storm%20Elliot%20OWG.pptx

## Slide 8: Appendix

## Slide 9
1. Software Change

## Slide 10: Software Upgrade and Impacts
A software upgrade for Itron went live on 12/6/2022
A change in how holidays are accounted for was not uncovered during testing
  Resulted in holidays being significantly under-forecasted
  Rendered E, E1, E2, and E3 unusable for most of the week
As a result, ERCOT selected the A3 forecast

## Slide 11
2. Weather Forecast

## Slide 12: MTLF Available Weather Forecasts
The following weather forecasts are available for the Itron models:
  European Model (Euro)
  Global Forecast System (GFS)
  Global Forecast System Ensemble (GENS)
  North American Model (NAM)
  3 vendor models
ERCOT is actively working on increasing the number of raw weather forecasts to those mentioned above
  Particularly of interest are the Canadian and HRRR models

## Slide 13: Weather Forecasts
Chart: DFW Forecasts for 12/23 @0800
| 44909 | 44910 | 44911 | 44912 | 44913 | 44914 | 44915 | 44916 | 44917 | 44918
NAM | 25 | 21 | 19 | 18 | 19 | 11 | 11 | 9 | 10 | 9
GENS | 24 | 21 | 21 | 17 | 11 | 10 | 14 | 14 | 14 | 13
MDA | 21 | 21 | 19 | 18 | 18 | 12 | 14 | 14 | 13 | 12
Actual | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
NAM was the preferred forecast but was unavailable to the A3 and A6 forecasts

## Slide 14: Weather Forecasts
Chart: IAM Forecasts for 12/23 @0800
| 44909 | 44910 | 44911 | 44912 | 44913 | 44914 | 44915 | 44916 | 44917 | 44918
NAM | 30 | 28 | 24 | 23 | 24 | 15 | 18 | 20 | 15 | 18
GENS | 32 | 28 | 28 | 25 | 18 | 18 | 20 | 19 | 19 | 19
MDA | 30 | 28 | 24 | 23 | 24 | 18 | 19 | 19 | 18 | 16
Actual | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
NAM was the preferred forecast but was unavailable to the A3 and A6 forecasts

## Slide 15: Weather Forecasts
Chart: AUS Forecasts for 12/23 @0800
| 44909 | 44910 | 44911 | 44912 | 44913 | 44914 | 44915 | 44916 | 44917 | 44918
NAM | 24 | 23 | 22 | 20 | 18 | 16 | 17 | 14 | 16 | 17
GENS | 28 | 26 | 25 | 23 | 16 | 16 | 18 | 17 | 17 | 17
MDA | 22 | 24 | 22 | 20 | 18 | 15 | 17 | 17 | 17 | 14
Actual | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
NAM was the preferred forecast but was unavailable to the A3 and A6 forecasts

## Slide 16: Load Forecasts
Chart: Selected Forecast Peak Demand for 12/23 @0900
| 44918.334722222222 | 44917.334722222222 | 44916.334722222222 | 44915.334722222222 | 44914.334722222222 | 44913.334722222222 | 44912.334722222222
A3 | 70898.2109 | 67574.2656 | 67943.2109 | 69313.125 | 69324.3047 | 67237.8984
Actual | 73910.4609
Forecasts were created at 8:02 am each day

## Slide 17
3. Historical Cold Weather Data

## Slide 18: ERCOT Load-Weighted Temperatures