## Slide 1
ERCOT Winter 2022-2023 Inspections
And Generation Performance during
Winter Storm Elliot
David Kezell
Director, Weatherization and Inspection
Technical Advisory Committee (TAC)
March 21, 2023

## Slide 2: Overview
Phase 1 of the PUCT Weather Emergency Preparedness rule was in place for winter 2021-2022. 302 winter weatherization inspections were conducted.
Phase 2 of the PUCT Weather Emergency Preparedness rule was in place for winter 2022-2023. 774 winter weatherization inspections were conducted.
Weather-related outages during Elliott in December, 2022 peaked at ~4,500 MW. During Uri in February, 2021, weather-related outages peaked at over 30,000 MW. While the storms differed in severity, duration, and precipitation, there does appear to be improvement in the overall ability of the generation fleet to operate during extreme cold weather.

## Slide 3: Winter 2022-2023 On-Site Inspections
36 TSP Stations
28 Dispatchable units
28 IRR units
11 TSP Stations
13 Dispatchable units
54 IRR units
16 TSP Stations
26 Dispatchable units
1 IRR unit
17 TSP Stations
43 Dispatchable units
5 IRR units
16 TSP Stations
72 Dispatchable units
19 IRR units
19 TSP Stations
200 Dispatchable units
19 IRR units
17 TSP Stations
37 Dispatchable units
60 IRR units
8 TSP Stations
9 Dispatchable units
20 IRR units
*IRR – Intermittent Renewable Resources
On-site Inspections
140 Transmission
428 Dispatchable
206 IRR
774 Total
Inspections Completed between December 2, 2022, and February 28, 2023
69 Facilities were assigned cure periods, most of which are already complete.

## Slide 4: Winter Storm Elliot – Outages by Age of Facility
Chart: Thermal Unit Outages by Age (RFI Responses)
Peak weather-caused outage levels for all age bands were reached at 10:00 on 12/23 with all age bands being most affected shortly after the coldest temperatures were recorded.
40+ year units peaked at 2209 MW but rebounded to 15 MW 5 hours later.
10-20 year units peaked at 1895 MW and were still at 570 MW through 12/25.
In terms of MWh lost over 4 days: 10-20 yr = 73,941, 40+ yr = 23,463, 0-10 yr = 8,540
  20-30 yr = 6,977, 30-40 yr = 0.
Chart: All Unit Outages by Age (RFI Responses)

## Slide 5: Next Steps
Continue to diligently pursue all weather emergency preparation measures and their maintenance as required by the PUCT Weather Emergency Preparedness rule.
A summer weatherization workshop for Resource Entities and TSPs is being scheduled for Wednesday 4/19/23 at the MET Center. The first round of summer weatherization inspections will start in early June.
Facilities with cure periods for compliance deficiencies must expeditiously resolve those deficiencies.
Keeping records of implementation of measures AND their maintenance through the appropriate season is critical.