## Slide 1
ERCOT Frequency Control Report
February 2023
ERCOT
Operations Planning
PDCWG | March 22nd, 2023

## Slide 2: Summary of February 2023
CPS1: 176.90%
Current CPS1 12-Month Rolling Average: 173.56%
0 BAAL Exceedance(s)
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2021
2021 BAAL-003 FRM Performance: -913.56
2023 RMS1 Statistics
  Mean: 14.42 mHz
  Min: 11.76 mHz
  Max: 17.30 mHz
Energy Statistics
  Total Energy: 30,335,510 MWh
  Wind Energy: 10,195,515 MWh
  Percent Energy from Wind: 33.61%
  Solar Energy: 1,442,064 MWh
  Percent Energy from Solar: 4.75%
Minimum System Inertia
  Mean: 178,997 MW*s
  Max: 348,505 MW*s on Jan 31st
  Min: 135,268 MW*s on Jan 15th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Feb-23 CPS1 (%): 176.90

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedance(s) in December.

## Slide 6: 15-Minute Average CPS1%
Feb-23 CPS1 (%): 176.90
Notes: Overall the 15 min CPS1 score is consistently above 160

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 173.56%
Notes: 12 month rolling average CPS1 score is 173.48, which is in line with expectations, and the CPS1 score for Jan is slightly higher than the last month.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is so far slightly smaller overall compared with 2022.
  Mean: 14.42 mHz
  Min: 11.76 mHz
  Max: 17.3 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
14.37mHz on avg for Feb 2023

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data with 10 years shown instead of 15

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile between Feb 2022 and Feb 2023, we see fewer instances of frequency hovering at or below the lower deadband in Feb 2023.

## Slide 13: Frequency Profile Comparison
Notes: Comparison of frequency profile between Feb 2021 and Feb 2023, we see fewer instances of frequency hovering well below the lower deadband in Feb 2023, and significantly fewer instances of frequency crossing the higher deadband in Feb 2023.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error
Notes: We did not make time error corrections and the time error was fairly small during the entire month of Feb.

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2021 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2021 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO = -471.0, FRM median = -913.56, FRM average = -992.

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 30,335,510 MWh

## Slide 22: Total Energy from Wind Generation
Notes:   10,195,515 MWH

## Slide 23: % Energy from Wind Generation
Notes: 33.61%
of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 1,442,064 MWh

## Slide 25: % Energy from Solar Generation
Notes: 4.75% of total
energy was provided by solar generation, which is highest solar penetration level so far.

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia =135,268 MW*s on 1/15/2023
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 178,997 MW*s
Max: 348,505 MW*s on Jan 31st
Min: 135,268 MW*s on Jan 15th

## Slide 28: ERCOT Inertia 2013-2023
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.

## Slide 29: Questions?
Thank you!