## Slide 1
Workshop on ERCOT’s Proposed Reliability Standard Study Framework
Woody Rickerson
VP Planning and Weatherization
Pete Warnken
Senior Manager, Resource Adequacy
ERCOT Public
March 15, 2023

## Slide 2: Reliability Standard Study Process
Key Takeaways:
Senate Bill 3 mandated the creation of an ERCOT Reliability Standard by the Public Utility Commission.
The Public Utility Commission created a Project (#54584) to facilitate that work, and issued a list of stakeholder questions on March 7, 2023.
A memo from Commissioner McAdams has requested ERCOT to work with PUC staff and Market Participants to begin the analysis.
ERCOT will use the Strategic Energy & Risk Valuation (SERVM) model for the study.
ERCOT presented a proposed study framework to its Board Members; the purpose of this workshop is to present, and solicit comments on, the study framework.
ERCOT is recommending a standard for study defined by three probabilistic metrics that cover the dimensions of loss-of-load events and addresses both average reliability and extreme event avoidance:
  Limit on the magnitude of any single loss of load event
  Limit the frequency of loss of load events
  Limit on the duration of any single loss of load event

## Slide 3: Proposed Reliability Standard Analysis Process
Recommendation for metrics to be used by ERCOT for study
2026 assessment using different metric criteria; a combination of criteria is a Scenario
Multiple Scenarios to capture incremental production cost and reliability impacts of metric criteria changes
Determine the Generation Portfolio needed to avoid exceeding the metric criteria defined for each Scenario
Corresponding Market incentives needed to attract new generation to meet new standard
Proposed Study Metrics
(Magnitude) Maximum load that can be rotated for any event should not exceed x% of peak (~x MW for today)
(Frequency) Load Shed events for generator inadequacy should not occur more than once in x years
(Duration) Any Load Shed event should not last for more than x hours.

## Slide 4: Current Study Work and Modeling Details
SERVM is a probabilistic Monte Carlo simulation tool, used by ERCOT for reserve margins and NERC probabilistic loss-of-load studies since 2014, that produces a distribution of expected reliability events and their costs based on many independent hourly chronological simulations (or trials).
ERCOT began training to enable staff to perform resource reliability studies previously performed by Astrape Consulting.
The current phase of work consists of updating the SERVM model:
  Latest ERCOT load forecast, November CDR resources, and fuel price forecasts
  Include ERCOT Contingency Reserve Service and update Load Resources
  Coding to implement new metric definitions (extreme event limits)
  Address expected impact of weatherization standards
  Conduct test model runs to assess reasonability of results
The Scenario resource portfolios will reflect new generation that is already expected to be built, likely retirements, and incremental levels of new dispatchable generation needed to meet the different level of reliability defined for each Scenario.
Scenario outputs will be used to compare:
  Incremental amounts of additional dispatchable resources
  Overall production cost
  Cost to the Market

## Slide 5: Next Steps
ERCOT anticipates commissioning a study to determine the Value of Lost Load (VOLL); decisions on the study scope and timeline are expected to be made at the March 23 PUC Open Meeting.
ERCOT is engaging Market Participants and PUC staff for input concerning the metrics used for the Reliability Standard study.
ERCOT will present a final proposed study framework to the PUCT and stakeholders:
  Metrics selected
  Scenarios defined for the study
  Metric criteria selected for each Scenario
ERCOT will start the Scenario analysis upon receiving direction from the PUCT.
An update on the progress will be made at appropriate stakeholder meetings, as well as the April and June ERCOT Board Meetings.

## Slide 6: Reliability Metrics / Criteria Used in Other Jurisdictions

## Slide 7: Reliability Metrics / Criteria Used in Other Jurisdictions

## Slide 8: Reliability Metrics / Criteria Used in Other Jurisdictions

## Slide 9: Supplemental

## Slide 10: Loss-of-Load Reliability Metric Definitions
Measure | Definition | LOL Attribute of Interest | Calculation Example
Loss of Load Hours (LOLH) | The expected number of LOL events for a given period. Alternatively, LOLH is the expected combined duration of LOL events for a given period. | Duration (number of hours) | There are 10 trials that had 2 LOL events, and 2 trials that had 4 LOL. Events. The remaining 88 trials had no LOL events: LOLH = (10 trials x 2 hours/year x 0.01) + (2 trials x 4 hours/year x 0.01) = 0.2 + 0.08 = 0.28 hours/year
Loss of Load Expectation (LOLE) | The expected number of LOL days for a given period. | Frequency (number of days) | There are 6 trials that had one day with a single LOL event, and 4 trials that had two days with two LOL events during each day. The remaining 90 trials had no LOL events: LOLE = (6 trials x 1 day/year x 0.01) + (4 trials x 2 days/year x 0.01) = 0.06 + 0.08 = 0.14 days/year Note that the conventional definition of LOLE does not distinguish between a day with a single LOL event and a day with multiple LOL events.
Expected Unserved Energy (EUE) | The expected total magnitude (in MWh) of LOL events for a given period. A variant, Normalized EUE (NEUE), is EUE divided by the total annual energy. | Size (MWh) | There is one trial with 2,500 MWh of unserved energy and one trial with 1,000 MWh of unserved energy. The remaining 98 trials had no LOL events: EUE = (1 trial x 2,500 MWh/year x 0.01) + (1 trial x 1,000 MWh/year x 0.01) = 25 + 10 = 35 MWh/year
A LOL event is defined as an hour during which firm load exceeds available generation capacity.
A LOL day is defined as a day during which there is at least one LOL event; note that a day with one LOL event is equivalent to a day with two or more LOL events.
The table below provides descriptions and calculation examples of the key probabilistic Reliability Standard metrics that should be considered by the Commission. For the measure calculation examples, it is assumed that there are 100 Monte Carlo simulation trials conducted for a given forecast year, and each trial has the same probability of occurrence, which is 1% (0.01).

## Slide 11: Loss-of-Load Reliability Metric Definitions
Measure | Definition | LOL Attribute of Interest | Calculation Example
Loss of Load Probability (LOLP) | The probability that a LOL event will occur over a given period. | Likelihood of occurrence (probability) | For the winter period, there are 25 trials that had a total of 120 LOL days. The remaining 75 trials had no LOL days: LOLP = 120 / (90 days x 100 trials) = 1.3%