## Slide 1: Meter Working Group Update to WMS
April 5, 2023
Doug Breshears

## Slide 2: NPRR 945 Double Counting Scenarios
Scenario for the double counting of energy flows
  EPS Metering Design Proposal submitted and approved for a generation site where load is netted with generation, and
  ERCOT assigns gen site net load to the ESI ID assigned to the gen site, and
  A separate ESI ID is established in ERCOT systems by the TDSP for the netted Load with the TDSP as the MRE, and
  Transactions submitted by the TDSP for the separate ESI ID includes any portion of the meter data that was also assigned to a gen site ESI ID populated by ERCOT during the gen site settlement process.
Multiple options requiring protocol and system changes were discussed
  Current protocol language supporting the assignment of multiple ESIIDs to a generation facility was reviewed as a possible path forward. This would eliminate the concerns of double counting energy.
The general consensus of the MWG was that the individual market participants could decide if the existing Protocol language can be used to eliminate the double counting of energy.

## Slide 3: Loss Compensation For Joint Use Facilities
For scenarios where there is an EPS meter at the POI and another EPS Meter behind the POI, all losses are captured by the POI meter, so any meters behind the POI should not be loss compensated, as trying to determine losses in complicated networks behind a generation site POI can be problematic.
For scenarios where no EPS meter is at the POI, generation and load meters behind the POI should be loss compensated to the POI. The generation meter would be compensated by programming loss compensation in the meter. The load meter would be compensated by programming loss compensation in the meter, or the use of a fixed factor based on the loads maximum value.
Concerns were raised about calculating the line loss in a private network.
Topic will warrant further discussion as ERCOT and TDSPs consider additional options.

## Slide 4: Composite Error Testing of Current Transformers
Composite Error Testing is a method to derive the Ratio Correction Factor (RCF) and Phase Angle(PA).
Per SMOG/ANSI for EPS metering CTs, RCF, and PA, must be determined by direct measurement, therefore Composite Error Testing is not acceptable for this application.