## Slide 1: Black Start Working Group
Chair- Michael Dieringer
Vice-Chair- Freddy Garcia
4/03/2023

## Slide 2: NPRR1164 – Black Start and Isochronous Control Capable Identification
Primary Focus – To identify units that are black start capably in case a contracted unit does not start.
Goals – Getting generator details and Operator tribal knowledge implemented into Grid Geo.
  This will be useful information not only at Black start training but supporting the primary focus stated above.
Definitions – Are they good as written?
In the Open session of the BSWG it was discussed to possibly add another definition for droop setting. It was agreed upon to leave as is since the verbiage clearly states Isochronous capable generator. Additionally, it was discussed and agreed upon to add “Governor” to the definition. End result would read, Isochronous Governor Control Capable Resource No other comments/concerns were disused about the definitions.
Additional comments/concerns that were discussed.
  What are the qualifications of non contracted Isochronous generators. (E.G. a generator that was previously a contracted Black Start unit but is no longer under contract.) Additionally this could include units that held a Black Start contract but have not gone through testing since the contract ended.
  If the unit met the requirements of the ERCOT Black Start test, ERCOT would want to know those units and model them in Grid Geo.
  These newly identified Isochronous generators would not be a requirement in the TO’s Black Start Plan, but would be in the ERCOT Black Start Plan. TO’s should focus on the contracted Black Start Units.
  Grid Geo currently has synchroscopes.
  Lastly, a motion was given to pass as written with the addition of “Governor”. Motion was seconded. There were none that opposed.

## Slide 3: Black Start Working Group
Closed Session.

## Slide 4: 2024-2026 Black Start Proposals
15 RFPs spanning 21 resources.
  RFPs are submitted by station.
  Some RFPs include multiple resources at a single station.
11 RFPs (15 resources) have 2022-2023 Black Start Contracts.
Only conventional resources submitted RFPs.
6 RFPs included Back-up Fuel option.
  One out of 6 RFPs included the option to install the Back-up Fuel facility.

## Slide 5: 2023 Black Start Training
ERCOT Black Start Training will be held on site at ERCOT in Taylor
Market Notice went out on 3/24/2023 dates were included.
Participants have been asked to update their information on the Cornerstone LMS.
Looking ahead at 2024 Black Start Training should utilize Grid Geo.
After 2024 discussion on rotating Black Start training to be on/off site.
  Pros/Cons to both, Pro is more realistic when off site, Con is offsite.

## Slide 6: Black Start Corridor File Template
Template will Improve Situation of Awareness

## Slide 7: Brainstorming ideas to improve Black Start
1)Communication Gap Concern – PUCT substantive rule tele-communication backup requirements only indicates a 4 hour battery requirement if do not have a diesel backup at the central communication provider sites. With phone services and broadband services using fiber that needs to be amplified at 50 mile lengths, will most of the phone and broadband communications go down in a blackout after the battery backup time frames? Not sure anyone knows how bad this could be but needs to be researched and proactive actions taken. Other RTOs require more than just the black start units to have satellite back up phone requirements. Cranking paths can not proceed if the TOs can not talk to the units that are next start or 3rd start units.
2)Get Dynamic Frequency and Reactive Response on Quickly -The speed of the restoration will be enhanced by getting as much dynamic frequency and dynamic reactive response on line as quick as possible to assist the black start unit or isochronous unit. Using the dynamic capability to respond to the load pickups or system disturbances will enhance the speed of the path expansion. With that in mind need ERCOT and all companies to utilize batteries and solar and wind category 4 machines to get as much capability on line without causing contingency issues by loading them up and creating contingency issues. The batteries could also be used to be short term MW balancing if optimized properly and properly monitored and dispatched. Need to clearly define the sites that have the proper desired dynamic capability for frequency or reactive for these black start situations and formalize their use in the Black start Plans.
3)Enhance System to Allow Energizing Redundant Bulk Transmission Lines Quicker -The speed of the restoration will be enhanced if select 345kv between zones is planned to have smaller and redundant reactive control so contingencies don’t create large swings on generators and allows for building redundant and large transmission reserves and connect larger units quicker. Determine where planning smaller redundant reactive reactors are needed to energize 345kv earlier in the cranking paths where it makes sense and is not a large expense to the market. Using item 2 and this item in combination could speed up the restoration significantly.
4)Mutual Assistance Agreements with other RTOs - similar to item 2 the restoration will be enhanced if we can build sections of the grid back by building by utilizing strength that is readily available. While AEP has in it’s plan to utilize the Laredo VFT as a black start resource from CFE there is also potential to utilize other block start up sections to get significant amount of load / generation up prior to separating from the other grid and combining ERCOT islands. Needs to be planned and thought through to optimize this potential ( in conjunction with item 6) and have mutual assistance agreements in place.

## Slide 8: Brainstorming ideas to improve Black Start
5)CBT Training Material for Generators – While blackstart units are part of the black start training the remaining of the cranking path units may or may not be familiar with their responsibilities, gaps and etc. When AEP did a black start in the Del Rio area a number of years ago the unit did not understand they could not have two of their units on isochronous control at the same time and led to a system that was started and collapse many times. The cranking path units need to understand that instructions are coming from a different direction (TO Versus ERCOT) , minimum excitation relay limiters are no longer at the correct steady state limits and other gap issues.
6)Isochronous Machine Expansion – While ERCOT has now required the units to indicate in RIOO which units are Isochronous capable , it does not identify which larger units could add this capability with minimum dollars. For example Oklaunion had determined it could add this capability with minimum investment of about $50000. While there might need to be market repayments , if there are proper large units that could add isochronous control capability inexpensively it might be possible in combination with item 4 for significant enhancement to the restoration time frames.
7)Constant Frequency Control Enhancement - ERCOT has recognized the benefit of getting on Constant Frequency Control but there is no real plan of which companies will be used for which zones beyond the big cities where most the QSEs reside. Would need to plan out by zones which companies would control which zones and if possible have the control system allow for the frequency sensing to be reassigned to the zones that they would control.
  It was suggested to move ideas to Open session for next meeting to get additional feedback. Ask for more ideas and see which ideas we can utilize to help improve the BSWG, Black Start Plans, and Black Start Training.