## Slide 1
ERCOT Interconnection Inertia Analysis
04/21/2023
ERCOT Staff

## Slide 2: Effect of Synchronous Inertia on System Frequency
With increasing integration of inverter-based generation, there could be periods when total inertia of the system could be low since less synchronous machines will be online.
UFLS trigger
Notes: UFLS trigger indicates the frequency (59.3 Hz) at which the first stage of involuntary underfrequency load shedding will happen. ERCOT plans and operates the system such that for the simultaneous trip of two largest generating units (2750 MW), UFLS should not be triggered, though it still can happen in some extreme unexpected situations.

## Slide 3: Inertia Calculation
In 2013, as instantaneous wind power penetration reached 30%, ERCOT started analyzing impacts of inverter-based generation on system inertia.
In 2015, ERCOT implemented a real-time inertia calculation using inertia parameters of each individual synchronous generator and its status (on/off) telemetry.
where I is the set of online synchronous generators or condensers,
MVAi is MVA base of on-line synchronous generator or synchronous condenser i, and
Hi is inertia constant for on-line generator or synchronous condenser i in a system (in seconds on machine MVAi)

## Slide 4: Inertia Constants
ERCOT reviews inertia constants in EMS each year following DWG case release
DWG cases were released on 2/28/23
  Inertia constant updates will enter model in coming months
where I is the set of online synchronous generators or condensers,
MVAi is MVA base of on-line synchronous generator or synchronous condenser i, and
Hi is inertia constant for on-line generator or synchronous condenser i in a system (in seconds on machine MVAi)
Notes: Since adjustments are yearly, typically do not have as large as an impact as 2021 update (first annual update)

## Slide 5: Inertia Monitoring in Real-Time
In 2016, inertia monitoring was implemented in the control room. Visual alarms are raised alarms when inertia gets close to critical levels.
As inertia approaches critical levels, ERCOT System Operators may take actions to bring additional synchronous generation resources with sufficient inertia online.
Current system inertia posted on ERCOT.com https://www.ercot.com/content/cdr/html/real_time_system_conditions.html

## Slide 6: ERCOT Inertia 2013-2023^
Date and Time | 2013 3/10 3:00 AM | 2014 3/30 3:00 AM | 2015 11/25 2:00 AM | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021* 03/22 1:00 AM | 2022 03/21 2:00 AM | 2023^ 03/16 4:00 AM
Min synch. Inertia (GW*s) | 132 | 135 | 152 | 143 | 130 | 128.8 | 134.5 | 131.1 | 116.6* | 115.0 | 131.6
System load at minimum synch. Inertia (MW) | 24,726 | 24,540 | 27,190 | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 31,767 | 33,784 | 37,098
Non-synch. Gen. in % of System Load | 31 | 34 | 42 | 47 | 54 | 53 | 50 | 57 | 66 | 65 | 65
* Measured at 109.6 GW*s, re-calculated using corrected inertia constants
^ data through 4/1/2023
Notes: For each box, the central dark blue line is the median, the edges of the box are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia at the highest IRR penetration in that year.
ERCOT tripled installed wind capacity between 2013 and 2020, adding nearly 20 GW of wind generation (including all synchronized projects)
An equal amount of coal capacity has about 55 GW*s of inertia contribution.
Have observed lower minimum inertia in recent years;
Counterintuitively, the inertia trend is not declining as installed IBR capacity increases, as was anticipated, due to other factors, such as load growth, gas prices, wind curtailments etc.

## Slide 7: ERCOT Inertia 2017-2023^

## Slide 8: Generation Retirement
420 MW of GAS-ST retired in 2022
Total Generation Capacity Retired Since 2013 |  |  |  |  |  | 
Biomass | Coal | Gas-CC | Gas-GT | Gas-ST | Storage | Wind
45 | 5,531 | 804 | 35 | 4,166.5 | 2 | 316.55

## Slide 9: Coal and Combined Cycle Inertia Trends
Combined Cycle Plant has about 1.5x higher inertia than a Coal Plant with the same MVA rating
Notes: Coal outlier occurred on 3/9/22 when Total Inertia close to 200 GW*s, CC Inertia >> 100 GW*s

## Slide 10: PUN Inertia
Notes: PUN generators may be online at all times regardless of electricity market conditions.
Even when PUNs are not exporting power, they are contributing to system inertia, because they are synchronized to the ERCOT grid.

## Slide 11: Wind Generation Capacity
+1,893 MW
+3,198 MW
+2,625 MW
+2,247 MW
+1,384 MW
+4,587 MW
+3,908 MW
+2,802 MW
+2,977 MW

## Slide 12: Wind Generation by Year

## Slide 13: Solar Generation Capacity
+696 MW
+3,429 MW
+4,780 MW
+4,003 MW

## Slide 14: Solar Generation by Year
Notes: Daytime hours (generation > 5MW)

## Slide 15: Energy Storage Resource (ESR) Capacity
+1,041 MW
+1,472 MW

## Slide 16: ESR Generation by Hour

## Slide 17: Total Load by Year

## Slide 18: Net Load by Year
Net Load = Load – Wind Generation – Solar Generation

## Slide 19: Lowest 100 Inertia Hours 2017-2022
 | 2017 | 2018 | 2019 | 2020 | 2021* | 2022
Lowest Inertia Hour (GW*s) | 130 | 129 | 135 | 131 | 117 | 115
100th Lowest Inertia Hour (GW*s) | 146 | 155 | 152 | 147 | 135 | 125

## Slide 20: Low Net Load Hours 2017-2022

## Slide 21: Median Inertia by Source During Lowest 100 Total Inertia Hours

## Slide 22: Combined Cycle Outages during Low Inertia Hours

## Slide 23: CC Inertia vs. Net Load
Less conventional generation is dispatched during low net load hours
More low net load hours (below 14 GW) in 2022 and 2021 than in past years
  CC inertia is low in 2022’s lowest total inertia hours regardless of net load
Notes: r^2 = 0.249
r^2 = 0.813 (all hours)

## Slide 24: Coal & Gas-Steam vs. Net Load
Very small correlation between coal inertia and net load; gas-steam inertia and net load
Less synchronous generation to be dispatched at low net load
  CC inertia appears to be affected most by lower net load
Notes: r^2 (coal) = 0.039
r^2 (coal) = 0.221 (all hours)
r^2 (GS) = 0.048
r^2 (GS) = 0. (all hours)

## Slide 25: Natural Gas Prices
https://www.macrotrends.net/2478/natural-gas-prices-historical-chart
Notes: About 50% of ERCOT’s generation fleet is natural gas based
Fluctuations in natural gas prices affect generating unit commitment patterns and, thus, system inertia
More combined cycle units are committed during periods with low gas prices (higher inertia than coal)
More Coal units are committed in periods with high gas prices (lower inertia than combined cycle)

## Slide 26: Summary
Lowest system inertia in 2022 was 115 GW*s
2022 experienced more hours below 150 GW*s than in previous years; more hours above 300 GW*s
As in 2021, lower contribution from combined cycle units was correlated with the lowest system-wide inertia hours
  CC capacity has not decreased over last 5 years
  A combination of increased outages, higher natural gas prices, and lower net load led to different dispatch of CC units during lowest inertia hours
Higher ERCOT load offset the increase in IRR generation
  Lowest net load hours in 2022 were similar to lowest net load hours in 2021

## Slide 27: Thank you! Questions?

## Slide 28: Appendix

## Slide 29: Inertia by Unit Type during Minimum Inertia Hour 2023^

## Slide 30: Inertia by Unit Type during Minimum Inertia Hour
Date and Time | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 1:00 AM | 2022 03/21 2:00 AM
Min synch. Inertia (GW*s) | 130 | 128.8 | 134.5 | 131.1 | 116.6* | 115.0

## Slide 31: Low Combined Cycle Inertia Hours
Notes: ** function of net load?
Trim to 500

## Slide 32: Low Load Hours 2017-2022
Notes: ** talk to Chris C about potential drivers for load

## Slide 33: Combined Cycle by Month 2020-2022

## Slide 34: Low Inertia Hours by Month

## Slide 35: Average Combined Cycle Outages by Month

## Slide 36: High Wind Generation Hours 2017-2022

## Slide 37: High Solar Generation Hours 2017-2022