## TitlePage
Report on the Capacity, Demand and Reserves
(CDR) in the ERCOT Region, 2024-2033
May 3, 2023

## Contents
Table of Contents
Tab | Notes
Disclaimer | Please read
Changes from previous CDR | List of significant changes relative to the last CDR, published November 2022
Definitions | List of definitions
Executive Summary | Synopsis of considerations for this report
SummerSummary | Shows load forecast, resource capacity and reserve margin for Summer 2024 through Summer 2033
SummerCapacities | List of registered resources and capabilities used in determining the capacity contribution for Summer Peak Season
Peak v High Net Load Hour 2024 | Presents a scenario comparison of the summer 2024 summary tab with a version based on load, wind and solar values for the Net Peak hour, assumed to be hour-ending 8:00 PM
Planned Resources Scenarios | Condensed versions of the Summer Summary tab for 2024-2028 under different sets of planned project inclusion criteria
WinterSummary | Shows load forecast, resource capacity and reserve margin for Winter 2024/2025 through Winter 2033/2034
WinterCapacities | List of registered resources and capabilities used in determining the capacity contribution for Winter Peak Season
Fuel Type Capacity Mix | Lists generation fuel types by MW and by percentage for Summer 2024 through Summer 2033 and Winter 2024/25 through Winter 2033/2034
Unconfirmed Retirement Capacity | A list of units for which public retirement announcements have been made but no formal retirement notices have been provided to ERCOT ("Unconfirmed" planned retirements)
Fossil Fuel SODG Capacities | Fossil Fuel Settlement Only Distributed Generator (SODG) Capacities
Decommissioned Gen. Resources | Lists Generation Resources that have been decommissioned and retired per a Notification of Suspension of Operations (NSO) or a Notification of Change of Generation Resource Designation (NCGRD)

## Disclaimer
Disclaimer
CDR WORKING PAPER
FOR PLANNING PURPOSES ONLY
This ERCOT Working Paper has been prepared for specific ERCOT and market participant purposes and has been developed from data provided by ERCOT market participants. The data may contain errors or become obsolete and thereby affect the conclusions and opinions of the Working Paper. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT WORKING PAPER IS SUPPLIED WITH ALL FAULTS. The specific suitability for any use of the Working Paper and its accuracy should be confirmed by each ERCOT market participant that contributed data for this Working Paper.

## Changes
Notes on Changes Relative to the Last CDR Report, Published November 2022
5.6
1 | The following Planned Resources have finalized the necessary agreements and permits to be added to the CDR report: | [8 empty] | 5.6
| Project Name | GENERATION INTERCONNECTION PROJECT CODE | County | Fuel | Zone | Year of Projected Commercial Operations (a) | Summer Capacity MW | Summer Capacity Contribution % | Summer Peak Ave. Capacity Contribution MW
| BROTMAN POWER STATION (U1 - U2) | 23INR0613 | BRAZORIA | GAS-GT | COASTAL | 2024 | 89.2 | 100% | 89.2
| BROTMAN II POWER STATION (U7- U8) | 23INR0551 | BRAZORIA | GAS-GT | COASTAL | 2023 | 89.2 | 100% | 89.2
| REMY JADE II POWER STATION | 24INR0382 | HARRIS | GAS-GT | HOUSTON | 2024 | 103.7 | 100% | 103.7
| SKY SEALY | 21INR0500 | AUSTIN | GAS-IC | SOUTH | 2025 | 129 | 100% | 129
| TECO GTG2 | 23INR0408 | HARRIS | GAS-GT | HOUSTON | 2024 | 50 | 100% | 50
| ALILA SOLAR | 23INR0093 | SAN PATRICIO | SOLAR | COASTAL | 2024 | 256.5 | 79% | 202.635
| ASH CREEK SOLAR | 21INR0379 | HILL | SOLAR | NORTH | 2024 | 408.9 | 79% | 323.031
| COMPADRE SOLAR | 24INR0023 | HILL | SOLAR | NORTH | 2024 | 405.3 | 79% | 320.187
| CRADLE SOLAR | 23INR0150 | BRAZORIA | SOLAR | COASTAL | 2025 | 225 | 79% | 177.75
| DESERT VINE SOLAR | 22INR0307 | ZAPATA | SOLAR | SOUTH | 2024 | 121.3 | 79% | 95.827
| DORI BQ SOLAR | 23INR0040 | HARRIS | SOLAR | HOUSTON | 2024 | 50.4 | 79% | 39.816
| ORIANA SOLAR | 24INR0093 | VICTORIA | SOLAR | SOUTH | 2024 | 201.3 | 79% | 159.027
| SP JAGUAR SOLAR | 24INR0038 | MCLENNAN | SOLAR | NORTH | 2024 | 300 | 79% | 237
| AEP_N_ALAMO_LD02(SMT ALAMO) | 23INR0477 | HIDALGO | STORAGE | SOUTH | 2023 | 10 | 0% | 0
| AL PASTOR BESS | 24INR0273 | DAWSON | STORAGE | WEST | 2024 | 100.8 | 0% | 0
| BOCO BESS | 23INR0470 | BORDEN | STORAGE | WEST | 2024 | 153.3 | 0% | 0
| BRP AVILA BESS | 23INR0287 | PECOS | STORAGE | WEST | 2024 | 164.9 | 0% | 0
| BRP ZEYA BESS | 23INR0290 | GALVESTON | STORAGE | HOUSTON | 2024 | 256.8 | 0% | 0
| CONNOLLY STORAGE | 23INR0403 | WISE | STORAGE | NORTH | 2024 | 131.1 | 0% | 0
| DAMON STORAGE | 23INR0523 | BRAZORIA | STORAGE | COASTAL | 2023 | 5 | 0% | 0
| FERDINAND GRID BESS | 22INR0422 | BEXAR | STORAGE | SOUTH | 2025 | 202.6 | 0% | 0
| FIVE WELLS STORAGE | 23INR0159 | BELL | STORAGE | NORTH | 2023 | 220.8 | 0% | 0
| FORT DUNCAN BESS | 23INR0350 | MAVERICK | STORAGE | SOUTH | 2025 | 106.2 | 0% | 0
| IRON BELT ENERGY STORAGE | 25INR0208 | DAWSON | STORAGE | WEST | 2025 | 401.9 | 0% | 0
| MYRTLE STORAGE | 21INR0442 | BRAZORIA | STORAGE | COASTAL | 2023 | 155 | 0% | 0
| ORIANA BESS | 24INR0109 | VICTORIA | STORAGE | SOUTH | 2024 | 61.4 | 0% | 0
| PLATINUM STORAGE | 22INR0554 | FANNIN | STORAGE | NORTH | 2024 | 303.5 | 0% | 0
| SMT ALAMO (DGR) | 23INR0477 | HIDALGO | STORAGE | SOUTH | 2023 | 10 | 0% | 0
| SMT LOS FRESNOS (DGR) | 23INR0508 | CAMERON | STORAGE | COASTAL | 2023 | 10 | 0% | 0
| SMT MISSION (DGR) | 23INR0511 | CAMERON | STORAGE | COASTAL | 2023 | 10 | 0% | 0
| SMT RIO GRANDE (DGR) | 23INR0509 | STARR | STORAGE | SOUTH | 2023 | 10 | 0% | 0
| SMT RIO GRANDE II (DGR) | 23INR0510 | STARR | STORAGE | SOUTH | 2023 | 10 | 0% | 0
| SOHO BESS | 23INR0419 | BRAZORIA | STORAGE | COASTAL | 2024 | 206.3 | 0% | 0
| SP JAGUAR BESS | 24INR0039 | MCLENNAN | STORAGE | NORTH | 2024 | 300 | 0% | 0
| ST. GALL I ENERGY STORAGE | 22INR0524 | PECOS | STORAGE | WEST | 2023 | 102.6 | 0% | 0
| SUN VALLEY BESS | 22INR0429 | HILL | STORAGE | NORTH | 2023 | 101.4 | 0% | 0
| TALITHA BESS | 23INR0331 | JIM WELLS | STORAGE | SOUTH | 2024 | 61.4 | 0% | 0
| TOTAL | [5 empty] | 5524.8 |  | 2016.373
(a) This date is based on the projected Commercial Operations Date (COD) reported by the project developer. In contrast, a unit's first summer CDR forecast year (reported in the SummerCapacities sheet) is defined as the first year in which the capacity is available for the entire summer Peak Load Season. (The summer Peak Load Season constitutes the months of June, July, August and September.) For example, if a unit has a projected COD of July 1, 2022, the first summer CDR forecast year would be 2022. Planned projects with (DGR) suffix are Distributed Generation Resources (DGRs).
2 | A new scenario tab has been added (Peak v Net Peak Comparison 2024) that compares the summer 2024 summary tab column with a version based on load, wind and solar values for the Net Peak hour, assumed to be hour-ending 8:00 PM. The new tab also includes reserve margin comparison for summer 2024 when a battery storage capacity contribution is included.

## Definitions
Definitions
Available Mothballed Capacity based on Owner's Return Probability
Mothballed capacity with a return-to-service probability of 50% or greater for a given season of the year, as provided by its owner, constitutes available mothballed generation. Return probabilities for individual units are considered protected information under the ERCOT Protocols and therefore are not included in this report.
Capacity Pending Retirement
Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
Decommissioned Generation Resource
A Generation Resource for which a Resource Entity has submitted a Notification of Suspension of Operations (NSO) or a Notification of Change of Generation Resource Designation (NCGRD), for which ERCOT has declined to execute a Reliability Must-Run (RMR) Agreement, and which has been decommissioned and permanently retired.
Distribution Resource Types:
Settlement Only Distribution Generator (SODG)
A generator that is connected to the Distribution System with a rating of: (1) One MW or less that chooses to register as an SODG; or (2) Greater than one and up to ten MW that is capable of providing a net export to the ERCOT System and does not register as a Distribution Generation Resource (DGR). SODGs are settled for exported energy only, but may not participate in the Ancillary Services market, Reliability Unit Commitment (RUC), Security-Constrained Economic Dispatch (SCED), or make energy offers. SODGs are listed in the SummerCapacities and WinterCapacities with a DG_ prefix in the UNIT CODE column
Distribution Generation Resource (DGR)
A Generation Resource connected to the Distribution System that is either: (1) Greater than ten MW and not registered with the Public Utility Commission of Texas (PUCT) as a self-generator; or (2) Ten MW or less that chooses to register as a Generation Resource to participate in the ERCOT markets. DGRs must be registered with ERCOT in accordance with Planning Guide Section 6.8.2, Resource Registration Process, and will be modeled in ERCOT systems in accordance with Section 3.10.7.2, Modeling of Resources and Transmission Loads. DGRs are listed in the SummerCapacities and WinterCapacities tabs with a (DGR) suffix in the UNIT NAME column
Emergency Response Service
ERCOT uses the methodology specified in Protocol Section 3.2.6.2.1, Peak Load Estimate, to derive the ERS capacity forecast for future years. The Current Year for the calculations is defined as the latest year for which ERS has been procured. The ERS capacity amounts are grossed up by 2% to reflect avoided transmission line losses.
Energy Efficiency Program Savings Forecast
ERCOT's energy efficiency forecast uses the PUCT's annual verified energy efficiency program savings estimates as the starting point. (See the definition for verified energy efficiency program savings below.) Savings from TDSP standard offer load management programs are not included in the ERCOT energy efficiency forecast. ERCOT computes the historical average annual verified savings, but excludes 2017 from the calculation due to Hurricane Harvey load impacts. (For prior forecasts, ERCOT used a formula based on the State energy efficiency goals in Utilities Code Section 39.905. Since the impacts of the goals were assumed to accumulate for just seven years from the time that the goals must be first met (2013), ERCOT no longer uses the goal-based forecasting approach.) Finally, ERCOT incorporates annual energy efficiency estimates from municipal utilities and electric cooperatives provided to the State Energy Conservation Office (SECO). Annual SECO report submission by these entities is required under S.B. No. 924. If annual reports for the previous calendar year are not available at the time the CDR is prepared, ERCOT incorporates report data for the most recently available reporting year. The energy efficiency capacity amounts are grossed up by a factor representing avoided transmission and distribution line losses. The factor is currently 1.076, reflecting 2% for avoided transmission losses and 5.6% for avoided distribution losses. The loss percentages are based on transmission and distribution loss factors posted to ERCOT's MIS website.
Energy Emergency Alert (EEA)
An ERCOT EEA declaration is made when operating reserves and system frequency drop below established severity levels (Levels 1, 2 and 3) and reserves are not projected to recover within 30 minutes unless certain actions are taken. An EEA declaration initiates an orderly, predetermined procedure for maximizing the use of available Resources, including the use of voluntary load reduction programs that are only available under EEA operations. Only under the most severe EEA level, would ERCOT direct Transmission and Distribution Service Providers to start shedding Load on a rotating basis in order to maintain system reliability and integrity. See Nodal Protocol Section 6.5.9.4, Energy Emergency Alert, for more details.
Forecast Zone
The CDR report uses Forecast Zones to identify the geographical location of generation resources. Forecast Zones generally have the same boundaries as the 2003 Congestion Management Zones with the following exceptions: A) Panhandle Zone for resources in the Texas Panhandle counties and outside the 2003 Congestion Management Zones, and B) Coastal Zone for resources in 11 counties along the Texas Gulf Coast and formerly in the South Zone of the 2003 Congestion Management Zones. There are six Forecast Zones: Coastal, Houston, North, Panhandle, South, and West. Note that the CDR Forecast Zones are only used for resource adequacy reporting and are distinct from other ERCOT geographical reporting schemes used for planning, operational, or data reporting purposes.
Full Interconnection Study (FIS)
The set of studies conducted by a Transmission Service Provider (TSP) for the purpose of identifying any electric system improvements or enhancements required to reliably interconnect a new All-Inclusive Generation Resource consistent with the provisions of Planning Guide Section 5, Generation Resource Interconnection or Change Request. These studies may include steady-state studies, system protection (short-circuit) studies, dynamic and transient stability studies, facility studies, and sub-synchronous oscillation studies.
Inactive Projects
Per Planning Guide Section 5.7.6, a proposed Resource shall be given the status of “Inactive” if the Resource has not met the conditions for inclusion in the ERCOT planning models, as specified in Section 6.9, Addition of Proposed Generation to the Planning Models, within two years of the date on which ERCOT posts the final FIS studies for the Resource to the MIS Secure Area. A developer may also elect Inactive status and stop any interconnection studies in process at its own discretion. When an Inactive Resource subsequently meets the requirements of Section 6.9, it shall be added to the planning models and the status changed back to Planned. If a Resource has been Inactive for five years, ERCOT may cancel the project pursuant to Planning Guide Section 5.7.7, Cancellation of a Project Due to Failure to Comply with Requirements. According to ERCOT Nodal Protocol rules (NPRR980), Inactive planned projects are excluded from the CDR's reserve margin calculations.
Installed Capacity Rating
The installed capacity rating is the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. ERCOT uses Real Power Ratings that reflect the continous flow of power to loads (as opposed to reactive power, which is the power that flows back and forth between the power source and loads, and doesn't perform useful work.)
Mothballed Unit
A generation resource for which a generation entity has submitted a Notification of Suspension of Operations, for which ERCOT has declined to execute an RMR agreement, and for which the generation entity has not announced retirement of the generation resource. A seasonal mothballed unit is one in which the generation entity requests a seasonal operation period that must include the summer Peak Load Season, June 1 through September 30.
LRs (Load Resources)
Load capable of reducing or increasing the need for electrical energy or providing Ancillary Services to the ERCOT System, as described in the ERCOT Protocols, Section 6, Ancillary Services. These Resources may provide the following Ancillary Services: Responsive Reserve Service, Non-Spinning Reserve Service, Replacement Reserve Service, and Regulation Service. The Resources must be registered and qualified by ERCOT and will be scheduled by a Qualified Scheduling Entity (QSE). LR capacity has been grossed up by 2% to reflect avoided transmission line losses.
Mothballed Capacity
Capacity that is designated as mothballed by a generating unit's owner as described above, and which is not available for operations during the summer Peak Load Season (June, July, August and September) or winter Peak Load Season (December, January and February).
Peak Load Seasons
Summer months are June, July, August, and September; winter months are December, January, and February.
Private Use Networks
An electric network connected to the ERCOT transmission grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation).
Non-Synchronous Tie
Any non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems.
Reliability Must-Run (RMR) Unit
A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
Signed SGIA (Standard Generation Interconnection Agreement)
An agreement that sets forth requirements for physical connection between an eligible transmission service customer and a transmission or distribution service provider.
Switchable Generation Resource (SWGR)
A generation resource that can be connected to either the ERCOT transmission grid or a grid outside the ERCOT Region.
Synchronized but not Approved for Commerical Operations Capacity
These units have met requirements to Energize Equipment (Part 1 of Generator Commissioning Checklist): provided latest model data, verified Voltage Ride-Through capability and communication capabilities specified by ERCOT Operating Guides are in place. Output for these resources is not limited once they have passed a curtailment test and the project developer has submitted an attestation for the following plant controls: Automatic Voltage Regulator (AVR), Primary Frequency Response (PFR), Voltage Support Service (VSS), and Power System Stabilizer (PSS). A Synchronized unit get approved for Commerical Operations after the plant controls have been verified by ERCOT. More information on Synchronized units can be found in the Resource Interconnection Handbook pages 24 – 33.http://www.ercot.com/content/wcm/lists/168284/Resource_Interconnection_Handbook_v1.91_01082021.docx
TDSP Standard Offer Load Management Programs
For the May releases of the CDR report, ERCOT uses the megawatt amount of verified peak load capacity reductions, adjusted for avoided transmission losses, due to TDSP Standard Offcer load management programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. The reported amounts are for the most current reporting year, which is the calendar year prior to the year during which the May CDR is prepared. (For example, the May 2019 CDR report used verified program savings for the 2018 reporting year.) For the December CDR releases, ERCOT uses TDSP data received for the current load management program year, which is more timely than the verified savings estimates provided to the PUCT. The data obtained from the TDSPs reflect verified program performance for the summer based on testing, and is adjusted for avoided transmission losses.
Unconfirmed Retirement
A Generation Resource for which a public announcement of the intent to permanently shut the unit down has been released, but a Notice of Suspension of Operations for the unit has not been received by ERCOT. This is an informal definition that is not currently included in the Nodal Protocols or Other Binding Documents. The criteria for classifying a Generation Resource as an Unconfirmed Retirement include the following: a. A specific retirement date is cited in the announcement, or other timing information is given that indicates the unit will be unavailable as of June 1 of a CDR Reporting Year. b. The announcement, with follow-up inquiry by ERCOT, does not indicate that retirement timing is highly speculative.
Verified Energy Efficiency Program Savings
The total megawatt (MW) amount of verified peak load capacity reductions due to residential and commercial sector energy efficiency incentive programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. See Utilities Code Section 39.905. Note that savings from TDSP standard offer load management programs are not included in the ERCOT energy efficiency forecast, but rather handled as a separate reporting line item.
Wind Peak Average Capacity Contribution
The seasonal net capacity rating of wind resources multiplied by the Seasonal Peak Average Capacity Percentage for the Coastal, Panhandle and Other CDR reporting regions.
Wind Seasonal Peak Average Capacity Percentage
The average wind capacity available for the summer and winter Peak Load Seasons for a CDR reporting region (Coastal, Panhandle, Other) divided by the installed capacity for the region, expressed as a percentage. Details for the derivation of the percentages are outlined in ERCOT Protocol Section 3.2.6.2.2 (see http://www.ercot.com/content/wcm/current_guides/53528/03-110119_Nodal.docx).
Wind Regions: Coastal, Panhandle, and Other
Wind Generation Resources (WGRs) are classified into regions based on the county that contains their Point of Interconnection (POI). The Coastal region is defined as the following counties along the Gulf Coast: Aransas, Brazoria, Calhoun, Cameron, Kenedy, Kleberg, Matagorda, Nueces, Refugio, San Patricio, and Willacy. The Panhandle region is defined as the following counties: Armstrong, Bailey, Briscoe, Carson, Castro, Childress, Cochran, Collingsworth, Crosby, Dallam, Deaf Smith, Dickens, Donley, Floyd, Gray, Hale, Hall, Hansford, Hartley, Hemphill, Hockley, Hutchinson, Lamb, Lipscomb, Lubbock, Moore, Motley, Ochiltree, Oldham, Parmer, Potter, Randall, Roberts, Sherman, Swisher, and Wheeler. The "Other" WInd Region consists of all other counties in the ERCOT Region. The assigned Wind Region for each WGR is indicated as "WIND-C," "WIND-P," or "WIND-O" in the Fuel columns of the summer/winter Capacities tabs.

## Executive_Summary
CDR Report - Executive Summary
CDR Report Background
The main purpose of the CDR report is to provide forecasted Planning Reserve Margins for the ERCOT summer and winter Peak Load Seasons (June through September, and December through February, respectively). The Planning Reserve Margin represents the percentage of resource capacity, in excess of firm electricity demand, available to cover uncertainty in future demand, generator availability and new resource supply. Firm demand accounts for load reductions available through interruptible load programs controlled by ERCOT as well as incremental load reductions from rooftop solar systems not accounted for in the load forecast model. The methodologies used to develop Planning Reserve Margins and other elements of the CDR report are outlined in the ERCOT Nodal Protocols, Section 3.2.6 (https://www.ercot.com/files/docs/2023/03/31/03-040123_Nodal.docx). ERCOT's load forecasts are based on normal weather conditions and determined by the methodologies described in the 2023 Long-Term Load Forecast Report posted on ERCOT's Load Forecast webpage in late December (https://www.ercot.com/files/docs/2023/01/18/2023-LTLF-Report.pdf).
Resource data comes from generation capacity developers and owners as reported in ERCOT's Resource Integration and Ongoing Operations (RIOO) system, as well as other data collection mechanisms described in the ERCOT Protocols.
Note that the CDR is not intended for characterizing the risk of capacity scarcity conditions from a real-time operations perspective.
Highlights
The forecasted peak demand for summer 2024 is 85,029 MW, while the firm peak demand (which includes the impact of curtailable load programs) is 81,643 MW. The winter 2024-25 peak demand forecast is 71,547 MW and firm peak demand forecast is 68,835 MW.
The peak demand forecast incorporates expected load increases during the seasonal peak demand hours due to the interconnection of Large Loads (such as crypto-mining facilities) to Transmission Service Provider networks. For this report, that forecast utilizes an assumption that LFLs are only consuming 10% of their total load. There are also Large Loads, totalling approximately 760 MW, that have been connected directly to co-located generation plants. For this CDR report, such co-located Large Loads are not netted against the generation capacities and are thus assumed to be fully curtailable if needed by ERCOT when reserve capacity is tight. This is an interim CDR planning assumption to be used until ERCOT implements a forecast methodology for addressing Large Loads in Reserve Margins. Note that this is different from the SARA which utilizes an interim short term forecast based on historical prices during tight grid conditions. ERCOT has also adopted the policy of not identifying the generating units with co-located Large Loads in the CDR and SARA until formal reporting rules have been adopted.
The Planning Reserve Margin for summer 2024 is forecasted to be 34.1%, representing a 5.8 percentage point decrease relative to the 39.9% margin reported in the November 2022 CDR report. This decrease is due mainly to delays of planned projects that were previously expected to be in service by July 1, 2024. The Reserve Margin rises to 44.4% for summer 2025, largely reflecting solar capacity additions, much of which represents project delays from prior years. The 'Planned Resource Scenarios' tab provides smaller planned resource amounts and lower Reserve Margins based on more stringent eligibility criteria for including planned resources in the CDR.
Planned resource capacity expected by July 2024 totals 26,230 MW, and of this total,14,038 MW are expected to be available during peak load periods. This includes 1,335 MW of summer-rated gas-fired resources, 542 MW of wind resources, and 12,161 MW of solar resources. These amounts of solar and wind capacity are what ERCOT expects to be available on an average basis during seasonal peak demand hours (the peak-average capacity contribution). Since the November 2022 CDR was released, two new gas-fired resources (totaling 233 MW) have qualified to be included in this CDR.
ERCOT also forecasts 10,340 MW of installed battery storage capacity by July 2024. ERCOT protocols currently don't include a methodology for determining the peak-average capacity contribution of battery storage, so the contribution in this CDR is officially reported as zero MW. ERCOT developed an interim capacity contribution methodology for the SARA reports. The summer 2023 capacity contribution percentage is 17.9% based on the interim method. Applying this percentage to the summer 2024 installed capacity yields a capacity contribution of 1,851 MW. ERCOT is developing a capacity contribution methodology for future CDR reports.
Pending U.S. Environmental Protection Agency Rulemakings
ERCOT and thermal generation owners are closely monitoring the potential impacts of the U.S. Environmental Protection Agency’s March 15th approval of its “Good Neighbor Plan” for reducing cross-state emissions of ozone-forming nitrogen oxides (NOx). The Plan imposes NOx budgets for Texas for the 2023 through 2029 summer ozone seasons, with the budgets significantly decreasing over the next several years. (Ozone seasons start May 1 and end September 30.) On May 1, 2023, the Fifth Circuit court granted a stay of the EPA's denial of the Texas State Implementation Plan (SIP) in response to a motion filed by Texas, Louisiana, and other parties claiming irreparable harm starting as early as the 2023 ozone season. The stay halts the Good Neighbor Plan until after the SIP denial is reviewed.
In addition to the Good Neighbor Plan, the EPA also recently proposed new standards for mercury and other toxic air emissions (MATS). Other pending rulemakings include Coal Combustion Residuals (CCRs, or coal ash) standards and guidelines for wastewater discharge. The full implications of these rulemakings are still being studied by generation owners, and there is uncertainty regarding the timing impacts due to pending and possible future litigation efforts. Nevertheless, it is likely that a several coal- and gas-fired generation units in the ERCOT region will retire during the next several years due to compliance costs. The 'Unconfirmed Retirement Capacity' tab lists units for which a public retirement announcement has been made and confirmed by the generation owners. As retirement plans for units impacted by these regulatory actions become known, ERCOT will update the unconfirmed planned unit retirement list accordingly.
New "Peak Load Hour vs. High Net Load Hour" Scenario Tab
A new scenario tab has been added (Peak v High Net Peak 2024) that compares the summer 2024 summary tab column with a version based on load, wind and solar capacity values for a high Net Peak hour, hour-ending 8:00 PM. This comparison is intended to show reserve capacity availability during the evening hour that typically experiences the largest drop-off in solar production. This tab also shows the reserve margin impact of including an energy storage capacity contribution based on the interim methodology used for the Summer 2023 Assessment of Resource Adequacy (SARA).

## SummerSummary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Summer Summary: 2024-2033
These columns indicate the impact of not adding any new resources during the latter half of the CDR forecast period. Project developers typically submit interconnection requests no more than two to four years before the facilities are expected to enter commercial operations.
Load Forecast, MW: |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
| Summer Peak Demand (based on normal weather) |  | 85029.0907 | 86715.4358 | 88377.7049 | 90035.7478 | 90879.4264 | 91684.7388 | 92451.8092 | 93166.7295 | 93853.2809 | 94530
| plus: Energy Efficiency Program Savings Forecast |  | 3310.5748 | 3687.4731 | 4064.3713 | 4441.2696 | 4818.1679 | 5195.0661 | 5571.9644 | 5948.8626 | 6325.7609 | 6702.6591
| Total Summer Peak Demand (before Reductions from Energy Efficiency Programs) |  | 88339.6656 | 90402.9089 | 92442.0762 | 94477.0174 | 95697.5943 | 96879.8049 | 98023.7735 | 99115.5921 | 100179.0418 | 101232.6591
| less: Incremental Rooftop PV Forecast |  | -703.6488 | -974.95 | -1246.2512 | -1517.5524 | -1789.5969 | -2060.8981 | -2332.1993 | -2603.5005 | -2875.545 | -3147
| less: Load Resources providing Responsive Reserves |  | -1409.64 | -1409.64 | -1409.64 | -1409.64 | -1409.64 | -1409.64 | -1409.64 | -1409.64 | -1409.64 | -1409.64
| less: Load Resources providing Non-Spinning Reserves |  | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502
| less: Emergency Response Service (10- and 30-min ramp products) |  | -893.9994 | -893.9994 | -893.9994 | -893.9994 | -893.9994 | -893.9994 | -893.9994 | -893.9994 | -893.9994 | -893.9994
| less: TDSP Standard Offer Load Management Programs |  | -330.48 | -330.48 | -330.48 | -330.48 | -330.48 | -330.48 | -330.48 | -330.48 | -330.48 | -330.48
| less: Energy Efficiency Program Savings Forecast |  | -3310.5748 | -3687.4731 | -4064.3713 | -4441.2696 | -4818.1679 | -5195.0661 | -5571.9644 | -5948.8626 | -6325.7609 | -6702.6591
| Firm Peak Demand, MW |  | 81643.3723 | 83058.4163 | 84449.3841 | 85836.1259 | 86407.76 | 86941.7711 | 87437.5403 | 87881.1594 | 88295.6663 | 88700.9304
Resources, MW: |  |  | 2024: Expected Capacity Available for Summer Peak Demands
|  | Cumulative Installed Capacity Ratings by 2027 (see Note) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
| Installed Summer-rated Capacity, Thermal | 73239.33 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3
| Hydroelectric, Peak Average Capacity Contribution (84% of installed capacity) | 563.3 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044
| Switchable Capacity | 3840.12 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490
| less: Switchable Capacity Unavailable to ERCOT | -757 | -692 | -692 | -692 | -542 | -542 | -542 | -542 | -542 | -542 | -542
| Available Mothballed Capacity | 712.75 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5
| Capacity from Private Use Networks | 9575 | 2868.925 | 2868.925 | 2868.925 | 2863.925 | 2863.925 | 2863.925 | 2863.925 | 2863.925 | 2863.925 | 2863.925
| Coastal Wind, Peak Average Capacity Contribution (60% of installed capacity) | 5436.37 | 3258.12 | 3258.12 | 3258.12 | 3258.12 | 3258.12 | 3258.12 | 3258.12 | 3258.12 | 3258.12 | 3258.12
| Panhandle Wind, Peak Average Capacity Contribution (30% of installed capacity) | 4410.43 | 1322.31 | 1322.31 | 1322.31 | 1322.31 | 1322.31 | 1322.31 | 1322.31 | 1322.31 | 1322.31 | 1322.31
| Other Wind, Peak Average Capacity Contribution (21% of installed capacity) | 27896.15 | 5846.652 | 5846.652 | 5846.652 | 5846.652 | 5846.652 | 5846.652 | 5846.652 | 5846.652 | 5846.652 | 5846.652
| Solar Utility-Scale, Peak Average Capacity Contribution (79% of installed capacity) | 15658.81 | 12263.802 | 12263.802 | 12263.802 | 12263.802 | 12263.802 | 12263.802 | 12263.802 | 12263.802 | 12263.802 | 12263.802
| Storage, Peak Average Capacity Contribution | 3285.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity Pending Retirement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, MW | 143860.82 | 94628.0134 | 94628.0134 | 94628.0134 | 94773.0134 | 94773.0134 | 94773.0134 | 94773.0134 | 94773.0134 | 94773.0134 | 94773.0134
| Non-Synchronous Ties (Based on average net import contribution during summer 2019 EEA events) | 1220 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974
| Planned Resources (not wind, solar or storage) with Signed IA, Air Permits and Adequate Water Supplies | 1683.6 | 1335.1 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (60% of installed capacity) | 461.8 | 0 | 277.08 | 277.08 | 277.08 | 277.08 | 277.08 | 277.08 | 277.08 | 277.08 | 277.08
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution (30% of installed capacity) | 696.7 | 159.3 | 209.01 | 209.01 | 209.01 | 209.01 | 209.01 | 209.01 | 209.01 | 209.01 | 209.01
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution (21% of installed capacity) | 2947.8 | 382.557 | 619.038 | 619.038 | 619.038 | 619.038 | 619.038 | 619.038 | 619.038 | 619.038 | 619.038
| Planned Solar Utility-Scale, Peak Average Capacity Contribution (79% of installed capacity) | 30232.7 | 12160.549 | 21749.095 | 23725.833 | 23883.833 | 23883.833 | 23883.833 | 23883.833 | 23883.833 | 23883.833 | 23883.833
| Planned Storage, Peak Average Capacity Contribution | 10788.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Planned Generation Capacity, MW | 46810.8 | 14037.506 | 24422.023 | 26398.761 | 26556.761 | 26556.761 | 26556.761 | 26556.761 | 26556.761 | 26556.761 | 26556.761
| Total Capacity, MW | 191891.62 | 109515.4934 | 119900.0104 | 121876.7484 | 122179.7484 | 122179.7484 | 122179.7484 | 122179.7484 | 122179.7484 | 122179.7484 | 122179.7484
|  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
| Reserve Margin |  | 34.14% | 44.36% | 44.32% | 42.34% | 41.4% | 40.53% | 39.73% | 39.03% | 38.38% | 37.74%
(Total Resources - Firm Load Forecast) / Firm Load Forecast
Note on Installed Capacities: Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer.

## SummerCapacities
| Unit Megawatt Capacities - Summer | [7 empty] | SUMMER CAPACITY (MW)
| UNIT NAME | INR | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | INSTALLED CAPACITY RATING (MW) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1269 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1269 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1365 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1293.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1365 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 650 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 615 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 615 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599
11 | FAYETTE POWER U2 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 460 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 437
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 555 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 922 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 893 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 956.8 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 893 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 893 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 893 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 916.8 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 916.8 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 430 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 1008 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 174.6 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 174.6 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 734.1 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 734.1 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 614.6 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 653.99 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 222 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
35 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 352.8 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 351 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 242 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
40 | BEACHWOOD POWER STATION U1 |  | BCH_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
41 | BEACHWOOD POWER STATION U2 |  | BCH_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
42 | BEACHWOOD POWER STATION U3 |  | BCH_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
43 | BEACHWOOD POWER STATION U4 |  | BCH_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
44 | BEACHWOOD POWER STATION U5 |  | BCH_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
45 | BEACHWOOD POWER STATION U6 |  | BCH_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
46 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
47 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
48 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 188.7 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
49 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 94.95 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5
50 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 254.15 | 213.5 | 213.5 | 213.5 | 213.5 | 213.5 | 213.5 | 213.5 | 213.5 | 213.5 | 213.5
51 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7
52 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7
53 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 275.57 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9
54 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-CC | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
55 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-CC | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
56 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
57 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
58 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
59 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
60 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
61 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
62 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
63 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 765 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
64 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 765 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
65 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5
66 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8
67 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 82.1 | 82.1 | 82.1 | 82.1 | 82.1 | 82.1 | 82.1 | 82.1 | 82.1 | 82.1
68 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 75.9 | 75.9 | 75.9 | 75.9 | 75.9 | 75.9 | 75.9 | 75.9 | 75.9 | 75.9
69 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 105 | 103.2 | 103.2 | 103.2 | 103.2 | 103.2 | 103.2 | 103.2 | 103.2 | 103.2 | 103.2
70 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 108.8 | 107.6 | 107.6 | 107.6 | 107.6 | 107.6 | 107.6 | 107.6 | 107.6 | 107.6 | 107.6
71 | COLORADO BEND II CTG 7 |  | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3
72 | COLORADO BEND II CTG 8 |  | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335
73 | COLORADO BEND II STG 9 |  | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 508.5 | 478.4 | 478.4 | 478.4 | 478.4 | 478.4 | 478.4 | 478.4 | 478.4 | 478.4 | 478.4
74 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
75 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
76 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
77 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2002 | 150 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
78 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 48 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
79 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
80 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 120 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
81 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
82 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
83 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
84 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
85 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
86 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
87 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
88 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
89 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
90 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
91 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
92 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
93 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 199 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
94 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 274.5 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287
95 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
96 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
97 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
98 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
99 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
100 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
101 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 202 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
102 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
103 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 140 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
104 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
105 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
106 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
107 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
108 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
109 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
110 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 204 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
111 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
112 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
113 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
114 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
115 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
116 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
117 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406
118 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406
119 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
120 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
121 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
122 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
123 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
124 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
125 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 129 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
126 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 225 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
127 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 387 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
128 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
129 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
130 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
131 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
132 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
133 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
134 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
135 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
136 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
137 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
138 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
139 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 100 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
140 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
141 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
142 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
143 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
144 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198
145 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198
146 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375
147 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
148 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
149 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
150 | HAYS ENERGY FACILITY CSG 2 | 21INR0527 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
151 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
152 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213
153 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149
154 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149
155 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 198.05 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
156 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
157 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
158 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
159 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
160 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 320.6 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289 | 289
161 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 320.6 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
162 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 185 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
163 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 107 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
164 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 397 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
165 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 531 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523
166 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
167 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
168 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
169 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
170 | LAMAR ENERGY CENTER STG 1 | 23INR0486 | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
171 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
172 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1
173 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3
174 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
175 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
176 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
177 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
178 | LIGNIN (CHAMON 2) U1 |  | LIG_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5
179 | LIGNIN (CHAMON 2) U2 |  | LIG_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5
180 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
181 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
182 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 204 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
183 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
184 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
185 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 258.4 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236
186 | MIDLOTHIAN ENERGY FACILITY CTG 1 | 23INR0489 | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 229
187 | MIDLOTHIAN ENERGY FACILITY CTG 2 | 21INR0534 | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227
188 | MIDLOTHIAN ENERGY FACILITY CTG 3 | 22INR0543 | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227
189 | MIDLOTHIAN ENERGY FACILITY CTG 4 | 22INR0523 | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227
190 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241
191 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243
192 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
193 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
194 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
195 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
196 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
197 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
198 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
199 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
200 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
201 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
202 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 351 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
203 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 445 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
204 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 435 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410
205 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 176 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7
206 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 176 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2
207 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 176 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7
208 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 176 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2
209 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 224 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206
210 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 224 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206
211 | OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
212 | OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
213 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199
214 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199
215 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287 | 287
216 | PANDA TEMPLE I POWER CTG 1 | 22INR0533 | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 232 | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 223
217 | PANDA TEMPLE I POWER CTG 2 | 22INR0533 | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 232 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
218 | PANDA TEMPLE I POWER STG 1 | 22INR0533 | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 326
219 | PANDA TEMPLE II POWER CTG 1 | 23INR0524 | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 232 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2
220 | PANDA TEMPLE II POWER CTG 2 | 23INR0524 | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 232 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2
221 | PANDA TEMPLE II POWER STG 1 | 23INR0524 | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7
222 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
223 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
224 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 90 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
225 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5
226 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5
227 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 195.5 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4
228 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
229 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
230 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
231 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
232 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 89.4 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
233 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
234 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
235 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 89.4 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
236 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 89.4 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
237 | PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
238 | PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
239 | PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
240 | PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
241 | PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
242 | PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
243 | PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
244 | PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
245 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
246 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
247 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
248 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
249 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
250 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
251 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 25 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5
252 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 43.2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
253 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
254 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
255 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
256 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
257 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98.1 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
258 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98.1 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
259 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
260 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
261 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 74.98 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
262 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 113.61 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
263 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 216.01 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
264 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 88.4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
265 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 113.64 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
266 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 156.6 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
267 | RABBS POWER STATION U1 |  | RAB_UNIT1 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
268 | RABBS POWER STATION U2 |  | RAB_UNIT2 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
269 | RABBS POWER STATION U3 |  | RAB_UNIT3 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
270 | RABBS POWER STATION U4 |  | RAB_UNIT4 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
271 | RABBS POWER STATION U5 |  | RAB_UNIT5 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
272 | RABBS POWER STATION U6 |  | RAB_UNIT6 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
273 | RABBS POWER STATION U7 |  | RAB_UNIT7 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
274 | RABBS POWER STATION U8 |  | RAB_UNIT8 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
275 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
276 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
277 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
278 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
279 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5
280 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
281 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
282 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 373.16 | 303 | 303 | 303 | 303 | 303 | 303 | 303 | 303 | 303 | 303
283 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
284 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
285 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
286 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 41.98 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
287 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
288 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
289 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
290 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
291 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
292 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
293 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 198.9 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142
294 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
295 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
296 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 191 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139
297 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 60.5 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
298 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
299 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
300 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 136 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
301 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
302 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 351 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336
303 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 25.71 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
304 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 25.71 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
305 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 177 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
306 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 479 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
307 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 16.32 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
308 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
309 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
310 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
311 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
312 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
313 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
314 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
315 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
316 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
317 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
318 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
319 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
320 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
321 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
322 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
323 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
324 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3
325 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3
326 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3
327 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 143.65 | 124.9 | 124.9 | 124.9 | 124.9 | 124.9 | 124.9 | 124.9 | 124.9 | 124.9 | 124.9
328 | TEXAS GULF SULPHUR CTG 1 |  | TGS_GT01 | WHARTON | GAS-GT | SOUTH | 1985 | 94 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5
329 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 239 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
330 | TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
331 | TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
332 | TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
333 | TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
334 | TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
335 | TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
336 | TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
337 | TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
338 | TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
339 | TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
340 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
341 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
342 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
343 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
344 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 225 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217
345 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
346 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 420 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412
347 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
348 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
349 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
350 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
351 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 196.86 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
352 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 180.2 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
353 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 16.32 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
354 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
355 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
356 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 299.2 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
357 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 580.5 | 527 | 527 | 527 | 527 | 527 | 527 | 527 | 527 | 527 | 527
358 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
359 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
360 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
361 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
362 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
363 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
364 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
365 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
366 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 275 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4
367 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 275 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4
368 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 290 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298
369 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 238.5 | 238.5 | 238.5 | 238.5 | 238.5 | 238.5 | 238.5 | 238.5 | 238.5 | 238.5
370 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 230.5 | 230.5 | 230.5 | 230.5 | 230.5 | 230.5 | 230.5 | 230.5 | 230.5 | 230.5
371 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 300 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268
372 | WOLF HOLLOW 2 CTG 4 |  | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 360 | 327.8 | 327.8 | 327.8 | 327.8 | 327.8 | 327.8 | 327.8 | 327.8 | 327.8 | 327.8
373 | WOLF HOLLOW 2 CTG 5 |  | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 360 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3
374 | WOLF HOLLOW 2 STG 6 |  | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 511.2 | 458.3 | 458.3 | 458.3 | 458.3 | 458.3 | 458.3 | 458.3 | 458.3 | 458.3 | 458.3
375 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 116.45 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
376 | BIOENERGY AUSTIN-WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
377 | BIOENERGY TEXAS-COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
378 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
379 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
380 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
381 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
382 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
383 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
384 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
385 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
386 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 72744.83 | 64709.9 | 64709.9 | 64709.9 | 64709.9 | 64709.9 | 64709.9 | 64709.9 | 64709.9 | 64709.9 | 64709.9
387
388 | Operational Resources - Synchronized but not Approved for Commercial Operations (Thermal)
389 | BRANDON (LP&L) (DGR) | 21INR0201 | BRANDON_UNIT1 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
390 | BROTMAN POWER STATION U3 | 23INR0095 | BTM_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
391 | BROTMAN POWER STATION U4 | 23INR0095 | BTM_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
392 | BROTMAN POWER STATION U5 | 23INR0095 | BTM_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
393 | BROTMAN POWER STATION U6 | 23INR0095 | BTM_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
394 | COLORADO BEND ENERGY CENTER CTG 11 | 21INR0512 | CBEC_GT11 | WHARTON | GAS-GT | HOUSTON | 2023 | 41.65 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
395 | COLORADO BEND ENERGY CENTER CTG 12 | 21INR0512 | CBEC_GT12 | WHARTON | GAS-GT | HOUSTON | 2023 | 41.65 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
396 | R MASSENGALE CTG 1 (LP&L) | 21INR0202 | MASSENGL_G6 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
397 | R MASSENGALE CTG 2 (LP&L) | 21INR0202 | MASSENGL_G7 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
398 | R MASSENGALE STG (LP&L) | 21INR0202 | MASSENGL_G8 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 58.9 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
399 | TY COOKE CTG 1 (LP&L) | 21INR0506 | TY_COOKE_GT2 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 18.7 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
400 | TY COOKE CTG 2 (LP&L) | 21INR0506 | TY_COOKE_GT3 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 26.6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
401 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 494.5 | 381.4 | 381.4 | 381.4 | 381.4 | 381.4 | 381.4 | 381.4 | 381.4 | 381.4 | 381.4
402
403 | Operational Capacity Thermal Unavailable due to Extended Outage or Derate |  | THERMAL_UNAVAIL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
404 | Operational Capacity Thermal Total |  | THERMAL_OPERATIONAL |  |  |  |  | 73239.33 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3 | 65091.3
405
406 | Operational Resources (Hydro)
407 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 34.7 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
408 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 34.7 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
409 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
410 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
411 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
412 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
413 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 18.3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
414 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 50.8 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
415 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 50.8 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
416 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
417 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
418 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
419 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
420 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 27 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
421 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 27 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
422 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
423 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
424 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
425 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
426 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
427 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
428 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
429 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
430 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
431 | Operational Capacity Total (Hydro) | [6 empty] | 549.6 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4
432 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 549.6 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464
433
434 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
435 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
436 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDTP_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
437 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
438 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
439 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
440 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
441 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  |  |  |  | 19.7 | 16.399 | 16.399 | 16.399 | 16.399 | 16.399 | 16.399 | 16.399 | 16.399 | 16.399 | 16.399
442
443 | Operational Capacity Hydroelectric Unavailable due to Extended Outage or Derate |  | HYDRO_UNAVAIL |  |  |  |  | -6 | -4.9946 | -4.9946 | -4.9946 | -4.9946 | -4.9946 | -4.9946 | -4.9946 | -4.9946 | -4.9946 | -4.9946
444 | Operational Capacity Hydroelectric Total |  | HYDRO_OPERATIONAL |  |  |  |  | 563.3 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044
445
446 | Operational Resources (Switchable)
447 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
448 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
449 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
450 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
451 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
452 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
453 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
454 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
455 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
456 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 179 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
457 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
458 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 179 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
459 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402
460 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
461 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
462 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310
463 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
464 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152
465 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311 | 311
466 | Switchable Capacity Total | [6 empty] | 3840.12 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490 | 3490
467
468 | Switchable Capacity Unavailable to ERCOT
469 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
470 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
471 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
472 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -202 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190
473 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -202 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190
474 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101_UNAVAIL | FANNIN | GAS-CC | NORTH | 2003 | -185 | -150 | -150 | -150 | 0 | 0 | 0 | 0 | 0 | 0 | 0
475 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -757 | -692 | -692 | -692 | -542 | -542 | -542 | -542 | -542 | -542 | -542
476
477 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | GAS |  |  | 712.75 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5
478
479 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 9575 | 2940 | 2940 | 2940 | 2940 | 2940 | 2940 | 2940 | 2940 | 2940 | 2940
480 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  |  | -71.075 | -71.075 | -71.075 | -76.075 | -76.075 | -76.075 | -76.075 | -76.075 | -76.075 | -76.075
481
482 | Operational Resources (Wind)
483 | WESTERN TRAIL WIND (AJAX WIND) U1 |  | AJAXWIND_UNIT1 | WILBARGER | WIND-O | WEST | 2022 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6
484 | WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WILBARGER | WIND-O | WEST | 2022 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
485 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
486 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8
487 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7
488 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.83 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
489 | AQUILLA LAKE WIND U1 |  | AQUILLA_U1_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
490 | AQUILLA LAKE WIND U2 |  | AQUILLA_U1_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4
491 | AQUILLA LAKE 2 WIND U1 |  | AQUILLA_U2_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
492 | AQUILLA LAKE 2 WIND U2 |  | AQUILLA_U2_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8
493 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.12 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1
494 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.64 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6
495 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.26 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3
496 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
497 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
498 | BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | ANDREWS | WIND-O | WEST | 2021 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2
499 | BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | ANDREWS | WIND-O | WEST | 2021 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5
500 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
501 | BLUE SUMMIT WIND 1 A | 22INR0550 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 132.84 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8
502 | BLUE SUMMIT WIND 1 B | 22INR0550 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 6.96 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
503 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 92.5 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
504 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.86 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5
505 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.7 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
506 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 186.5 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4
507 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
508 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.85 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8
509 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
510 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
511 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9
512 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7
513 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
514 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
515 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
516 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
517 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 89 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
518 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
519 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
520 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4
521 | CACTUS FLATS WIND U1 |  | CFLATS_U1 | CONCHO | WIND-O | WEST | 2022 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4
522 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1
523 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
524 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 134.42 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
525 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 123.6 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
526 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1
527 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7
528 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
529 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9
530 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | STERLING | WIND-O | WEST | 2008 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
531 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
532 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
533 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.25 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3
534 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
535 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
536 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4
537 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
538 | CRANELL WIND |  | CRANELL_UNIT1 | REFUGIO | WIND-C | COASTAL | 2022 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
539 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
540 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
541 | DESERT SKY WIND 1 A | 17INR0070 | DSKYWND1_UNIT_1A | PECOS | WIND-O | WEST | 2022 | 65.79 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1
542 | DESERT SKY WIND 1 B | 17INR0070 | DSKYWND2_UNIT_2A | PECOS | WIND-O | WEST | 2022 | 65.79 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
543 | DESERT SKY WIND 2 A | 17INR0070 | DSKYWND1_UNIT_1B | PECOS | WIND-O | WEST | 2022 | 23.93 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7
544 | DESERT SKY WIND 2 B | 17INR0070 | DSKYWND2_UNIT_2B | PECOS | WIND-O | WEST | 2022 | 14.74 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
545 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
546 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
547 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 101.2 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
548 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 99 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
549 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
550 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 101.31 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
551 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 134.29 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
552 | EL ALGODON ALTO W U1 |  | ALGODON_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6
553 | EL ALGODON ALTO W U2 |  | ALGODON_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
554 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2
555 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2
556 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
557 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8
558 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6
559 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.48 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5
560 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8
561 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
562 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
563 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
564 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
565 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
566 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
567 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4
568 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
569 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 21INR0532 | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
570 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 21INR0532 | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
571 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
572 | GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7
573 | GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9
574 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
575 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
576 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.93 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9
577 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 165.6 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
578 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9
579 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
580 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
581 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5
582 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
583 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
584 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
585 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
586 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
587 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 51.9 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
588 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3
589 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.4 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5
590 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3
591 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.5 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6
592 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.5 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
593 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 134.81 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
594 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 101.69 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
595 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
596 | HORSE HOLLOW WIND 2 | 17INR0053 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
597 | HORSE HOLLOW WIND 3 | 17INR0053 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4
598 | HORSE HOLLOW WIND 4 | 17INR0053 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
599 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
600 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
601 | INDIAN MESA WIND | 18INR0069 | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8
602 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.69 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
603 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
604 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
605 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
606 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
607 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.15 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2
608 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.55 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
609 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
610 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
611 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.42 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
612 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
613 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
614 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
615 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
616 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
617 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 159.96 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
618 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7
619 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.26 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3
620 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.85 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
621 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
622 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
623 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
624 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
625 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
626 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
627 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
628 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
629 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
630 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
631 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
632 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
633 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
634 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
635 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.83 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
636 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.46 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5
637 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
638 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
639 | MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | CONCHO | WIND-O | WEST | 2022 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
640 | MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | CONCHO | WIND-O | WEST | 2022 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
641 | MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | CONCHO | WIND-O | WEST | 2022 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
642 | MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | CONCHO | WIND-O | WEST | 2022 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
643 | MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | CONCHO | WIND-O | WEST | 2022 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
644 | MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | CONCHO | WIND-O | WEST | 2022 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
645 | MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | CONCHO | WIND-O | WEST | 2022 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
646 | MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | CONCHO | WIND-O | WEST | 2022 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
647 | MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | CONCHO | WIND-O | WEST | 2022 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8
648 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
649 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
650 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
651 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
652 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
653 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8
654 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
655 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.61 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
656 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
657 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
658 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
659 | OVEJA WIND U1 |  | OVEJA_G1 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
660 | OVEJA WIND U2 |  | OVEJA_G2 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
661 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9
662 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
663 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
664 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.19 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
665 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
666 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
667 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
668 | PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | HOWARD | WIND-O | WEST | 2022 | 106.92 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9
669 | PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | HOWARD | WIND-O | WEST | 2022 | 108.54 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5
670 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.85 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9
671 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.12 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
672 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7
673 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8
674 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
675 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
676 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
677 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
678 | PYRON WIND 1 | 23INR0525 | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
679 | PYRON WIND 2 | 23INR0525 | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5
680 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
681 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
682 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6
683 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7
684 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6
685 | RELOJ DEL SOL WIND U1 |  | RELOJ_UNIT1 | ZAPATA | WIND-O | SOUTH | 2022 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
686 | RELOJ DEL SOL WIND U2 |  | RELOJ_UNIT2 | ZAPATA | WIND-O | SOUTH | 2022 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
687 | RELOJ DEL SOL WIND U3 |  | RELOJ_UNIT3 | ZAPATA | WIND-O | SOUTH | 2022 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1
688 | RELOJ DEL SOL WIND U4 |  | RELOJ_UNIT4 | ZAPATA | WIND-O | SOUTH | 2022 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8
689 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
690 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.44 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4
691 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
692 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
693 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
694 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9
695 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9
696 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
697 | SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
698 | SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
699 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
700 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
701 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.25 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
702 | SAND BLUFF WIND U1 |  | MCDLD_SB1_2 | GLASSCOCK | WIND-O | WEST | 2022 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
703 | SAND BLUFF WIND U2 |  | MCDLD_SB3_282 | GLASSCOCK | WIND-O | WEST | 2022 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1
704 | SAND BLUFF WIND U3 |  | MCDLD_SB4_G87 | GLASSCOCK | WIND-O | WEST | 2022 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
705 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
706 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
707 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.24 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
708 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.05 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1
709 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1
710 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
711 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8
712 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
713 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
714 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
715 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8
716 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 101.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2
717 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 160.95 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
718 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
719 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
720 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 123.6 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
721 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
722 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 213.82 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2
723 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 166.52 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7
724 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 37.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
725 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8
726 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 105.3 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8
727 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 30.78 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
728 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 108.54 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6
729 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 119 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
730 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 105.8 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
731 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 80.5 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
732 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
733 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
734 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
735 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
736 | TG EAST WIND U1 |  | TRUSGILL_UNIT1 | KNOX | WIND-O | WEST | 2022 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
737 | TG EAST WIND U2 |  | TRUSGILL_UNIT2 | KNOX | WIND-O | WEST | 2022 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8
738 | TG EAST WIND U3 |  | TRUSGILL_UNIT3 | KNOX | WIND-O | WEST | 2022 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
739 | TG EAST WIND U4 |  | TRUSGILL_UNIT4 | KNOX | WIND-O | WEST | 2022 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2
740 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
741 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
742 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5
743 | TRENT WIND 1 A | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 38.25 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
744 | TRENT WIND 1 B |  | TRENT_UNIT_1B | NOLAN | WIND-O | WEST | 2018 | 15.59 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
745 | TRENT WIND 2 |  | TRENT_UNIT_2 | NOLAN | WIND-O | WEST | 2018 | 50.49 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5
746 | TRENT WIND 3 A |  | TRENT_UNIT_3A | NOLAN | WIND-O | WEST | 2018 | 38.25 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
747 | TRENT WIND 3 B |  | TRENT_UNIT_3B | NOLAN | WIND-O | WEST | 2018 | 13.79 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8
748 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4
749 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6
750 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
751 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 174.6 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
752 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6
753 | VENADO WIND U1 |  | VENADO_UNIT1 | ZAPATA | WIND-O | SOUTH | 2021 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
754 | VENADO WIND U2 |  | VENADO_UNIT2 | ZAPATA | WIND-O | SOUTH | 2021 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
755 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
756 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
757 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
758 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
759 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
760 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
761 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.91 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9
762 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.35 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3
763 | WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6
764 | WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2
765 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 59.8 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
766 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.34 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3
767 | WHITE MESA WIND U1 |  | WHMESA_UNIT1 | CROCKETT | WIND-O | WEST | 2022 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
768 | WHITE MESA 2 WIND U1 |  | WHMESA_UNIT2_23 | CROCKETT | WIND-O | WEST | 2022 | 13.92 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
769 | WHITE MESA 2 WIND U2 |  | WHMESA_UNIT2_28 | CROCKETT | WIND-O | WEST | 2022 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3
770 | WHITE MESA 2 WIND U3 |  | WHMESA_UNIT3_23 | CROCKETT | WIND-O | WEST | 2022 | 18.56 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
771 | WHITE MESA 2 WIND U4 |  | WHMESA_UNIT3_28 | CROCKETT | WIND-O | WEST | 2022 | 132.54 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5
772 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
773 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
774 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
775 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.62 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6
776 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
777 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
778 | Operational Capacity Total (Wind) | [6 empty] | 31558.05 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7
779
780 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 4862.27 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1
781 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 100 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
782
783 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4410.43 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7
784 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 100 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
785
786 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 22285.35 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9
787 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 100 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
788
789 | Operational Resources (Wind) - Synchronized but not Approved for Commercial Operations
790 | AGUAYO WIND U1 | 20INR0250 | AGUAYO_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 193.5 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9
791 | ANCHOR WIND U1 | 21INR0546 | ANCHOR_WIND1 | CALLAHAN | WIND-O | WEST | 2023 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
792 | ANCHOR WIND U2 | 21INR0387 | ANCHOR_WIND2 | CALLAHAN | WIND-O | WEST | 2023 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
793 | ANCHOR WIND U3 | 21INR0539 | ANCHOR_WIND3 | CALLAHAN | WIND-O | WEST | 2023 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
794 | ANCHOR WIND U4 | 21INR0539 | ANCHOR_WIND4 | CALLAHAN | WIND-O | WEST | 2023 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7
795 | ANCHOR WIND U5 | 22INR0562 | ANCHOR_WIND5 | CALLAHAN | WIND-O | WEST | 2023 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3
796 | APPALOOSA RUN WIND U1 | 20INR0249 | APPALOSA_UNIT1 | UPTON | WIND-O | WEST | 2023 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9
797 | APPALOOSA RUN WIND U2 | 20INR0249 | APPALOSA_UNIT2 | UPTON | WIND-O | WEST | 2023 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
798 | APOGEE WIND U1 | 21INR0467 | APOGEE_UNIT1 | THROCKMORTON | WIND-O | WEST | 2023 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
799 | APOGEE WIND U2 | 21INR0467 | APOGEE_UNIT2 | THROCKMORTON | WIND-O | WEST | 2023 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
800 | APOGEE WIND U3 | 21INR0467 | APOGEE_UNIT3 | THROCKMORTON | WIND-O | WEST | 2023 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
801 | APOGEE WIND U4 | 21INR0467 | APOGEE_UNIT4 | THROCKMORTON | WIND-O | WEST | 2023 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
802 | APOGEE WIND U5 | 21INR0467 | APOGEE_UNIT5 | THROCKMORTON | WIND-O | WEST | 2023 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
803 | APOGEE WIND U6 | 21INR0467 | APOGEE_UNIT6 | THROCKMORTON | WIND-O | WEST | 2023 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
804 | APOGEE WIND U7 | 21INR0467 | APOGEE_UNIT7 | THROCKMORTON | WIND-O | WEST | 2023 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
805 | BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | CALLAHAN | WIND-O | WEST | 2023 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
806 | BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | CALLAHAN | WIND-O | WEST | 2023 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
807 | BLACKJACK CREEK WIND U1 | 20INR0068 | BLACKJAK_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
808 | BLACKJACK CREEK WIND U2 | 20INR0068 | BLACKJAK_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
809 | BOARD CREEK WP U1 | 21INR0324 | BOARDCRK_UNIT1 | NAVARRO | WIND-O | NORTH | 2023 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8
810 | BOARD CREEK WP U2 | 21INR0324 | BOARDCRK_UNIT2 | NAVARRO | WIND-O | NORTH | 2023 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4
811 | COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | SCURRY | WIND-O | WEST | 2023 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
812 | COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | SCURRY | WIND-O | WEST | 2023 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6
813 | COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | SCURRY | WIND-O | WEST | 2023 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
814 | EL SUAZ RANCH U1 | 20INR0097 | ELSAUZ_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
815 | EL SUAZ RANCH U2 | 20INR0097 | ELSAUZ_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
816 | FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2
817 | FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
818 | FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | BEE | WIND-O | SOUTH | 2023 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
819 | HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | GLASSCOCK | WIND-O | WEST | 2023 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
820 | INERTIA WIND U1 | 22INR0326 | INRT_W_UNIT1 | HASKELL | WIND-O | WEST | 2023 | 67.68 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7
821 | INERTIA WIND U2 | 22INR0326 | INRT_W_UNIT2 | HASKELL | WIND-O | WEST | 2023 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
822 | INERTIA WIND U3 | 22INR0326 | INRT_W_UNIT3 | HASKELL | WIND-O | WEST | 2023 | 205.86 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9
823 | LACY CREEK WIND U1 | 18INR0043 | LACY_CRK_UNIT1 | GLASSCOCK | WIND-O | WEST | 2023 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4
824 | LACY CREEK WIND U2 | 18INR0043 | LACY_CRK_UNIT2 | GLASSCOCK | WIND-O | WEST | 2023 | 15.12 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
825 | LACY CREEK WIND U3 | 18INR0043 | LACY_CRK_UNIT3 | GLASSCOCK | WIND-O | WEST | 2023 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2
826 | LACY CREEK WIND U4 | 18INR0043 | LACY_CRK_UNIT4 | GLASSCOCK | WIND-O | WEST | 2023 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6
827 | LAS MAJADAS WIND U1 | 17INR0035 | LMAJADAS_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
828 | LAS MAJADAS WIND U2 | 17INR0035 | LMAJADAS_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
829 | LAS MAJADAS WIND U3 | 17INR0035 | LMAJADAS_UNIT3 | WILLACY | WIND-C | COASTAL | 2023 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6
830 | MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | NOLAN | WIND-O | WEST | 2023 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4
831 | MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | STARR | WIND-O | SOUTH | 2023 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
832 | PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | LIMESTONE | WIND-O | NORTH | 2023 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
833 | PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | LIMESTONE | WIND-O | NORTH | 2023 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
834 | PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2
835 | PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | MILLS | WIND-O | NORTH | 2023 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
836 | VORTEX WIND U1 | 20INR0120 | VORTEX_WIND1 | THROCKMORTON | WIND-O | WEST | 2023 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
837 | VORTEX WIND U2 | 20INR0120 | VORTEX_WIND2 | THROCKMORTON | WIND-O | WEST | 2023 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2
838 | VORTEX WIND U3 | 20INR0120 | VORTEX_WIND3 | THROCKMORTON | WIND-O | WEST | 2023 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4
839 | VORTEX WIND U4 | 20INR0120 | VORTEX_WIND4 | THROCKMORTON | WIND-O | WEST | 2023 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
840 | WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | FISHER | WIND-O | WEST | 2023 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4
841 | WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | FISHER | WIND-O | WEST | 2023 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5
842 | WILDWIND U1 | 20INR0033 | WILDWIND_UNIT1 | COOKE | WIND-O | NORTH | 2023 | 18.38 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4
843 | WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | COOKE | WIND-O | NORTH | 2023 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
844 | WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | COOKE | WIND-O | NORTH | 2023 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
845 | WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | COOKE | WIND-O | NORTH | 2023 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
846 | WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | COOKE | WIND-O | NORTH | 2023 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8
847 | YOUNG WIND U1 | 21INR0401 | YNG_WND_UNIT1 | YOUNG | WIND-O | WEST | 2023 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4
848 | YOUNG WIND U2 | 21INR0401 | YNG_WND_UNIT2 | YOUNG | WIND-O | WEST | 2023 | 152.28 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
849 | YOUNG WIND U3 | 21INR0401 | YNG_WND_UNIT3 | YOUNG | WIND-O | WEST | 2023 | 149.46 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
850 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 6184.9 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4
851
852 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Coastal Counties) |  | WIND_SYNCHRONIZED_C |  |  |  |  | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1
853 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_SYNC_PEAK_PCT_C | % |  |  |  | 100 | 60 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
854
855 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Panhandle Counties) |  | WIND_SYNCHRONIZED_P |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
856 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_SYNC_PEAK_PCT_P | % |  |  |  | 100 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
857
858 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Other Counties) |  | WIND_SYNCHRONIZED_O |  |  |  |  | 5610.8 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3
859 | Wind Peak Average Capacity Percentage (Other) |  | WIND_SYNC_PEAK_PCT_O | % |  |  |  | 100 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
860
861 | Operational Resources (Solar)
862 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
863 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
864 | ANSON SOLAR U1 |  | ANSON1_UNIT1 | JONES | SOLAR | WEST | 2022 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
865 | ANSON SOLAR U2 |  | ANSON1_UNIT2 | JONES | SOLAR | WEST | 2022 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
866 | ARAGORN SOLAR |  | ARAGORN_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 188.2 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
867 | AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | HASKELL | SOLAR | WEST | 2021 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9
868 | AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | HASKELL | SOLAR | WEST | 2021 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5
869 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1 | bar: SUMMER CAPACITY (MW) 2024 to SUMMER CAPACITY (MW) 2033
870 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 50 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
871 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
872 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
873 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
874 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
875 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
876 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
877 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
878 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
879 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
880 | BRIGHTSIDE SOLAR |  | BRIGHTSD_UNIT1 | BEE | SOLAR | SOUTH | 2022 | 53.4 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
881 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
882 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
883 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
884 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
885 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
886 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
887 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
888 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
889 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7
890 | CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | WEBB | SOLAR | SOUTH | 2021 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
891 | DANCIGER SOLAR U1 |  | DAG_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
892 | DANCIGER SOLAR U2 |  | DAG_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
893 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
894 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
895 | ELARA SOLAR |  | ELARA_SL_UNIT1 | FRIO | SOLAR | SOUTH | 2022 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4
896 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) |  | EGROVESL_UNIT1 | CRANE | SOLAR | WEST | 2023 | 109.5 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
897 | EUNICE SOLAR U1 |  | EUNICE_PV1 | ANDREWS | SOLAR | WEST | 2021 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6
898 | EUNICE SOLAR U2 |  | EUNICE_PV2 | ANDREWS | SOLAR | WEST | 2021 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1
899 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
900 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 152.5 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
901 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
902 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 126 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1
903 | GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | CONCHO | SOLAR | WEST | 2021 | 251.4 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
904 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 126.3 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6
905 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 132.2 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4
906 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
907 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
908 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
909 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2
910 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3
911 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5
912 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
913 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5
914 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
915 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
916 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7
917 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
918 | LILY SOLAR |  | LILY_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2021 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6
919 | LONGBOW SOLAR |  | LON_SOLAR1 | BRAZORIA | SOLAR | HOUSTON | 2022 | 78.2 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
920 | LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | BORDEN | SOLAR | WEST | 2021 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
921 | LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | BORDEN | SOLAR | WEST | 2021 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3
922 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
923 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
924 | MISAE SOLAR U1 |  | MISAE_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4
925 | MISAE SOLAR U2 |  | MISAE_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6
926 | NEBULA SOLAR (RAYOS DEL SOL) U1 |  | NEBULA_UNIT1 | CAMERON | SOLAR | COASTAL | 2022 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5
927 | NOBLE SOLAR U1 |  | NOBLESLR_SOLAR1 | DENTON | SOLAR | NORTH | 2022 | 148.8 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7
928 | NOBLE SOLAR U2 |  | NOBLESLR_SOLAR2 | DENTON | SOLAR | NORTH | 2022 | 130.2 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3
929 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
930 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
931 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.18 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2
932 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
933 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
934 | OCI ALAMO 4 SOLAR-BRACKETVILLE | 22INR0600 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.62 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
935 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
936 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2
937 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
938 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.04 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1
939 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 127.95 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1
940 | PHOENIX SOLAR |  | PHOENIX_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9
941 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
942 | PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
943 | PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
944 | PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | ANDREWS | SOLAR | WEST | 2021 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
945 | PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | ANDREWS | SOLAR | WEST | 2021 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
946 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
947 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
948 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
949 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
950 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 211.19 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
951 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
952 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
953 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PECOS | SOLAR | WEST | 2021 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222
954 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PECOS | SOLAR | WEST | 2021 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
955 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
956 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 155.44 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
957 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
958 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
959 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
960 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
961 | STRATEGIC SOLAR 1 |  | STRATEGC_UNIT1 | ELLIS | SOLAR | NORTH | 2022 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
962 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
963 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
964 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
965 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
966 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9
967 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9
968 | TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8
969 | TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | CULBERSON | SOLAR | WEST | 2021 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
970 | TPE ERATH SOLAR |  | DG_ERATH_ERATH21 | ERATH | SOLAR | NORTH | 2021 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
971 | VANCOURT SOLAR |  | VANCOURT_UNIT1 | CAMERON | SOLAR | COASTAL | 2023 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7
972 | VISION SOLAR 1 |  | VISION_UNIT1 | NAVARRO | SOLAR | NORTH | 2022 | 129.2 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
973 | WAGYU SOLAR |  | WGU_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2021 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
974 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
975 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
976 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
977 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
978 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
979 | WESTORIA SOLAR U1 |  | WES_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
980 | WESTORIA SOLAR U2 |  | WES_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
981 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
982 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
983 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
984 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
985 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
986 | Operational Capacity Total (Solar) | [6 empty] | 9991.32 | 9941.9 | 9941.9 | 9941.9 | 9941.9 | 9941.9 | 9941.9 | 9941.9 | 9941.9 | 9941.9 | 9941.9
987 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 100 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
988
989 | Operational Resources (Solar) - Synchronized but not Approved for Commercial Operations
990 | BIG STAR SOLAR U1 | 21INR0413 | BIG_STAR_UNIT1 | BASTROP | SOLAR | SOUTH | 2023 | 132.27 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
991 | BIG STAR SOLAR U2 | 21INR0413 | BIG_STAR_UNIT2 | BASTROP | SOLAR | SOUTH | 2023 | 70.83 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
992 | BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | GRIMES | SOLAR | NORTH | 2023 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
993 | BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | GRIMES | SOLAR | NORTH | 2023 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
994 | BPL FILES SOLAR | 20INR0164 | FILESSLR_PV1 | HILL | SOLAR | NORTH | 2023 | 146.09 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
995 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5
996 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3
997 | CROWN SOLAR | 21INR0323 | CRWN_SLR_UNIT1 | FALLS | SOLAR | NORTH | 2023 | 101.3 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7
998 | FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 179.5 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
999 | FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 171.8 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9
1000 | GOLINDA SOLAR | 21INR0434 | GOLINDA_UNIT1 | FALLS | SOLAR | NORTH | 2023 | 101.1 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
1001 | GRIZZLY RIDGE SOLAR | 21INR0375 | GRIZZLY_SOLAR1 | HAMILTON | SOLAR | NORTH | 2023 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1002 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b | HOVEY_UNIT2 | PECOS | SOLAR | WEST | 2023 | 7.41 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
1003 | JADE SOLAR U1 | 22INR0360 | JADE_SLR_UNIT1 | SCURRY | SOLAR | WEST | 2023 | 158.8 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
1004 | JADE SOLAR U2 | 22INR0360 | JADE_SLR_UNIT2 | SCURRY | SOLAR | WEST | 2023 | 162.4 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
1005 | MCLEAN (SHAKES) SOLAR | 19INR0073 | MCLNSLR_UNIT1 | DIMMIT | SOLAR | SOUTH | 2023 | 207.4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1006 | MUSTANG CREEK SOLAR U1 | 18INR0050 | MUSTNGCK_SOLAR1 | JACKSON | SOLAR | SOUTH | 2023 | 60.2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1007 | MUSTANG CREEK SOLAR U2 | 18INR0050 | MUSTNGCK_SOLAR2 | JACKSON | SOLAR | SOUTH | 2023 | 90.3 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
1008 | MYRTLE SOLAR U1 | 19INR0041 | MYR_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 171.6 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2
1009 | MYRTLE SOLAR U2 | 19INR0041 | MYR_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 149.6 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8
1010 | PISGAH RIDGE SOLAR U1 | 22INR0254 | PISGAH_SOLAR1 | NAVARRO | SOLAR | NORTH | 2023 | 189.4 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5
1011 | PISGAH RIDGE SOLAR U2 | 22INR0254 | PISGAH_SOLAR2 | NAVARRO | SOLAR | NORTH | 2023 | 64.4 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
1012 | PLAINVIEW SOLAR (RAMSEY SOLAR) U1 | 20INR0130 | PLN_UNIT1 | WHARTON | SOLAR | SOUTH | 2023 | 270 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
1013 | PLAINVIEW SOLAR (RAMSEY SOLAR) U2 | 20INR0130 | PLN_UNIT2 | WHARTON | SOLAR | SOUTH | 2023 | 270 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
1014 | RADIAN SOLAR U1 | 21INR0205 | RADN_SLR_UNIT1 | BROWN | SOLAR | NORTH | 2023 | 161.41 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9
1015 | RADIAN SOLAR U2 | 21INR0205 | RADN_SLR_UNIT2 | BROWN | SOLAR | NORTH | 2023 | 166.02 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9
1016 | RATLIFF SOLAR (CONCHO VALLEY SOLAR) | 21INR0384 | RATLIFF_SOLAR1 | TOM GREEN | SOLAR | WEST | 2023 | 162.43 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8
1017 | ROSELAND SOLAR U1 | 20INR0205 | ROSELAND_SOLAR1 | FALLS | SOLAR | NORTH | 2023 | 254 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
1018 | ROSELAND SOLAR U2 | 20INR0205 | ROSELAND_SOLAR2 | FALLS | SOLAR | NORTH | 2023 | 167.9 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3
1019 | ROSELAND SOLAR U3 | 22INR0506 | ROSELAND_SOLAR3 | FALLS | SOLAR | NORTH | 2023 | 86.1 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7
1020 | ROWLAND SOLAR I | 19INR0131 | ROW_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1021 | TAYGETE II SOLAR U1 | 21INR0233 | TAYGETE2_UNIT1 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
1022 | TAYGETE II SOLAR U2 | 21INR0233 | TAYGETE2_UNIT2 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
1023 | TAVENER (FORT BEND SOLAR) | 18INR0053 | TAV_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 143.61 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6
1024 | SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1025 | SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1026 | SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1027 | SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1028 | SUN VALLEY U1 | 19INR0169 | SUNVASLR_UNIT1 | HILL | SOLAR | NORTH | 2023 | 165.75 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8
1029 | SUN VALLEY U2 | 19INR0169 | SUNVASLR_UNIT2 | HILL | SOLAR | NORTH | 2023 | 86.19 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2
1030 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Solar) | [6 empty] | 5667.49 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9
1031 | Solar Peak Average Capacity Percentage |  | SOLAR_SYNC_PEAK_PCT | % |  |  |  | 100 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
1032
1033 | Operational Resources (Storage)
1034 | AZURE SKY BESS |  | AZURE_BESS1 | HASKELL | STORAGE | WEST | 2022 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6
1035 | BAT CAVE |  | BATCAVE_BES1 | MASON | STORAGE | SOUTH | 2021 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
1036 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
1037 | BRP ALVIN (DGR) |  | ALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1038 | BRP ANGELTON (DGR) |  | ANGLETON_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1039 | BRP BRAZORIA |  | BRAZORIA_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1040 | BRP DICKINSON (DGR) |  | DICKNSON_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1041 | BRP HEIGHTS (DGR) |  | HEIGHTTN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1042 | BRP LOOP 463 (DGR) |  | L_463S_UNIT1 | VICTORIA | STORAGE | SOUTH | 2023 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1043 | BRP LOPENO (DGR) |  | BRP_LOP1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1044 | BRP MAGNOLIA (DGR) |  | MAGNO_TN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1045 | BRP ODESSA SW (DGR) |  | ODESW_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1046 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1047 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1048 | BRP RANCHTOWN (DGR) |  | BRP_RNC1_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1049 | BRP SWEENY (DGR) |  | SWEENY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1050 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1051 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1052 | BYRD RANCH STORAGE |  | BYRDR_ES_BESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 50.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1053 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1054 | CATARINA BESS (DGR) |  | CATARINA_BESS | DIMMIT | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1055 | CEDARVALE BESS (DGR) |  | CEDRVALE_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1056 | CHISHOLM GRID |  | CHISMGRD_BES1 | TARRANT | STORAGE | NORTH | 2021 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1057 | COMMERCE ST ESS (DGR) |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1058 | COYOTE SPRINGS BESS (DGR) |  | COYOTSPR_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1059 | CROSSETT POWER U1 |  | CROSSETT_BES1 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1060 | CROSSETT POWER U2 |  | CROSSETT_BES2 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1061 | DECORDOVA BESS U1 |  | DCSES_BES1 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
1062 | DECORDOVA BESS U2 |  | DCSES_BES2 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
1063 | DECORDOVA BESS U3 |  | DCSES_BES3 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
1064 | DECORDOVA BESS U4 |  | DCSES_BES4 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
1065 | ENDURANCE PARK STORAGE |  | ENDPARKS_ESS1 | SCURRY | STORAGE | WEST | 2022 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1066 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2021 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
1067 | FAULKNER BESS (DGR) |  | FAULKNER_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1068 | FLAT TOP BATTERY (DGR) |  | FLAT_TOP_BESS1 | REEVES | STORAGE | WEST | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1069 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2021 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1070 | FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | REEVES | STORAGE | WEST | 2022 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1071 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 102.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1072 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2020 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
1073 | HOLCOMB BESS (DGR) |  | HOLCOMB_BESS | LA SALLE | STORAGE | SOUTH | 2023 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1074 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1075 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.25 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
1076 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
1077 | LILY STORAGE |  | LILY_BESS1 | KAUFMAN | STORAGE | NORTH | 2021 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7
1078 | LONESTAR BESS (DGR) |  | LONESTAR_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1079 | MADERO GRID U1 |  | MADERO_UNIT1 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1080 | MADERO GRID U2 (IGNACIO GRID) |  | MADERO_UNIT2 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1081 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
1082 | NOBLE STORAGE U1 |  | NOBLESLR_BESS1 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
1083 | NOBLE STORAGE U2 |  | NOBLESLR_BESS2 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
1084 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 36 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
1085 | NORTH COLUMBIA (ROUGHNECK STORAGE) |  | NCO_ESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 51.75 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1086 | NORTH FORK |  | NF_BRP_BES1 | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
1087 | PORT LAVACA BATTERY (DGR) |  | PRTLAVS_BESS1 | CALHOUN | STORAGE | COASTAL | 2020 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1088 | PROSPECT STORAGE (DGR) |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1089 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1090 | RABBIT HILL ENERGY STORAGE PROJECT (DGR) |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1091 | RATTLESNAKE BESS (DGR) |  | RTLSNAKE_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1092 | REPUBLIC ROAD STORAGE |  | RPUBRDS_ESS1 | ROBERTSON | STORAGE | NORTH | 2022 | 51.75 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1093 | SADDLEBACK BESS (DGR) |  | SADLBACK_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1094 | SARAGOSA BESS (DGR) |  | SGSA_BESS1 | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1095 | SCREWBEAN BESS (DGR) |  | SBEAN_BESS | CULBERSON | STORAGE | WEST | 2023 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1096 | SILICON HILL STORAGE U1 |  | SLCNHLS_ESS1 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1097 | SILICON HILL STORAGE U2 |  | SLCNHLS_ESS2 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1098 | SNYDER (DGR) |  | SNY_BESS_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1099 | SWEETWATER BESS (DGR) |  | SWT_BESS_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1100 | SWOOSE BATTERY (PYOTE) (DGR) |  | SWOOSE1_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1101 | SWOOSE II |  | SWOOSEII_BESS1 | WARD | STORAGE | WEST | 2022 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1102 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
1103 | TOYAH POWER STATION (DGR) |  | TOYAH_BESS | REEVES | STORAGE | WEST | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1104 | TRIPLE BUTTE (DGR) |  | TRIPBUT1_BELU1 | PECOS | STORAGE | WEST | 2021 | 9.18 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
1105 | WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1106 | WORSHAM BATTERY (DGR) |  | WORSHAM_BESS1 | REEVES | STORAGE | WEST | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1107 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
1108 | Operational Capacity Total (Storage) | [6 empty] | 2364.46 | 2335 | 2335 | 2335 | 2335 | 2335 | 2335 | 2335 | 2335 | 2335 | 2335
1109 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1110
1111 | Operational Resources (Storage) - Synchronized but not Approved for Commercial Operations
1112 | ANCHOR BESS U1 | 21INR0474 | ANCHOR_BESS1 | CALLAHAN | STORAGE | WEST | 2023 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2
1113 | ANCHOR BESS U2 | 21INR0474 | ANCHOR_BESS2 | CALLAHAN | STORAGE | WEST | 2023 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
1114 | BLUE JAY BESS | 23INR0019 | BLUEJAY_BESS1 | GRIMES | STORAGE | NORTH | 2023 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1115 | GOMEZ BESS (DGR) | 23INR0519 | GOMZ_BESS | REEVES | STORAGE | WEST | 2023 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1116 | HIGH LONESOME BESS | 20INR0280 | HI_LONEB_BESS1 | CROCKETT | STORAGE | WEST | 2023 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1117 | OLNEY BESS (DGR) | 22INR0603 | OLNEYTN_BESS | YOUNG | STORAGE | WEST | 2023 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1118 | PYRON BESS 2A | 20INR0268 | PYR_ESS2A | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
1119 | PYRON BESS 2B | 20INR0268 | PYR_ESS2B | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
1120 | QUEEN BESS | 20INR0281 | QUEEN_BA_BESS1 | UPTON | STORAGE | WEST | 2023 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1121 | RIVER VALLEY STORAGE U1 | 20INR0290 | RVRVLYS_ESS1 | WILLIAMSON | STORAGE | SOUTH | 2023 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1122 | RIVER VALLEY STORAGE U2 | 20INR0293 | RVRVLYS_ESS2 | WILLIAMSON | STORAGE | SOUTH | 2023 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1123 | ROSELAND STORAGE | 22INR0280 | ROSELAND_BESS1 | FALLS | STORAGE | NORTH | 2023 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1124 | SP TX-12B BESS | 21INR0357 | SPTX12B_BES1 | UPTON | STORAGE | WEST | 2023 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7
1125 | TURQUOISE STORAGE | 22INR0509 | TURQBESS_BESS1 | HUNT | STORAGE | NORTH | 2023 | 196.2 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
1126 | VORTEX BESS | 21INR0473 | VORTEX_BESS1 | THROCKMORTON | STORAGE | WEST | 2023 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8
1127 | WOLF TANK STORAGE | 22INR0551 | WFTANK_ESS1 | WEBB | STORAGE | SOUTH | 2023 | 150.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
1128 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Storage) | [6 empty] | 921.1 | 906 | 906 | 906 | 906 | 906 | 906 | 906 | 906 | 906 | 906
1129 | Storage Peak Average Capacity Percentage |  | STORAGE_SYNC_PEAK_PCT | % |  |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1130
1131 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1132
1133 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1134
1135 | Non-Synchronous Tie Resources
1136 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
1137 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
1138 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1139 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1140 | Non-Synchronous Ties Total | [6 empty] | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220
1141 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 100 | 69.67 | 69.67 | 69.67 | 69.67 | 69.67 | 69.67 | 69.67 | 69.67 | 69.67 | 69.67
1142
1143 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
1144 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2023 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1145 | BEACHWOOD II POWER STATION (U7-U8) | 23INR0506 |  | BRAZORIA | GAS-GT | COASTAL | 2024 | 121 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
1146 | BROTMAN POWER STATION (U1 - U2) | 23INR0613 |  | BRAZORIA | GAS-GT | COASTAL | 2024 | 121 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
1147 | BROTMAN II POWER STATION (U7- U8) | 23INR0551 |  | BRAZORIA | GAS-GT | COASTAL | 2023 | 121 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
1148 | FRONTERA ENERGY CENTER | 23INR0472 |  | HIDALGO | GAS-CC | SOUTH | 2023 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5
1149 | MIRAGE CTG 1 | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2023 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
1150 | REMY JADE POWER STATION | 23INR0339 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408
1151 | REMY JADE II POWER STATION | 24INR0382 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 103.7 | 0 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7
1152 | SKY SEALY | 21INR0500 |  | AUSTIN | GAS-IC | SOUTH | 2025 | 149.4 | 0 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129
1153 | TECO GTG2 | 23INR0408 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1154 | Planned Thermal Resources Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 1683.6 | 1335.1 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8 | 1567.8
1155
1156 | Planned Wind Resources with Executed SGIA
1157 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2024 | 400 | 0 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
1158 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2023 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1
1159 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2024 | 165.7 | 0 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7
1160 | CRAWFISH | 19INR0177 |  | WHARTON | WIND-O | SOUTH | 2023 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2
1161 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2023 | 531 | 531 | 531 | 531 | 531 | 531 | 531 | 531 | 531 | 531 | 531
1162 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2024 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
1163 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2024 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1164 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2025 | 351 | 0 | 351 | 351 | 351 | 351 | 351 | 351 | 351 | 351 | 351
1165 | MONTE ALTO 2 WIND | 19INR0023 |  | WILLACY | WIND-C | COASTAL | 2024 | 272.8 | 0 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8
1166 | MONTE ALTO I WIND | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2024 | 189 | 0 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189
1167 | MONTGOMERY RANCH WIND | 20INR0040 |  | FOARD | WIND-O | WEST | 2023 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2
1168 | PIONEER DJ WIND | 23INR0387 |  | MIDLAND | WIND-O | WEST | 2024 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3
1169 | RAY GULF WIND | 22INR0517 |  | WHARTON | WIND-O | SOUTH | 2023 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207
1170 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2023 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128
1171 | SHAMROCK | 22INR0502 |  | CROCKETT | WIND-O | WEST | 2024 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9
1172 | SHEEP CREEK WIND | 21INR0325 |  | CALLAHAN | WIND-O | WEST | 2023 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
1173 | SIETE | 20INR0047 |  | WEBB | WIND-O | SOUTH | 2024 | 375.1 | 0 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1
1174 | Planned Capacity Total (Wind) | [6 empty] | 4106.3 | 2352.7 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3
1175
1176 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 461.8 | 0 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8
1177 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 100 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1178
1179 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 696.7 | 531 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7
1180 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 100 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
1181
1182 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 2947.8 | 1821.7 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8
1183 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 100 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
1184
1185 | Planned Solar Resources with Executed SGIA
1186 | 7V SOLAR | 21INR0351 |  | FAYETTE | SOLAR | SOUTH | 2024 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6
1187 | ADAMSTOWN SOLAR | 21INR0210 |  | WICHITA | SOLAR | WEST | 2025 | 254.1 | 0 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1
1188 | ALILA SOLAR | 23INR0093 |  | SAN PATRICIO | SOLAR | COASTAL | 2024 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5
1189 | AMSTERDAM SOLAR | 21INR0256 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9
1190 | ANDROMEDA SOLAR | 22INR0412 |  | SCURRY | SOLAR | WEST | 2023 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
1191 | ANGELO SOLAR | 19INR0203 |  | TOM GREEN | SOLAR | WEST | 2024 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4
1192 | ANGUS SOLAR | 20INR0035 |  | BOSQUE | SOLAR | NORTH | 2024 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
1193 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2024 | 204 | 0 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
1194 | ARROYO SOLAR | 20INR0086 |  | CAMERON | SOLAR | COASTAL | 2024 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
1195 | ASH CREEK SOLAR | 21INR0379 |  | HILL | SOLAR | NORTH | 2024 | 408.9 | 0 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9
1196 | BAKER BRANCH SOLAR | 23INR0026 |  | LAMAR | SOLAR | NORTH | 2024 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4
1197 | BIG ELM SOLAR | 21INR0353 |  | BELL | SOLAR | NORTH | 2024 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2
1198 | BLUE SKY SOL | 22INR0455 |  | CROCKETT | SOLAR | WEST | 2024 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
1199 | BRASS FORK SOLAR | 22INR0270 |  | HASKELL | SOLAR | WEST | 2025 | 304.8 | 0 | 0 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8
1200 | BRIGHT ARROW SOLAR | 22INR0242 |  | HOPKINS | SOLAR | NORTH | 2023 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1201 | BUCKEYE CORPUS FUELS SOLAR | 22INR0397 |  | NUECES | SOLAR | COASTAL | 2025 | 57.6 | 0 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6
1202 | CACHENA SOLAR | 23INR0027 |  | WILSON | SOLAR | SOUTH | 2025 | 600 | 0 | 0 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
1203 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2025 | 223.2 | 0 | 0 | 223.2 | 223.2 | 223.2 | 223.2 | 223.2 | 223.2 | 223.2 | 223.2
1204 | CASTRO SOLAR | 20INR0050 |  | CASTRO | SOLAR | PANHANDLE | 2025 | 222.9 | 0 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9
1205 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2025 | 406.8 | 0 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8
1206 | CLUTCH CITY SOLAR | 22INR0279 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 204.2 | 0 | 0 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2
1207 | COMPADRE SOLAR | 24INR0023 |  | HILL | SOLAR | NORTH | 2024 | 405.3 | 0 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3
1208 | CORAL SOLAR | 22INR0295 |  | FALLS | SOLAR | NORTH | 2023 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6
1209 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2025 | 202.6 | 0 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
1210 | COTTONWOOD BAYOU SOLAR I | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4
1211 | CRADLE SOLAR | 23INR0150 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 225 | 0 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
1212 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2025 | 217.6 | 0 | 0 | 217.6 | 217.6 | 217.6 | 217.6 | 217.6 | 217.6 | 217.6 | 217.6
1213 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2025 | 188.8 | 0 | 0 | 188.8 | 188.8 | 188.8 | 188.8 | 188.8 | 188.8 | 188.8 | 188.8
1214 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2023 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8
1215 | DAWN SOLAR | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2024 | 515.7 | 0 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7
1216 | DELILAH SOLAR 1 | 22INR0202 |  | LAMAR | SOLAR | NORTH | 2024 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1217 | DELILAH SOLAR 2 | 22INR0203 |  | LAMAR | SOLAR | NORTH | 2024 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6
1218 | DELILAH SOLAR 3 | 23INR0042 |  | LAMAR | SOLAR | NORTH | 2023 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1219 | DELILAH SOLAR 4 | 23INR0060 |  | LAMAR | SOLAR | NORTH | 2023 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
1220 | DESERT VINE SOLAR | 22INR0307 |  | ZAPATA | SOLAR | SOUTH | 2024 | 121.3 | 0 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3
1221 | DILEO SOLAR | 22INR0359 |  | BOSQUE | SOLAR | NORTH | 2023 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
1222 | DONEGAL SOLAR | 23INR0089 |  | DICKENS | SOLAR | PANHANDLE | 2024 | 204.2 | 0 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2
1223 | DORI BQ SOLAR | 23INR0040 |  | HARRIS | SOLAR | HOUSTON | 2024 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
1224 | DR SOLAR | 22INR0454 |  | CULBERSON | SOLAR | WEST | 2024 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
1225 | EASTBELL MILAM SOLAR | 21INR0203 |  | MILAM | SOLAR | SOUTH | 2023 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9
1226 | EIFFEL SOLAR | 22INR0223 |  | LAMAR | SOLAR | NORTH | 2023 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241
1227 | ELIZA SOLAR | 21INR0368 |  | KAUFMAN | SOLAR | NORTH | 2024 | 151.9 | 0 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9
1228 | ELLIS SOLAR | 21INR0493 |  | ELLIS | SOLAR | NORTH | 2023 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
1229 | EQUINOX SOLAR 1 | 21INR0226 |  | STARR | SOLAR | SOUTH | 2026 | 200 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1230 | ESTONIAN SOLAR FARM | 22INR0335 |  | DELTA | SOLAR | NORTH | 2024 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5
1231 | FAGUS SOLAR PARK (MISAE SOLAR II) | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2024 | 519.5 | 0 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5
1232 | FENCE POST SOLAR | 22INR0404 |  | NAVARRO | SOLAR | NORTH | 2024 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236
1233 | FIVE WELLS SOLAR | 24INR0015 |  | BELL | SOLAR | NORTH | 2023 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8
1234 | FRYE SOLAR | 20INR0080 |  | SWISHER | SOLAR | PANHANDLE | 2024 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1
1235 | GALACTIC SOLAR | 23INR0144 |  | GRAYSON | SOLAR | NORTH | 2024 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2
1236 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2023 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9
1237 | GARCITAS CREEK SOLAR | 23INR0223 |  | JACKSON | SOLAR | SOUTH | 2024 | 201.9 | 0 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9
1238 | GP SOLAR | 23INR0045 |  | VAN ZANDT | SOLAR | NORTH | 2024 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
1239 | GRANDSLAM SOLAR | 21INR0391 |  | ATASCOSA | SOLAR | SOUTH | 2024 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
1240 | GRANSOLAR TEXAS ONE | 22INR0511 |  | MILAM | SOLAR | SOUTH | 2024 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1241 | GREATER BRYANT G SOLAR | 23INR0300 |  | MIDLAND | SOLAR | WEST | 2024 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6
1242 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2024 | 413.6 | 0 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6
1243 | GREYHOUND SOLAR | 21INR0268 |  | ECTOR | SOLAR | WEST | 2025 | 608.7 | 0 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7
1244 | GRIMES COUNTY SOLAR | 23INR0160 |  | GRIMES | SOLAR | NORTH | 2025 | 210 | 0 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
1245 | GULF STAR SOLAR SLF (G-STAR SOLAR) | 23INR0111 |  | WHARTON | SOLAR | SOUTH | 2024 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6
1246 | HALO SOLAR | 21INR0304 |  | BELL | SOLAR | NORTH | 2023 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254
1247 | HAYHURST TEXAS SOLAR | 22INR0363 |  | CULBERSON | SOLAR | WEST | 2023 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8
1248 | HOPKINS SOLAR | 20INR0210 |  | HOPKINS | SOLAR | NORTH | 2023 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1
1249 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2023 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5
1250 | HORNET SOLAR | 23INR0021 |  | SWISHER | SOLAR | PANHANDLE | 2024 | 611 | 0 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611
1251 | HOWLE SOLAR | 20INR0075 |  | ELLIS | SOLAR | NORTH | 2024 | 60 | 0 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1252 | HOYTE SOLAR | 23INR0235 |  | MILAM | SOLAR | SOUTH | 2024 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
1253 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2024 | 125 | 0 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1254 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2025 | 202.4 | 0 | 0 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4
1255 | JACKALOPE SOLAR | 23INR0180 |  | SAN PATRICIO | SOLAR | COASTAL | 2024 | 156.4 | 0 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4
1256 | JUNGMANN SOLAR | 22INR0356 |  | MILAM | SOLAR | SOUTH | 2024 | 40 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
1257 | LAVACA BAY SOLAR | 23INR0084 |  | MATAGORDA | SOLAR | COASTAL | 2024 | 243.5 | 0 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5
1258 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 101.3 | 0 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3
1259 | LUNIS CREEK SOLAR 1 | 21INR0344 |  | JACKSON | SOLAR | SOUTH | 2024 | 617.1 | 0 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1
1260 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2024 | 254.9 | 0 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9
1261 | MARKUM SOLAR | 20INR0230 |  | MCLENNAN | SOLAR | NORTH | 2024 | 161.5 | 0 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5
1262 | MATAGORDA SOLAR | 22INR0342 |  | MATAGORDA | SOLAR | COASTAL | 2023 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101
1263 | MERCURY I SOLAR | 21INR0257 |  | HILL | SOLAR | NORTH | 2024 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5
1264 | MERCURY II SOLAR | 23INR0153 |  | HILL | SOLAR | NORTH | 2024 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2
1265 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2024 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
1266 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2025 | 365.7 | 0 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7
1267 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2025 | 204 | 0 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
1268 | NEPTUNE SOLAR | 21INR0499 |  | JACKSON | SOLAR | SOUTH | 2023 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3
1269 | NORIA SOLAR DCC | 23INR0061 |  | NUECES | SOLAR | COASTAL | 2024 | 145 | 0 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
1270 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2024 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1271 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2025 | 225.7 | 0 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7
1272 | ORIANA SOLAR | 24INR0093 |  | VICTORIA | SOLAR | SOUTH | 2024 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3
1273 | OUTPOST SOLAR | 23INR0007 |  | WEBB | SOLAR | SOUTH | 2024 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7
1274 | OYSTERCATCHER SOLAR | 21INR0362 |  | ELLIS | SOLAR | NORTH | 2024 | 220.3 | 0 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
1275 | PEREGRINE SOLAR | 22INR0283 |  | GOLIAD | SOLAR | SOUTH | 2024 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4
1276 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2024 | 305 | 0 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305
1277 | PINK SOLAR | 22INR0281 |  | HUNT | SOLAR | NORTH | 2023 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
1278 | PITTS DUDIK SOLAR | 20INR0074 |  | HILL | SOLAR | NORTH | 2023 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6
1279 | PORTER SOLAR | 21INR0458 |  | DENTON | SOLAR | NORTH | 2024 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245
1280 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2024 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260
1281 | REDONDA SOLAR | 23INR0162 |  | ZAPATA | SOLAR | SOUTH | 2024 | 253.2 | 0 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2
1282 | RED-TAILED HAWK SOLAR | 21INR0389 |  | WHARTON | SOLAR | SOUTH | 2024 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
1283 | ROCINANTE SOLAR | 23INR0231 |  | GONZALES | SOLAR | SOUTH | 2024 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
1284 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2025 | 200 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1285 | ROWLAND SOLAR II | 22INR0482 |  | FORT BEND | SOLAR | HOUSTON | 2024 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8
1286 | SAMSON SOLAR 2 | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2024 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
1287 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2024 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5
1288 | SCHOOLHOUSE SOLAR | 22INR0211 |  | LEE | SOLAR | SOUTH | 2025 | 150.8 | 0 | 0 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8
1289 | SECOND DIVISION SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
1290 | SHAULA I SOLAR | 22INR0251 |  | DEWITT | SOLAR | SOUTH | 2025 | 205.2 | 0 | 0 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2
1291 | SHAULA II SOLAR | 22INR0267 |  | DEWITT | SOLAR | SOUTH | 2026 | 205.2 | 0 | 0 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2
1292 | SIGNAL SOLAR | 20INR0208 |  | HUNT | SOLAR | NORTH | 2024 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8
1293 | SODA LAKE SOLAR 1 SLF | 20INR0143 |  | CRANE | SOLAR | WEST | 2024 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
1294 | SODA LAKE SOLAR 2 SLF | 23INR0080 |  | CRANE | SOLAR | WEST | 2023 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
1295 | SP JAGUAR SOLAR | 24INR0038 |  | MCLENNAN | SOLAR | NORTH | 2024 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1296 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2025 | 609.7 | 0 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7
1297 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2023 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
1298 | STAMPEDE SOLAR | 22INR0409 |  | HOPKINS | SOLAR | NORTH | 2023 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
1299 | STARLING SOLAR | 23INR0035 |  | GONZALES | SOLAR | SOUTH | 2024 | 123 | 0 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
1300 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2024 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7
1301 | SUNRAY | 21INR0395 |  | UVALDE | SOLAR | SOUTH | 2024 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1
1302 | TALITHA SOLAR | 21INR0393 |  | JIM WELLS | SOLAR | SOUTH | 2024 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131
1303 | TANGLEWOOD SOLAR | 23INR0054 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 257 | 0 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
1304 | TEXANA SOLAR | 18INR0058 |  | WHARTON | SOLAR | SOUTH | 2024 | 152.3 | 0 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
1305 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2023 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5
1306 | TEXAS SOLAR NOVA 2 | 20INR0269 |  | KENT | SOLAR | WEST | 2023 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1
1307 | TIERRA BONITA SOLAR | 21INR0424 |  | PECOS | SOLAR | WEST | 2024 | 309.7 | 0 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7
1308 | TRES BAHIAS SOLAR | 20INR0266 |  | CALHOUN | SOLAR | COASTAL | 2023 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4
1309 | TROJAN SOLAR | 23INR0296 |  | COOKE | SOLAR | NORTH | 2024 | 206.1 | 0 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1
1310 | TULSITA SOLAR | 21INR0223 |  | GOLIAD | SOLAR | SOUTH | 2024 | 261 | 0 | 261 | 261 | 261 | 261 | 261 | 261 | 261 | 261 | 261
1311 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2024 | 90 | 0 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
1312 | ULYSSES SOLAR | 21INR0253 |  | COKE | SOLAR | WEST | 2024 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
1313 | UMBRA (STOCKYARD) SOLAR | 23INR0155 |  | FRANKLIN | SOLAR | NORTH | 2024 | 210 | 0 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
1314 | XE MURAT SOLAR | 22INR0354 |  | HARRIS | SOLAR | HOUSTON | 2024 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4
1315 | ZIER SOLAR | 21INR0019 |  | KINNEY | SOLAR | SOUTH | 2023 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
1316 | Planned Capacity Total (Solar) | [6 empty] | 30232.7 | 15393.1 | 27530.5 | 30032.7 | 30232.7 | 30232.7 | 30232.7 | 30232.7 | 30232.7 | 30232.7 | 30232.7
1317 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 100 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
1318
1319 | Planned Storage Resources with Executed SGIA
1320 | ADAMSTOWN STORAGE | 21INR0209 |  | WICHITA | STORAGE | WEST | 2025 | 116.9 | 0 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9
1321 | AEP_N_ALAMO_LD02(SMT ALAMO) | 23INR0477 |  | HIDALGO | STORAGE | SOUTH | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1322 | AL PASTOR BESS | 24INR0273 |  | DAWSON | STORAGE | WEST | 2024 | 100.8 | 0 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
1323 | AMSTERDAM STORAGE | 22INR0417 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1
1324 | ANEMOI ENERGY STORAGE | 23INR0369 |  | HIDALGO | STORAGE | SOUTH | 2023 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205
1325 | ARROYO STORAGE SLF | 24INR0306 |  | CAMERON | STORAGE | COASTAL | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1326 | BIG STAR STORAGE | 21INR0469 |  | BASTROP | STORAGE | SOUTH | 2023 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
1327 | BOCO BESS | 23INR0470 |  | BORDEN | STORAGE | WEST | 2024 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3
1328 | BORDERTOWN BESS | 23INR0354 |  | STARR | STORAGE | SOUTH | 2025 | 106.2 | 0 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2
1329 | BRAZOS BEND BESS | 23INR0363 |  | FORT BEND | STORAGE | HOUSTON | 2024 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
1330 | BRIGHT ARROW STORAGE | 22INR0302 |  | HOPKINS | STORAGE | NORTH | 2023 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6
1331 | BRP ANTLIA BESS | 22INR0349 |  | VAL VERDE | STORAGE | WEST | 2023 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9
1332 | BRP AVILA BESS | 23INR0287 |  | PECOS | STORAGE | WEST | 2024 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9
1333 | BRP CACHI BESS | 22INR0388 |  | GUADALUPE | STORAGE | SOUTH | 2024 | 202.5 | 0 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5
1334 | BRP CARINA BESS | 22INR0353 |  | NUECES | STORAGE | COASTAL | 2024 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9
1335 | BRP DICKENS BESS | 22INR0325 |  | DICKENS | STORAGE | PANHANDLE | 2023 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3
1336 | BRP HYDRA BESS | 22INR0372 |  | PECOS | STORAGE | WEST | 2023 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3
1337 | BRP LIBRA BESS | 22INR0366 |  | GUADALUPE | STORAGE | SOUTH | 2023 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2
1338 | BRP PALEO BESS | 22INR0322 |  | HALE | STORAGE | PANHANDLE | 2023 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4
1339 | BRP PAVO BESS | 22INR0384 |  | PECOS | STORAGE | WEST | 2023 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9
1340 | BRP TORTOLAS BESS | 23INR0072 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7
1341 | BRP ZEYA BESS | 23INR0290 |  | GALVESTON | STORAGE | HOUSTON | 2024 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8
1342 | CALLISTO I ENERGY CENTER | 22INR0490 |  | HARRIS | STORAGE | HOUSTON | 2024 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
1343 | CITADEL BESS | 24INR0147 |  | HARRIS | STORAGE | HOUSTON | 2024 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3
1344 | CONNOLLY STORAGE | 23INR0403 |  | WISE | STORAGE | NORTH | 2024 | 131.1 | 0 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
1345 | CORAL STORAGE | 23INR0124 |  | FALLS | STORAGE | NORTH | 2023 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
1346 | COTTONWOOD BAYOU STORAGE | 21INR0443 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 150.8 | 0 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8
1347 | DAMON STORAGE | 23INR0523 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
1348 | DANISH FIELDS STORAGE | 21INR0450 |  | WHARTON | STORAGE | SOUTH | 2023 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4
1349 | DIBOLL BESS (DGR) | 23INR0522 |  | ANGELINA | STORAGE | NORTH | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1350 | EBONY ENERGY STORAGE | 23INR0154 |  | COMAL | STORAGE | SOUTH | 2024 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205
1351 | ELIZA STORAGE | 22INR0260 |  | KAUFMAN | STORAGE | NORTH | 2024 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
1352 | ESTONIAN ENERGY STORAGE | 22INR0336 |  | DELTA | STORAGE | NORTH | 2024 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
1353 | EVAL STORAGE | 22INR0401 |  | CAMERON | STORAGE | COASTAL | 2024 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
1354 | FENCE POST BESS | 22INR0405 |  | NAVARRO | STORAGE | NORTH | 2023 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
1355 | FERDINAND GRID BESS | 22INR0422 |  | BEXAR | STORAGE | SOUTH | 2025 | 202.6 | 0 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
1356 | FIVE WELLS STORAGE | 23INR0159 |  | BELL | STORAGE | NORTH | 2023 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8
1357 | FORT DUNCAN BESS | 23INR0350 |  | MAVERICK | STORAGE | SOUTH | 2025 | 106.2 | 0 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2
1358 | GIGA TEXAS ENERGY STORAGE | 23INR0239 |  | TRAVIS | STORAGE | SOUTH | 2023 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
1359 | GREAT KISKADEE STORAGE | 23INR0166 |  | HIDALGO | STORAGE | SOUTH | 2024 | 103.1 | 0 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1
1360 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2024 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1361 | GRIZZLY RIDGE BESS (DGR) | 22INR0596 |  | HAMILTON | STORAGE | NORTH | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1362 | GUAJILLO ENERGY STORAGE | 23INR0343 |  | WEBB | STORAGE | SOUTH | 2024 | 201.1 | 0 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1
1363 | HOUSE MOUNTAIN 2 BATT | 22INR0485 |  | BREWSTER | STORAGE | WEST | 2023 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1364 | HUMMINGBIRD STORAGE | 22INR0327 |  | DENTON | STORAGE | NORTH | 2023 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
1365 | INERTIA BESS | 22INR0328 |  | HASKELL | STORAGE | WEST | 2023 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
1366 | INERTIA BESS 2 | 22INR0375 |  | HASKELL | STORAGE | WEST | 2025 | 100.8 | 0 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
1367 | IRON BELT ENERGY STORAGE | 25INR0208 |  | DAWSON | STORAGE | WEST | 2025 | 401.9 | 0 | 0 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9
1368 | JUNCTION BESS (DGR) | 23INR0521 |  | KIMBLE | STORAGE | SOUTH | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1369 | LARKSPUR ENERGY STORAGE | 23INR0340 |  | UPTON | STORAGE | WEST | 2025 | 307.5 | 0 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5
1370 | LIMOUSIN OAK STORAGE | 22INR0338 |  | GRIMES | STORAGE | NORTH | 2023 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6
1371 | MUSTANG CREEK STORAGE | 21INR0484 |  | JACKSON | STORAGE | SOUTH | 2023 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5
1372 | MYRTLE STORAGE | 21INR0442 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
1373 | NORIA STORAGE | 23INR0062 |  | NUECES | STORAGE | COASTAL | 2024 | 75 | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
1374 | ORIANA BESS | 24INR0109 |  | VICTORIA | STORAGE | SOUTH | 2024 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4
1375 | PADUA GRID BESS | 22INR0368 |  | BEXAR | STORAGE | SOUTH | 2024 | 202.6 | 0 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
1376 | PLATINUM STORAGE | 22INR0554 |  | FANNIN | STORAGE | NORTH | 2024 | 303.5 | 0 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5
1377 | RAMSEY STORAGE | 21INR0505 |  | WHARTON | STORAGE | SOUTH | 2024 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4
1378 | RED HOLLY STORAGE | 21INR0033 |  | DAWSON | STORAGE | WEST | 2024 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1379 | ROCINANTE BESS | 23INR0232 |  | GONZALES | STORAGE | SOUTH | 2024 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
1380 | RODEO RANCH ENERGY STORAGE | 23INR0371 |  | REEVES | STORAGE | WEST | 2023 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5
1381 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2024 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1382 | SABAL STORAGE | 22INR0398 |  | CAMERON | STORAGE | COASTAL | 2023 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4
1383 | SMT ALAMO (DGR) | 23INR0477 |  | HIDALGO | STORAGE | SOUTH | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1384 | SMT LOS FRESNOS (DGR) | 23INR0508 |  | CAMERON | STORAGE | COASTAL | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1385 | SMT MISSION (DGR) | 23INR0511 |  | CAMERON | STORAGE | COASTAL | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1386 | SMT RIO GRANDE (DGR) | 23INR0509 |  | STARR | STORAGE | SOUTH | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1387 | SMT RIO GRANDE II (DGR) | 23INR0510 |  | STARR | STORAGE | SOUTH | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1388 | SOHO BESS | 23INR0419 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3
1389 | SOWERS STORAGE | 22INR0552 |  | KAUFMAN | STORAGE | NORTH | 2024 | 203 | 0 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
1390 | SP JAGUAR BESS | 24INR0039 |  | MCLENNAN | STORAGE | NORTH | 2024 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1391 | ST. GALL I ENERGY STORAGE | 22INR0524 |  | PECOS | STORAGE | WEST | 2023 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
1392 | STAMPEDE BESS | 22INR0410 |  | HOPKINS | STORAGE | NORTH | 2023 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
1393 | STOCKYARD GRID BATT | 21INR0492 |  | TARRANT | STORAGE | NORTH | 2023 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
1394 | SUN VALLEY BESS | 22INR0429 |  | HILL | STORAGE | NORTH | 2023 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4
1395 | TALITHA BESS | 23INR0331 |  | JIM WELLS | STORAGE | SOUTH | 2024 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4
1396 | TANZANITE STORAGE | 22INR0549 |  | HENDERSON | STORAGE | NORTH | 2024 | 257.7 | 0 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7
1397 | TIDWELL PRAIRIE STORAGE 1 | 21INR0517 |  | ROBERTSON | STORAGE | NORTH | 2024 | 304.8 | 0 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8
1398 | TIMBERWOLF BESS 2 | 22INR0495 |  | CRANE | STORAGE | WEST | 2023 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
1399 | UMBRA (STOCKYARD) BESS | 23INR0156 |  | FRANKLIN | STORAGE | NORTH | 2024 | 73 | 0 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
1400 | ZIER STORAGE | 21INR0027 |  | KINNEY | STORAGE | SOUTH | 2023 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4
1401 | SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * | [6 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
1402 | Planned Capacity Total (Storage) | [6 empty] | 10788.2 | 7054.1 | 10386.3 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2
1403 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1404
1405 | Inactive Planned Resources
1406 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1407 | CHILLINGHAM SOLAR | 23INR0070 |  | BELL | SOLAR | NORTH | 2023 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4
1408 | CHILLINGHAM STORAGE | 23INR0079 |  | BELL | STORAGE | NORTH | 2023 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8
1409 | DONEGAL BESS | 23INR0103 |  | DICKENS | STORAGE | PANHANDLE | 2024 | 101.3 | 0 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3
1410 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2026 | 165 | 0 | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
1411 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1
1412 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1
1413 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
1414 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
1415 | PARLIAMENT SOLAR | 23INR0044 |  | WALLER | SOLAR | HOUSTON | 2024 | 482.7 | 0 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7
1416 | PLEASANTON BESS (DGR) | 23INR0520 |  | ATASCOSA | STORAGE | SOUTH | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1417 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2025 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1418 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2024 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
1419 | Inactive Planned Capacity Total | [6 empty] | 2364.8 | 1385.8 | 1999.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8
1420
1421 | Seasonal Mothballed Resources
1422 | MOUNTAIN CREEK STG 8 (AS OF 3/1/2023, AVAILABLE 6/1 THROUGH 9/30) |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568
1423 | POWERLANE PLANT STG 1 (AS OF 10/1/2022, AVAILABLE 6/1 THROUGH 9/30) |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 18.75 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
1424 | SPENCER STG U4 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 61 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
1425 | SPENCER STG U5 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 65 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
1426 | Total Seasonal Mothballed Capacity | [6 empty] | 712.75 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5
1427
1428 | Mothballed Resources
1429 | RAY OLINGER STG 1 (AS OF 4/5/22) |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
1430 | CALENERGY-FALCON SEABOARD STG 3 (AS OF 7/8/22, DUE TO FORCED OUTAGE) |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62
1431 | Total Mothballed Capacity | [6 empty] | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
1432
1433 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
1434 | J T DEELY U1 (INDEFINITE MOTHBALL AS OF 12/31/2018, RETIRING ON 7/7/23) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 415 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
1435 | J T DEELY U2 (INDEFINITE MOTHBALL AS OF 12/31/2018, RETIRING ON 7/7/23) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 415 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
1436 | Total Retiring Capacity | [6 empty] | 830 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide Ancillary Services rather than sustained capacity available to meet system peak loads.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Reources Services (RIOO-RS) system.
Note on J443: Extended outages: GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE (3.6 MW) and 2.4 MW of the 4.8 MW GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP Hydro unit.

## Peak v High Net Load Hour 2024
Summer 2024
Load Forecast, MW [1] |  | Peak Load Hour (Hour-ending 5:00 PM) | High Net Load Hour (Hour-ending 8:00 PM) | MW Difference, 5:00 to 8:00 PM
| Summer Peak Demand (based on normal weather) | 85029.0907 | 79104.3916 | -5924.6991
| plus: Energy Efficiency Program Savings Forecast | 3310.5748 | 3310.5748 | 0
| Total Summer Peak Demand (before Reductions from Energy Efficiency Programs) | 88339.6656 | 82414.9664 | -5924.6991
| less: Incremental Rooftop PV Forecast | -703.6488 | -208.28 | 495.3687
| less: Load Resources providing Responsive Reserves | -1409.64 | -1409.64 | 0
| less: Load Resources providing Non-Spinning Reserves | -47.9502 | -47.9502 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -893.9994 | -993.7171 | -99.7177
| less: TDSP Standard Offer Load Management Programs | -330.48 | -330 | 0.48
| less: Energy Efficiency Program Savings Forecast | -3310.5748 | -3310.5748 | 0
| Firm Peak Demand, MW | 81643.3723 | 76114.8043 | -5528.5681
Resources, MW [2] |  | Peak Load Hour (Hour-ending 5:00 PM) | High Net Load Hour (Hour-ending 8:00 PM) | MW Change, 5:00 to 8:00 PM
| Installed Summer-rated Capacity, Thermal | 65091.3 | 65091.3 | 0
| Hydroelectric, Peak Average Capacity Contribution (84% of installed capacity) | 475.4044 | 475.4044 | 0
| Switchable Capacity | 3490 | 3490 | 0
| less: Switchable Capacity Unavailable to ERCOT | -692 | -692 | 0
| Available Mothballed Capacity | 703.5 | 703.5 | 0
| Capacity from Private Use Networks | 2868.925 | 2868.925 | 0
| Coastal Wind, Peak Average Capacity Contribution | 3258.12 | 4196.4586 | 938.3386
| Panhandle Wind, Peak Average Capacity Contribution | 1322.31 | 1703.1353 | 380.8253
| Other Wind, Peak Average Capacity Contribution | 5846.652 | 7530.4878 | 1683.8358
| Solar Utility-Scale, Peak Average Capacity Contribution | 12263.802 | 3630.0854 | -8633.7166
| Storage, Peak Average Capacity Contribution | 0 | 0 | 0
| RMR Capacity to be under Contract | 0 | 0 | 0
| Capacity Pending Retirement | 0 | 0 | 0
| Operational Generation Capacity, MW | 94628.0134 | 88997.2964 | -5630.717
| Non-Synchronous Ties (Based on average net import contribution during summer 2019 EEA events) | 849.974 | 849.974 | 0
| Planned Resources (not wind, solar or storage) with Signed IA, Air Permits and Adequate Water Supplies | 1335.1 | 1335.1 | 0
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | 0
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution | 159.3 | 205.1784 | 45.8784
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution | 382.557 | 492.7334 | 110.1764
| Planned Solar Utility-Scale, Peak Average Capacity Contribution | 12160.549 | 3599.5225 | -8561.0265
| Planned Storage, Peak Average Capacity Contribution | 0 | 0 | 0
| Planned Generation Capacity, MW | 14037.506 | 5632.5343 | -8404.9717
| Total Capacity, MW | 109515.4934 | 95479.8047 | -14035.6887
Percentage Point Difference
| Reserve Margin | 34.14% | 25.44% | -8.697
(Total Resources - Firm Load Forecast) / Firm Load Forecast
| Reserve Margin including a battery storage capacity contribution (2,099 MW) [3] | 36.71% | 28.2% | -8.5103
NOTES:
[1] Derivation of the Hourly Load Forecasts
The load forecasts for hours-ending 5:00 and 8:00 PM come from ERCOT's official Long Term Load Forecast, and assume that the summer peak load day occurs on August 4th.
[2] Derivation of Net Peak Load Wind and Solar Capacities
Hour-ending 8:00 PM wind and solar capacities are the original CDR values multiplied by a ratio of 50th-percentile values taken from synthetic profiles values representing the range of potential values for the 5:00 and 8:00 PM summer hours. Specifically, the wind and solar ratios are the 50th percentile (P50) values for 8:00 PM divided by the P50 values for 5:00 PM. The wind and solar ratios are 1.288 and 0.296, respectively. These ratios reflect the ramp-up of wind and ramp-down of solar in the evening hours.
[3] Reserve Margin with a Battery Storage Capacity Contribution
The 2,099 MW contribution is based on the amount of battery storage capability assumed to be available for dispatch prior to the highest summer net load hours for August 2024. The capacity contribution percentage is 0.203, and is multiplied by the forecasted installed capacity of operational plus planned units in the CDR for July 2024 (10,340 MW). The capacity contribution percentage is based on analysis of battery State-of-Charge available for energy, and accounting for Ancillary Service obligations, during hours-ending 4:00 PM through 7:00 PM for August 2022. Further analysis is needed to resolve contribution differences on an hourly basis. This methodology is used for the Summer 2023 Seasonal Assessment of Resource Adequacy (SARA), and is an interim methodology for use until a formal capacity contribution method is adopted for future resource adequacy reports.
Note on D10: An adjustment was applied to reflect a higher ERS amount available for HE 8:00.

## Planned Resource Scenarios
Planned Resources Scenarios, Summer
The tables below show condensed versions of the Summer Summary tab for 2024-2028 under different sets of planned project inclusion criteria. Table 1 shows the line items under the current CDR-eligibility criteria (signed IA and air permits/proof of adequate water supplies for fossil-fuel projects). Tables 2, 3, and 4 show the line items under more selective sets of criteria for including planned projects: Table 2 - Meets All Planning Guide Section 6.9(1) Requirements, Table 3 - Meets All Planning Guide Section 6.9 Requirements, Table 4 - meets Quarterly Stability Assessment prerequisites. Table 5 compares the Planning Reserve Margins across the four sets of CDR planned project inclusion criteria. An abbreviated summary of the Planning Guide criteria are listed below the data tables. See Planning Guide Sections 5.9 and 6.9 for the full text. Planned Projects data comes from generation capacity developers and owners as reported in ERCOT's Resource Integration and Ongoing Operations (RIOO) system and other data collection mechanisms described in the ERCOT Protocols.
Table 1: Summer Summary - CDR Eligibility Criteria for Planned Projects
| 2024 | 2025 | 2026 | 2027 | 2028
Firm Peak Load, MW | 81643.3723 | 83058.4163 | 84449.3841 | 85836.1259 | 86407.76
Operational Generation Capacity and Non-Synchronous Ties, MW | 95169.5274 | 95171.3274 | 95171.3274 | 95316.3274 | 95316.3274
Planned Project Capacity, MW
Planned Thermal (not wind, solar or storage) | 1335.1 | 1567.8 | 1567.8 | 1567.8 | 1567.8
Planned Wind | 541.857 | 1105.128 | 1105.128 | 1105.128 | 1105.128
Planned Solar | 12160.549 | 21749.095 | 23725.833 | 23883.833 | 23883.833
Planning Reserve Margin | 33.76% | 43.99% | 43.96% | 41.98% | 41.04%
Table 2: Summer Summary - Planned Projects that Meet All Planning Guide 6.9(1) Requirements
| 2024 | 2025 | 2026 | 2027 | 2028
Firm Peak Load, MW | 81643.3723 | 83058.4163 | 84449.3841 | 85836.1259 | 86407.76
Operational Generation Capacity and Non-Synchronous Ties, MW | 95169.5274 | 95171.3274 | 95171.3274 | 95316.3274 | 95316.3274
Planned Project Capacity, MW
Planned Thermal (not wind, solar or storage) | 1285.1 | 1285.1 | 1285.1 | 1285.1 | 1285.1
Planned Wind | 147.063 | 225.834 | 225.834 | 225.834 | 225.834
Planned Solar | 8324.783 | 12516.207 | 13887.015 | 13887.015 | 13887.015
Planning Reserve Margin | 28.52% | 31.47% | 30.93% | 28.98% | 28.13%
Table 3: Summer Summary - Planned Projects Meeting All Planning Guide 6.9 Requirements
| 2024 | 2025 | 2026 | 2027 | 2028
Firm Peak Load, MW | 81643.3723 | 83058.4163 | 84449.3841 | 85836.1259 | 86407.76
Operational Generation Capacity and Non-Synchronous Ties, MW | 95169.5274 | 95171.3274 | 95171.3274 | 95316.3274 | 95316.3274
Planned Project Capacity, MW
Planned Thermal (not wind, solar or storage) | 1285.1 | 1285.1 | 1285.1 | 1285.1 | 1285.1
Planned Wind | 55.272 | 55.272 | 55.272 | 55.272 | 55.272
Planned Solar | 6095.482 | 6377.038 | 6377.038 | 6377.038 | 6377.038
Planning Reserve Margin | 25.68% | 23.88% | 21.83% | 20.04% | 19.24%
Table 4: Summer Summary - Planned Projects Meeting Quarterly Stability (QSA) Study Prerequisites
| 2024 | 2025 | 2026 | 2027 | 2028
Firm Peak Load, MW | 81643.3723 | 83058.4163 | 84449.3841 | 85836.1259 | 86407.76
Operational Generation Capacity and Non-Synchronous Ties, MW | 95169.5274 | 95171.3274 | 95171.3274 | 95316.3274 | 95316.3274
Planned Project Capacity, MW
Planned Thermal (not wind, solar or storage) | 877.1 | 877.1 | 877.1 | 877.1 | 877.1
Planned Wind | 55.272 | 55.272 | 55.272 | 55.272 | 55.272
Planned Solar | 5914.73 | 5914.73 | 5914.73 | 5914.73 | 5914.73
Planning Reserve Margin | 24.95% | 22.83% | 20.8% | 19.02% | 18.23%
Table 5: Summer Planning Reserve Margin Comparison Based on Different Planned Project Inclusion Criteria
| 2024 | 2025 | 2026 | 2027 | 2028
Planning Reserve Margin—Current CDR-eligible criteria | 33.76% | 43.99% | 43.96% | 41.98% | 41.04%
Planning Reserve Margin—Section 6.9(1) Requirements | 28.52% | 31.47% | 30.93% | 28.98% | 28.13%
Planning Reserve Margin—Section 6.9 Requirements | 25.68% | 23.88% | 21.83% | 20.04% | 19.24%
Planning Reserve Margin—QSA Study Requirements | 24.95% | 22.83% | 20.8% | 19.02% | 18.23%
Planning Guide Section 6.9(1) Requirements
1. The Interconnecting Entity (IE) provides all data required for the Security Screening Study and Full Interconnection Study (FIS).
2. ERCOT determines that the IE has received all necessary Texas Commission on Environmental Quality (TCEQ)-approved air permits or that no such permits are required.
3. The IE submits a completed Declaration of Adequate Water Supplies. (Wind, solar and battery storage projects are exempted.)
4. ERCOT receives a signed Standard Generation Interconnection Agreement (SGIA) or other financially binding agreement from the Transmission Service Provider (TSP) and IE, and a written notice from the TSP that the IE has provided:
(A) A notice to proceed with the construction of the interconnection and; (B) The financial security required to fund the interconnection facilities.
or, a letter from an authorized official from a Municipally Owned Utility (MOU) or Electric Cooperative (EC) confirming the Entity’s intent to construct, interconnect and operate the resource.
Planning Guide Section 6.9 Requirements
1. The requirements for Section 6.9(1).
2. The IE shall provide within 60 days the remaining required data as specified in the Resource Registration Glossary using the applicable Resource Registration process.
Quarterly Stability Assessment Prerequisites from Planning Guide Section 5.9
1. All requirements under Planning Guide Section 6.9 have been met.
2. The IE has provided all dynamic model data to ERCOT.
3. The Full Interconnection Study has been completed.
4. The Reactive Power Study has been completed.
5. Completion of required system improvements or mitigation plans identified in these studies.

## WinterSummary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Winter Summary: 2024/2025 through 2033/2034
These columns indicate the impact of not adding any new resources during the latter half of the CDR forecast period. Project developers typically submit interconnection requests no more than two to four years before the facilities are expected to enter commercial operations.
Load Forecast, MW: |  |  | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032/2033 | 2033/2034
| Winter Peak Demand (based on normal weather) |  | 71546.5349 | 73285.5122 | 75019.0832 | 75984.8116 | 76799.5031 | 77585.6821 | 78329.4833 | 79029.8071 | 79715.1531 | 80374
| plus: Energy Efficiency Program Savings Forecast |  | 3310.5748 | 3687.4731 | 4064.3713 | 4441.2696 | 4818.1679 | 5195.0661 | 5571.9644 | 5948.8626 | 6325.7609 | 6702.6591
| Total Winter Peak Demand (before Reductions from Energy Efficiency Programs) |  | 74857.1098 | 76972.9853 | 79083.4546 | 80426.0812 | 81617.671 | 82780.7482 | 83901.4476 | 84978.6697 | 86040.9139 | 87076.6591
| less: Incremental Rooftop PV Forecast |  | -72.1229 | -95.4744 | -118.8258 | -142.1773 | -165.5927 | -188.9441 | -212.2956 | -235.647 | -259.0625 | -282
| less: Load Resources providing Responsive Reserves |  | -1480.938 | -1480.938 | -1480.938 | -1480.938 | -1480.938 | -1480.938 | -1480.938 | -1480.938 | -1480.938 | -1480.938
| less: Load Resources providing Non-Spinning Reserves |  | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502 | -47.9502
| less: Emergency Response Service (10- and 30-min ramp products) |  | -1040.0022 | -1040.0022 | -1040.0022 | -1040.0022 | -1040.0022 | -1040.0022 | -1040.0022 | -1040.0022 | -1040.0022 | -1040.0022
| less: TDSP Standard Offer Load Management Programs |  | -70.38 | -70.38 | -70.38 | -70.38 | -70.38 | -70.38 | -70.38 | -70.38 | -70.38 | -70.38
| less: Energy Efficiency Program Savings Forecast |  | -3310.5748 | -3687.4731 | -4064.3713 | -4441.2696 | -4818.1679 | -5195.0661 | -5571.9644 | -5948.8626 | -6325.7609 | -6702.6591
| Firm Peak Demand, MW |  | 68835.1416 | 70550.7674 | 72260.987 | 73203.3639 | 73994.6401 | 74757.4676 | 75477.9173 | 76154.8897 | 76816.8202 | 77452.7296
Resources, MW: |  |  | Expected Capacity Available for Winter Peak Demands
|  | Cumulative Installed Capacity Ratings by 2027 (see Note) | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032/2033 | 2033/2034
| Installed Winter-rated Capacity, Thermal | 73239.33 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1
| Hydroelectric, Peak Average Capacity Contribution (73% of installed capacity) | 563.3 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543
| Switchable Capacity | 3840.12 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816
| less: Switchable Capacity Unavailable to ERCOT | -185 | -185 | -185 | -185 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Available Mothballed Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity from Private Use Networks | 9575 | 3578.925 | 3578.925 | 3578.925 | 3573.925 | 3573.925 | 3573.925 | 3573.925 | 3573.925 | 3573.925 | 3573.925
| Coastal Wind, Peak Average Capacity Contribution (56% of installed capacity) | 5436.37 | 3040.912 | 3040.912 | 3040.912 | 3040.912 | 3040.912 | 3040.912 | 3040.912 | 3040.912 | 3040.912 | 3040.912
| Panhandle Wind, Peak Average Capacity Contribution (37% of installed capacity) | 4410.43 | 1630.849 | 1630.849 | 1630.849 | 1630.849 | 1630.849 | 1630.849 | 1630.849 | 1630.849 | 1630.849 | 1630.849
| Other Wind, Peak Average Capacity Contribution (26% of installed capacity) | 27896.15 | 7238.712 | 7238.712 | 7238.712 | 7238.712 | 7238.712 | 7238.712 | 7238.712 | 7238.712 | 7238.712 | 7238.712
| Solar Utility-Scale, Peak Average Capacity Contribution (14% of installed capacity) | 15658.81 | 2168.992 | 2168.992 | 2168.992 | 2168.992 | 2168.992 | 2168.992 | 2168.992 | 2168.992 | 2168.992 | 2168.992
| Storage, Peak Average Capacity Contribution | 3285.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RMR Capacity to be under Contract | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity Pending Retirement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, MW | 143720.07 | 90499.4443 | 90499.4443 | 90499.4443 | 90679.4443 | 90679.4443 | 90679.4443 | 90679.4443 | 90679.4443 | 90679.4443 | 90679.4443
| Non-Synchronous Ties (Based on average net import contribution during winter 2020/21 EEA events) | 1220 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8
| Planned Resources (not wind, solar or storage) with Signed IA, Air Permits and Adequate Water Supplies | 1683.6 | 1470 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution (56% of installed capacity) | 461.8 | 0 | 258.608 | 258.608 | 258.608 | 258.608 | 258.608 | 258.608 | 258.608 | 258.608 | 258.608
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution (37% of installed capacity) | 696.7 | 257.779 | 257.779 | 257.779 | 257.779 | 257.779 | 257.779 | 257.779 | 257.779 | 257.779 | 257.779
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution (26% of installed capacity) | 2947.8 | 675.168 | 766.428 | 766.428 | 766.428 | 766.428 | 766.428 | 766.428 | 766.428 | 766.428 | 766.428
| Planned Solar Utility-Scale, Peak Average Capacity Contribution (14% of installed capacity) | 30232.7 | 2919.672 | 3975.37 | 4204.578 | 4232.578 | 4232.578 | 4232.578 | 4232.578 | 4232.578 | 4232.578 | 4232.578
| Planned Storage, Peak Average Capacity Contribution | 10788.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Planned Generation Capacity, MW | 46810.8 | 5322.619 | 6877.585 | 7106.793 | 7134.793 | 7134.793 | 7134.793 | 7134.793 | 7134.793 | 7134.793 | 7134.793
| Total Capacity, MW | 191750.87 | 96541.8633 | 98096.8293 | 98326.0373 | 98534.0373 | 98534.0373 | 98534.0373 | 98534.0373 | 98534.0373 | 98534.0373 | 98534.0373
|  |  | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032/2033 | 2033/2034
| Reserve Margin |  | 40.25% | 39.04% | 36.07% | 34.6% | 33.16% | 31.8% | 30.55% | 29.39% | 28.27% | 27.22%
(Total Resources - Firm Load Forecast) / Firm Load Forecast
Note on Installed Capacities: Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer.

## WinterCapacities
| Unit Megawatt Capacities - Winter | [7 empty] | WINTER CAPACITY (MW)
| UNIT NAME | INR | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | INSTALLED CAPACITY RATING (MW) | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032/2033 | 2033/2034
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1269 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1269 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1365 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1365 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340 | 1340
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 650 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 615 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 615 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605
11 | FAYETTE POWER U2 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 460 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 555 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 922 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 893 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 956.8 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 893 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 893 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 893 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 916.8 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 916.8 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 430 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 1008 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 174.6 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 174.6 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 734.1 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 734.1 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 614.6 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 653.99 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 222 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
35 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 352.8 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 351 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 242 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
40 | BEACHWOOD POWER STATION U1 |  | BCH_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
41 | BEACHWOOD POWER STATION U2 |  | BCH_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
42 | BEACHWOOD POWER STATION U3 |  | BCH_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
43 | BEACHWOOD POWER STATION U4 |  | BCH_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
44 | BEACHWOOD POWER STATION U5 |  | BCH_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
45 | BEACHWOOD POWER STATION U6 |  | BCH_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
46 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9
47 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9
48 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 188.7 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5
49 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 94.95 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2
50 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 254.15 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7
51 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
52 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
53 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 275.57 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
54 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-CC | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
55 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-CC | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
56 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
57 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
58 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
59 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
60 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
61 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
62 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
63 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 765 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
64 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 765 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
65 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
66 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 79.6 | 79.6 | 79.6 | 79.6 | 79.6 | 79.6 | 79.6 | 79.6 | 79.6 | 79.6
67 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 86.7 | 86.7 | 86.7 | 86.7 | 86.7 | 86.7 | 86.7 | 86.7 | 86.7 | 86.7
68 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9
69 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 105 | 107.2 | 107.2 | 107.2 | 107.2 | 107.2 | 107.2 | 107.2 | 107.2 | 107.2 | 107.2
70 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 108.8 | 110.7 | 110.7 | 110.7 | 110.7 | 110.7 | 110.7 | 110.7 | 110.7 | 110.7 | 110.7
71 | COLORADO BEND II CTG 7 |  | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 360.2 | 360.2 | 360.2 | 360.2 | 360.2 | 360.2 | 360.2 | 360.2 | 360.2 | 360.2
72 | COLORADO BEND II CTG 8 |  | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 359.6 | 359.6 | 359.6 | 359.6 | 359.6 | 359.6 | 359.6 | 359.6 | 359.6 | 359.6
73 | COLORADO BEND II STG 9 |  | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 508.5 | 490.5 | 490.5 | 490.5 | 490.5 | 490.5 | 490.5 | 490.5 | 490.5 | 490.5 | 490.5
74 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
75 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
76 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
77 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2002 | 150 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
78 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
79 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
80 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 120 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
81 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
82 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
83 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
84 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
85 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
86 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
87 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
88 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
89 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
90 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
91 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
92 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 190.4 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
93 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 199 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
94 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 274.5 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
95 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
96 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
97 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
98 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
99 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4
100 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4
101 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 202 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
102 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245
103 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 140 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
104 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
105 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
106 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
107 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
108 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
109 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
110 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 204 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
111 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
112 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
113 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
114 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
115 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
116 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
117 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418
118 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418
119 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7
120 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7
121 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
122 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
123 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8
124 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7
125 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 129 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
126 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 225 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
127 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 387 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
128 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
129 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
130 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
131 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
132 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
133 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
134 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
135 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
136 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
137 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
138 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
139 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 100 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
140 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
141 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
142 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
143 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
144 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
145 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
146 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375
147 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
148 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
149 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
150 | HAYS ENERGY FACILITY CSG 2 | 21INR0527 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
151 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242
152 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243
153 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
154 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
155 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 198.05 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
156 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
157 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
158 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
159 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
160 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 320.6 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
161 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 320.6 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
162 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 185 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
163 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 107 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
164 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 397 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
165 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 531 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523
166 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
167 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
168 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
169 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
170 | LAMAR ENERGY CENTER STG 1 | 23INR0486 | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
171 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
172 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4
173 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4
174 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
175 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
176 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
177 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
178 | LIGNIN (CHAMON 2) U1 |  | LIG_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
179 | LIGNIN (CHAMON 2) U2 |  | LIG_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
180 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
181 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
182 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 204 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192
183 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6
184 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6
185 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 258.4 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9
186 | MIDLOTHIAN ENERGY FACILITY CTG 1 | 23INR0489 | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
187 | MIDLOTHIAN ENERGY FACILITY CTG 2 | 21INR0534 | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256
188 | MIDLOTHIAN ENERGY FACILITY CTG 3 | 22INR0543 | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
189 | MIDLOTHIAN ENERGY FACILITY CTG 4 | 22INR0523 | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
190 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276
191 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278
192 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
193 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
194 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
195 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
196 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
197 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
198 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
199 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
200 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
201 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
202 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 351 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
203 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 445 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
204 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 435 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410
205 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 176 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2
206 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 176 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1
207 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 176 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2
208 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 176 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1
209 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 224 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217
210 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 224 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217
211 | OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
212 | OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
213 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224
214 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224
215 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316
216 | PANDA TEMPLE I POWER CTG 1 | 22INR0533 | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 232 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222
217 | PANDA TEMPLE I POWER CTG 2 | 22INR0533 | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 232 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209
218 | PANDA TEMPLE I POWER STG 1 | 22INR0533 | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
219 | PANDA TEMPLE II POWER CTG 1 | 23INR0524 | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
220 | PANDA TEMPLE II POWER CTG 2 | 23INR0524 | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
221 | PANDA TEMPLE II POWER STG 1 | 23INR0524 | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
222 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
223 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
224 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 90 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
225 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
226 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
227 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 195.5 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
228 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
229 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
230 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
231 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
232 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 89.4 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
233 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 89.4 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
234 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 89.4 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
235 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 89.4 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
236 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 89.4 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
237 | PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
238 | PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
239 | PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
240 | PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
241 | PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
242 | PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
243 | PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
244 | PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
245 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
246 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
247 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
248 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
249 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
250 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
251 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 25 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5
252 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 43.2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
253 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
254 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
255 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
256 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
257 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98.1 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
258 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98.1 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
259 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
260 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
261 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 74.98 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
262 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 113.61 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
263 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 216.01 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
264 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 88.4 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
265 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 113.64 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
266 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 156.6 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
267 | RABBS POWER STATION U1 |  | RAB_UNIT1 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
268 | RABBS POWER STATION U2 |  | RAB_UNIT2 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
269 | RABBS POWER STATION U3 |  | RAB_UNIT3 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
270 | RABBS POWER STATION U4 |  | RAB_UNIT4 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
271 | RABBS POWER STATION U5 |  | RAB_UNIT5 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
272 | RABBS POWER STATION U6 |  | RAB_UNIT6 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
273 | RABBS POWER STATION U7 |  | RAB_UNIT7 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
274 | RABBS POWER STATION U8 |  | RAB_UNIT8 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
275 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
276 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
277 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
278 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
279 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
280 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
281 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
282 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 373.16 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
283 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
284 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
285 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
286 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 41.98 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
287 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
288 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
289 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
290 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
291 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
292 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
293 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 198.9 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
294 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
295 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
296 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 191 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
297 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 60.5 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
298 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 50 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
299 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 25 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
300 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 136 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
301 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
302 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 351 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340
303 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 25.71 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
304 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 25.71 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
305 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 177 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
306 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 479 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
307 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 16.32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
308 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
309 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
310 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
311 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
312 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
313 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 51.3 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
314 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
315 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
316 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
317 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
318 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
319 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
320 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
321 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
322 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
323 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
324 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
325 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
326 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
327 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 143.65 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5
328 | TEXAS GULF SULPHUR CTG 1 |  | TGS_GT01 | WHARTON | GAS-GT | SOUTH | 1985 | 94 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9
329 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 239 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
330 | TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
331 | TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
332 | TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
333 | TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
334 | TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
335 | TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
336 | TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
337 | TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
338 | TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
339 | TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
340 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
341 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
342 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
343 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
344 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 225 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217
345 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
346 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 420 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412
347 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
348 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
349 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
350 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
351 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 196.86 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
352 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 180.2 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
353 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 16.32 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
354 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
355 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
356 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 299.2 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
357 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 580.5 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552
358 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
359 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
360 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
361 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 20 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
362 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
363 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
364 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
365 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
366 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 275 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8
367 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 275 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8
368 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 290 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298
369 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4
370 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 235.4 | 235.4 | 235.4 | 235.4 | 235.4 | 235.4 | 235.4 | 235.4 | 235.4 | 235.4
371 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 300 | 269 | 269 | 269 | 269 | 269 | 269 | 269 | 269 | 269 | 269
372 | WOLF HOLLOW 2 CTG 4 |  | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 360 | 353.3 | 353.3 | 353.3 | 353.3 | 353.3 | 353.3 | 353.3 | 353.3 | 353.3 | 353.3
373 | WOLF HOLLOW 2 CTG 5 |  | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 360 | 354.6 | 354.6 | 354.6 | 354.6 | 354.6 | 354.6 | 354.6 | 354.6 | 354.6 | 354.6
374 | WOLF HOLLOW 2 STG 6 |  | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 511.2 | 473.1 | 473.1 | 473.1 | 473.1 | 473.1 | 473.1 | 473.1 | 473.1 | 473.1 | 473.1
375 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 116.45 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
376 | BIOENERGY AUSTIN-WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
377 | BIOENERGY TEXAS-COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
378 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
379 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
380 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
381 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
382 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
383 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
384 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
385 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
386 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 72744.83 | 68392.9 | 68392.9 | 68392.9 | 68392.9 | 68392.9 | 68392.9 | 68392.9 | 68392.9 | 68392.9 | 68392.9
387
388 | Operational Resources - Synchronized but not Approved for Commercial Operations (Thermal)
389 | BRANDON (LP&L) (DGR) | 21INR0201 | BRANDON_UNIT1 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
390 | BROTMAN POWER STATION U3 | 23INR0095 | BTM_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
391 | BROTMAN POWER STATION U4 | 23INR0095 | BTM_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
392 | BROTMAN POWER STATION U5 | 23INR0095 | BTM_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
393 | BROTMAN POWER STATION U6 | 23INR0095 | BTM_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
394 | COLORADO BEND ENERGY CENTER CTG 11 | 21INR0512 | CBEC_GT11 | WHARTON | GAS-GT | HOUSTON | 2023 | 41.65 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
395 | COLORADO BEND ENERGY CENTER CTG 12 | 21INR0512 | CBEC_GT12 | WHARTON | GAS-GT | HOUSTON | 2023 | 41.65 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
396 | R MASSENGALE CTG 1 (LP&L) | 21INR0202 | MASSENGL_G6 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
397 | R MASSENGALE CTG 2 (LP&L) | 21INR0202 | MASSENGL_G7 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
398 | R MASSENGALE STG (LP&L) | 21INR0202 | MASSENGL_G8 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 58.9 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
399 | TY COOKE CTG 1 (LP&L) | 21INR0506 | TY_COOKE_GT2 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 18.7 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
400 | TY COOKE CTG 2 (LP&L) | 21INR0506 | TY_COOKE_GT3 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 26.6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
401 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 494.5 | 402.2 | 402.2 | 402.2 | 402.2 | 402.2 | 402.2 | 402.2 | 402.2 | 402.2 | 402.2
402
403 | Operational Capacity Thermal Unavailable due to Extended Outage or Derate |  | THERMAL_UNAVAIL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
404 | Operational Capacity Thermal Total |  | THERMAL_OPERATIONAL |  |  |  |  | 73239.33 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1 | 68795.1
405
406 | Operational Resources (Hydro)
407 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 34.7 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
408 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 34.7 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
409 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
410 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
411 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
412 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
413 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 18.3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
414 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 50.8 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
415 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 50.8 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
416 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
417 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
418 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
419 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 10.5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
420 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 27 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
421 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 27 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
422 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
423 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
424 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
425 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
426 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
427 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
428 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
429 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
430 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
431 | Operational Capacity Total (Hydro) | [6 empty] | 549.6 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4 | 557.4
432 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 549.6 | 405 | 405 | 405 | 405 | 405 | 405 | 405 | 405 | 405 | 405
433
434 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
435 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
436 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDTP_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
437 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
438 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
439 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
440 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
441 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  |  |  |  | 19.7 | 14.3138 | 14.3138 | 14.3138 | 14.3138 | 14.3138 | 14.3138 | 14.3138 | 14.3138 | 14.3138 | 14.3138
442
443 | Operational Capacity Hydroelectric Unavailable due to Extended Outage or Derate |  | HYDRO_UNAVAIL |  |  |  |  | -6 | -4.3595 | -4.3595 | -4.3595 | -4.3595 | -4.3595 | -4.3595 | -4.3595 | -4.3595 | -4.3595 | -4.3595
444 | Operational Capacity Hydroelectric Total |  | HYDRO_OPERATIONAL |  |  |  |  | 563.3 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543
445
446 | Operational Resources (Switchable)
447 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
448 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
449 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
450 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
451 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
452 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
453 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
454 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
455 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
456 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 179 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
457 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179
458 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 179 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
459 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
460 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
461 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
462 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330
463 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
464 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
465 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330
466 | Switchable Capacity Total | [6 empty] | 3840.12 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816 | 3816
467
468 | Switchable Capacity Unavailable to ERCOT
469 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
471 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
472 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
473 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
474 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101_UNAVAIL | FANNIN | GAS-CC | NORTH | 2003 | -185 | -185 | -185 | -185 | 0 | 0 | 0 | 0 | 0 | 0 | 0
475 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -185 | -185 | -185 | -185 | 0 | 0 | 0 | 0 | 0 | 0 | 0
476
477 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | GAS |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
478
479 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 9575 | 3650 | 3650 | 3650 | 3650 | 3650 | 3650 | 3650 | 3650 | 3650 | 3650
480 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  |  |  |  | 0 | -71.075 | -71.075 | -71.075 | -76.075 | -76.075 | -76.075 | -76.075 | -76.075 | -76.075 | -76.075
481
482 | Operational Resources (Wind)
483 | WESTERN TRAIL WIND (AJAX WIND) U1 |  | AJAXWIND_UNIT1 | WILBARGER | WIND-O | WEST | 2022 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6
484 | WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WILBARGER | WIND-O | WEST | 2022 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
485 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
486 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8
487 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7
488 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.83 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
489 | AQUILLA LAKE WIND U1 |  | AQUILLA_U1_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
490 | AQUILLA LAKE WIND U2 |  | AQUILLA_U1_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4
491 | AQUILLA LAKE 2 WIND U1 |  | AQUILLA_U2_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
492 | AQUILLA LAKE 2 WIND U2 |  | AQUILLA_U2_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8
493 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.12 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1
494 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.64 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6
495 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.26 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3
496 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
497 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
498 | BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | ANDREWS | WIND-O | WEST | 2021 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2
499 | BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | ANDREWS | WIND-O | WEST | 2021 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5
500 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
501 | BLUE SUMMIT WIND 1 A | 22INR0550 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 132.84 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8
502 | BLUE SUMMIT WIND 1 B | 22INR0550 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 6.96 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
503 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 92.5 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
504 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.86 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5
505 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.7 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
506 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 186.5 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4
507 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
508 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.85 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8
509 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
510 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
511 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9
512 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7
513 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
514 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
515 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
516 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
517 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 89 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
518 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
519 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
520 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4
521 | CACTUS FLATS WIND U1 |  | CFLATS_U1 | CONCHO | WIND-O | WEST | 2022 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4
522 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1
523 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
524 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 134.42 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
525 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 123.6 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
526 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1
527 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7
528 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
529 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9
530 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | STERLING | WIND-O | WEST | 2008 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
531 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
532 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
533 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.25 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3
534 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
535 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
536 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4
537 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
538 | CRANELL WIND |  | CRANELL_UNIT1 | REFUGIO | WIND-C | COASTAL | 2022 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
539 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
540 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
541 | DESERT SKY WIND 1 A | 17INR0070 | DSKYWND1_UNIT_1A | PECOS | WIND-O | WEST | 2022 | 65.79 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1
542 | DESERT SKY WIND 1 B | 17INR0070 | DSKYWND2_UNIT_2A | PECOS | WIND-O | WEST | 2022 | 65.79 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
543 | DESERT SKY WIND 2 A | 17INR0070 | DSKYWND1_UNIT_1B | PECOS | WIND-O | WEST | 2022 | 23.93 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7
544 | DESERT SKY WIND 2 B | 17INR0070 | DSKYWND2_UNIT_2B | PECOS | WIND-O | WEST | 2022 | 14.74 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
545 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
546 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
547 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 101.2 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
548 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 99 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
549 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
550 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 101.31 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
551 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 134.29 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
552 | EL ALGODON ALTO W U1 |  | ALGODON_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6
553 | EL ALGODON ALTO W U2 |  | ALGODON_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
554 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2
555 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2
556 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
557 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8
558 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6
559 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.48 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5
560 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8
561 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
562 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
563 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
564 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
565 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
566 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
567 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4
568 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
569 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 21INR0532 | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
570 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 21INR0532 | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
571 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
572 | GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7
573 | GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9
574 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
575 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
576 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.93 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9
577 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 165.6 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
578 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9
579 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
580 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
581 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5
582 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
583 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
584 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
585 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
586 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
587 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 51.9 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
588 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3
589 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.4 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5
590 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3
591 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.5 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6
592 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.5 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
593 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 134.81 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
594 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 101.69 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
595 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
596 | HORSE HOLLOW WIND 2 | 17INR0053 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
597 | HORSE HOLLOW WIND 3 | 17INR0053 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4
598 | HORSE HOLLOW WIND 4 | 17INR0053 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
599 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
600 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
601 | INDIAN MESA WIND | 18INR0069 | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8 | 91.8
602 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.69 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
603 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
604 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
605 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
606 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
607 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.15 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2
608 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.55 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
609 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
610 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
611 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.42 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
612 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
613 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
614 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
615 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
616 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
617 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 159.96 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
618 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7
619 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.26 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3
620 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.85 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
621 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
622 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
623 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
624 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
625 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
626 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
627 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
628 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
629 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
630 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
631 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
632 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
633 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
634 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
635 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.83 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
636 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.46 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5
637 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
638 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
639 | MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | CONCHO | WIND-O | WEST | 2022 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
640 | MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | CONCHO | WIND-O | WEST | 2022 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
641 | MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | CONCHO | WIND-O | WEST | 2022 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
642 | MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | CONCHO | WIND-O | WEST | 2022 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
643 | MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | CONCHO | WIND-O | WEST | 2022 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
644 | MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | CONCHO | WIND-O | WEST | 2022 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
645 | MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | CONCHO | WIND-O | WEST | 2022 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
646 | MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | CONCHO | WIND-O | WEST | 2022 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
647 | MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | CONCHO | WIND-O | WEST | 2022 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8
648 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
649 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
650 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
651 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
652 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
653 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8
654 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
655 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.61 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
656 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
657 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
658 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
659 | OVEJA WIND U1 |  | OVEJA_G1 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
660 | OVEJA WIND U2 |  | OVEJA_G2 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
661 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9
662 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
663 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
664 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.19 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
665 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
666 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
667 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
668 | PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | HOWARD | WIND-O | WEST | 2022 | 106.92 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9
669 | PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | HOWARD | WIND-O | WEST | 2022 | 108.54 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5
670 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.85 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9
671 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.12 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
672 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7
673 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8
674 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
675 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
676 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
677 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
678 | PYRON WIND 1 | 23INR0525 | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
679 | PYRON WIND 2 | 23INR0525 | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5
680 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
681 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
682 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6
683 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7
684 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6
685 | RELOJ DEL SOL WIND U1 |  | RELOJ_UNIT1 | ZAPATA | WIND-O | SOUTH | 2022 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
686 | RELOJ DEL SOL WIND U2 |  | RELOJ_UNIT2 | ZAPATA | WIND-O | SOUTH | 2022 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
687 | RELOJ DEL SOL WIND U3 |  | RELOJ_UNIT3 | ZAPATA | WIND-O | SOUTH | 2022 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1
688 | RELOJ DEL SOL WIND U4 |  | RELOJ_UNIT4 | ZAPATA | WIND-O | SOUTH | 2022 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8
689 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
690 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.44 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4
691 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
692 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
693 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
694 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9
695 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9
696 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
697 | SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
698 | SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
699 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
700 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
701 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.25 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
702 | SAND BLUFF WIND U1 |  | MCDLD_SB1_2 | GLASSCOCK | WIND-O | WEST | 2022 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
703 | SAND BLUFF WIND U2 |  | MCDLD_SB3_282 | GLASSCOCK | WIND-O | WEST | 2022 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1
704 | SAND BLUFF WIND U3 |  | MCDLD_SB4_G87 | GLASSCOCK | WIND-O | WEST | 2022 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
705 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
706 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
707 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.24 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
708 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.05 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1
709 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1
710 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
711 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8
712 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
713 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
714 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
715 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8
716 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 101.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2
717 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 160.95 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
718 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
719 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
720 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 123.6 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
721 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
722 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 213.82 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2
723 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 166.52 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7
724 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 37.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
725 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8
726 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 105.3 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8
727 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 30.78 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
728 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 108.54 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6
729 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 119 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
730 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 105.8 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
731 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 80.5 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
732 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
733 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
734 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
735 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
736 | TG EAST WIND U1 |  | TRUSGILL_UNIT1 | KNOX | WIND-O | WEST | 2022 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
737 | TG EAST WIND U2 |  | TRUSGILL_UNIT2 | KNOX | WIND-O | WEST | 2022 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8
738 | TG EAST WIND U3 |  | TRUSGILL_UNIT3 | KNOX | WIND-O | WEST | 2022 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
739 | TG EAST WIND U4 |  | TRUSGILL_UNIT4 | KNOX | WIND-O | WEST | 2022 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2
740 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
741 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
742 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5 | 127.5
743 | TRENT WIND 1 A | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 38.25 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
744 | TRENT WIND 1 B |  | TRENT_UNIT_1B | NOLAN | WIND-O | WEST | 2018 | 15.59 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
745 | TRENT WIND 2 |  | TRENT_UNIT_2 | NOLAN | WIND-O | WEST | 2018 | 50.49 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5
746 | TRENT WIND 3 A |  | TRENT_UNIT_3A | NOLAN | WIND-O | WEST | 2018 | 38.25 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
747 | TRENT WIND 3 B |  | TRENT_UNIT_3B | NOLAN | WIND-O | WEST | 2018 | 13.79 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8
748 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4
749 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6
750 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
751 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 174.6 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
752 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6
753 | VENADO WIND U1 |  | VENADO_UNIT1 | ZAPATA | WIND-O | SOUTH | 2021 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
754 | VENADO WIND U2 |  | VENADO_UNIT2 | ZAPATA | WIND-O | SOUTH | 2021 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
755 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
756 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
757 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
758 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
759 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
760 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
761 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.91 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9
762 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.35 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3
763 | WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6
764 | WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2
765 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 59.8 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
766 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.34 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3
767 | WHITE MESA WIND U1 |  | WHMESA_UNIT1 | CROCKETT | WIND-O | WEST | 2022 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
768 | WHITE MESA 2 WIND U1 |  | WHMESA_UNIT2_23 | CROCKETT | WIND-O | WEST | 2022 | 13.92 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
769 | WHITE MESA 2 WIND U2 |  | WHMESA_UNIT2_28 | CROCKETT | WIND-O | WEST | 2022 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3
770 | WHITE MESA 2 WIND U3 |  | WHMESA_UNIT3_23 | CROCKETT | WIND-O | WEST | 2022 | 18.56 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
771 | WHITE MESA 2 WIND U4 |  | WHMESA_UNIT3_28 | CROCKETT | WIND-O | WEST | 2022 | 132.54 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5
772 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
773 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
774 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
775 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.62 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6
776 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
777 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
778 | Operational Capacity Total (Wind) | [6 empty] | 31558.05 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7 | 31494.7
779
780 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 4862.27 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1 | 4856.1
781 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 100 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
782
783 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4410.43 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7 | 4407.7
784 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 100 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
785
786 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 22285.35 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9 | 22230.9
787 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 100 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
788
789 | Operational Resources (Wind) - Synchronized but not Approved for Commercial Operations
790 | AGUAYO WIND U1 | 20INR0250 | AGUAYO_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 193.5 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9
791 | ANCHOR WIND U1 | 21INR0546 | ANCHOR_WIND1 | CALLAHAN | WIND-O | WEST | 2023 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
792 | ANCHOR WIND U2 | 21INR0387 | ANCHOR_WIND2 | CALLAHAN | WIND-O | WEST | 2023 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
793 | ANCHOR WIND U3 | 21INR0539 | ANCHOR_WIND3 | CALLAHAN | WIND-O | WEST | 2023 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
794 | ANCHOR WIND U4 | 21INR0539 | ANCHOR_WIND4 | CALLAHAN | WIND-O | WEST | 2023 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7
795 | ANCHOR WIND U5 | 22INR0562 | ANCHOR_WIND5 | CALLAHAN | WIND-O | WEST | 2023 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3
796 | APPALOOSA RUN WIND U1 | 20INR0249 | APPALOSA_UNIT1 | UPTON | WIND-O | WEST | 2023 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9
797 | APPALOOSA RUN WIND U2 | 20INR0249 | APPALOSA_UNIT2 | UPTON | WIND-O | WEST | 2023 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
798 | APOGEE WIND U1 | 21INR0467 | APOGEE_UNIT1 | THROCKMORTON | WIND-O | WEST | 2023 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
799 | APOGEE WIND U2 | 21INR0467 | APOGEE_UNIT2 | THROCKMORTON | WIND-O | WEST | 2023 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
800 | APOGEE WIND U3 | 21INR0467 | APOGEE_UNIT3 | THROCKMORTON | WIND-O | WEST | 2023 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
801 | APOGEE WIND U4 | 21INR0467 | APOGEE_UNIT4 | THROCKMORTON | WIND-O | WEST | 2023 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
802 | APOGEE WIND U5 | 21INR0467 | APOGEE_UNIT5 | THROCKMORTON | WIND-O | WEST | 2023 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
803 | APOGEE WIND U6 | 21INR0467 | APOGEE_UNIT6 | THROCKMORTON | WIND-O | WEST | 2023 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
804 | APOGEE WIND U7 | 21INR0467 | APOGEE_UNIT7 | THROCKMORTON | WIND-O | WEST | 2023 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
805 | BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | CALLAHAN | WIND-O | WEST | 2023 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
806 | BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | CALLAHAN | WIND-O | WEST | 2023 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
807 | BLACKJACK CREEK WIND U1 | 20INR0068 | BLACKJAK_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
808 | BLACKJACK CREEK WIND U2 | 20INR0068 | BLACKJAK_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
809 | BOARD CREEK WP U1 | 21INR0324 | BOARDCRK_UNIT1 | NAVARRO | WIND-O | NORTH | 2023 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8
810 | BOARD CREEK WP U2 | 21INR0324 | BOARDCRK_UNIT2 | NAVARRO | WIND-O | NORTH | 2023 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4
811 | COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | SCURRY | WIND-O | WEST | 2023 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
812 | COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | SCURRY | WIND-O | WEST | 2023 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6
813 | COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | SCURRY | WIND-O | WEST | 2023 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
814 | EL SUAZ RANCH U1 | 20INR0097 | ELSAUZ_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
815 | EL SUAZ RANCH U2 | 20INR0097 | ELSAUZ_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
816 | FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2
817 | FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
818 | FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | BEE | WIND-O | SOUTH | 2023 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
819 | HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | GLASSCOCK | WIND-O | WEST | 2023 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
820 | INERTIA WIND U1 | 22INR0326 | INRT_W_UNIT1 | HASKELL | WIND-O | WEST | 2023 | 67.68 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7
821 | INERTIA WIND U2 | 22INR0326 | INRT_W_UNIT2 | HASKELL | WIND-O | WEST | 2023 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
822 | INERTIA WIND U3 | 22INR0326 | INRT_W_UNIT3 | HASKELL | WIND-O | WEST | 2023 | 205.86 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9
823 | LACY CREEK WIND U1 | 18INR0043 | LACY_CRK_UNIT1 | GLASSCOCK | WIND-O | WEST | 2023 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4
824 | LACY CREEK WIND U2 | 18INR0043 | LACY_CRK_UNIT2 | GLASSCOCK | WIND-O | WEST | 2023 | 15.12 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
825 | LACY CREEK WIND U3 | 18INR0043 | LACY_CRK_UNIT3 | GLASSCOCK | WIND-O | WEST | 2023 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2
826 | LACY CREEK WIND U4 | 18INR0043 | LACY_CRK_UNIT4 | GLASSCOCK | WIND-O | WEST | 2023 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6
827 | LAS MAJADAS WIND U1 | 17INR0035 | LMAJADAS_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
828 | LAS MAJADAS WIND U2 | 17INR0035 | LMAJADAS_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
829 | LAS MAJADAS WIND U3 | 17INR0035 | LMAJADAS_UNIT3 | WILLACY | WIND-C | COASTAL | 2023 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6
830 | MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | NOLAN | WIND-O | WEST | 2023 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4
831 | MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | STARR | WIND-O | SOUTH | 2023 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
832 | PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | LIMESTONE | WIND-O | NORTH | 2023 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
833 | PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | LIMESTONE | WIND-O | NORTH | 2023 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
834 | PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2
835 | PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | MILLS | WIND-O | NORTH | 2023 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
836 | VORTEX WIND U1 | 20INR0120 | VORTEX_WIND1 | THROCKMORTON | WIND-O | WEST | 2023 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
837 | VORTEX WIND U2 | 20INR0120 | VORTEX_WIND2 | THROCKMORTON | WIND-O | WEST | 2023 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2
838 | VORTEX WIND U3 | 20INR0120 | VORTEX_WIND3 | THROCKMORTON | WIND-O | WEST | 2023 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4
839 | VORTEX WIND U4 | 20INR0120 | VORTEX_WIND4 | THROCKMORTON | WIND-O | WEST | 2023 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
840 | WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | FISHER | WIND-O | WEST | 2023 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4
841 | WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | FISHER | WIND-O | WEST | 2023 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5
842 | WILDWIND U1 | 20INR0033 | WILDWIND_UNIT1 | COOKE | WIND-O | NORTH | 2023 | 18.38 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4
843 | WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | COOKE | WIND-O | NORTH | 2023 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
844 | WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | COOKE | WIND-O | NORTH | 2023 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
845 | WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | COOKE | WIND-O | NORTH | 2023 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
846 | WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | COOKE | WIND-O | NORTH | 2023 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8
847 | YOUNG WIND U1 | 21INR0401 | YNG_WND_UNIT1 | YOUNG | WIND-O | WEST | 2023 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4 | 197.4
848 | YOUNG WIND U2 | 21INR0401 | YNG_WND_UNIT2 | YOUNG | WIND-O | WEST | 2023 | 152.28 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
849 | YOUNG WIND U3 | 21INR0401 | YNG_WND_UNIT3 | YOUNG | WIND-O | WEST | 2023 | 149.46 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
850 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 6184.9 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4 | 6184.4
851
852 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Coastal Counties) |  | WIND_SYNCHRONIZED_C |  |  |  |  | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1 | 574.1
853 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_SYNC_PEAK_PCT_C | % |  |  |  | 100 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
854
855 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Panhandle Counties) |  | WIND_SYNCHRONIZED_P |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
856 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_SYNC_PEAK_PCT_P | % |  |  |  | 100 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
857
858 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Other Counties) |  | WIND_SYNCHRONIZED_O |  |  |  |  | 5610.8 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3 | 5610.3
859 | Wind Peak Average Capacity Percentage (Other) |  | WIND_SYNC_PEAK_PCT_O | % |  |  |  | 100 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
860
861 | Operational Resources (Solar)
862 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
863 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
864 | ANSON SOLAR U1 |  | ANSON1_UNIT1 | JONES | SOLAR | WEST | 2022 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
865 | ANSON SOLAR U2 |  | ANSON1_UNIT2 | JONES | SOLAR | WEST | 2022 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
866 | ARAGORN SOLAR |  | ARAGORN_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 188.2 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
867 | AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | HASKELL | SOLAR | WEST | 2021 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9
868 | AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | HASKELL | SOLAR | WEST | 2021 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5
869 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
870 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 50 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
871 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
872 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
873 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
874 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
875 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
876 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
877 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
878 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
879 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
880 | BRIGHTSIDE SOLAR |  | BRIGHTSD_UNIT1 | BEE | SOLAR | SOUTH | 2022 | 53.4 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
881 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
882 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
883 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
884 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
885 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
886 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
887 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
888 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
889 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7
890 | CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | WEBB | SOLAR | SOUTH | 2021 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
891 | DANCIGER SOLAR U1 |  | DAG_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
892 | DANCIGER SOLAR U2 |  | DAG_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
893 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
894 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
895 | ELARA SOLAR |  | ELARA_SL_UNIT1 | FRIO | SOLAR | SOUTH | 2022 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4
896 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) |  | EGROVESL_UNIT1 | CRANE | SOLAR | WEST | 2023 | 109.5 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
897 | EUNICE SOLAR U1 |  | EUNICE_PV1 | ANDREWS | SOLAR | WEST | 2021 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6
898 | EUNICE SOLAR U2 |  | EUNICE_PV2 | ANDREWS | SOLAR | WEST | 2021 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1
899 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
900 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 152.5 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
901 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
902 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 126 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1
903 | GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | CONCHO | SOLAR | WEST | 2021 | 251.4 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
904 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 126.3 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6
905 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 132.2 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4
906 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
907 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
908 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
909 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2
910 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3
911 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5
912 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
913 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5
914 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
915 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
916 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7
917 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
918 | LILY SOLAR |  | LILY_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2021 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6
919 | LONGBOW SOLAR |  | LON_SOLAR1 | BRAZORIA | SOLAR | HOUSTON | 2022 | 78.2 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
920 | LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | BORDEN | SOLAR | WEST | 2021 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
921 | LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | BORDEN | SOLAR | WEST | 2021 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3
922 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
923 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
924 | MISAE SOLAR U1 |  | MISAE_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4
925 | MISAE SOLAR U2 |  | MISAE_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6
926 | NEBULA SOLAR (RAYOS DEL SOL) U1 |  | NEBULA_UNIT1 | CAMERON | SOLAR | COASTAL | 2022 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5
927 | NOBLE SOLAR U1 |  | NOBLESLR_SOLAR1 | DENTON | SOLAR | NORTH | 2022 | 148.8 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7
928 | NOBLE SOLAR U2 |  | NOBLESLR_SOLAR2 | DENTON | SOLAR | NORTH | 2022 | 130.2 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3
929 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
930 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
931 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.18 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2
932 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
933 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
934 | OCI ALAMO 4 SOLAR-BRACKETVILLE | 22INR0600 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.62 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
935 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
936 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2
937 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
938 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.04 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1
939 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 127.95 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1
940 | PHOENIX SOLAR |  | PHOENIX_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9
941 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
942 | PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
943 | PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
944 | PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | ANDREWS | SOLAR | WEST | 2021 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
945 | PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | ANDREWS | SOLAR | WEST | 2021 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
946 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
947 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
948 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
949 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
950 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 211.19 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
951 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
952 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
953 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PECOS | SOLAR | WEST | 2021 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222
954 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PECOS | SOLAR | WEST | 2021 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
955 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
956 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 155.44 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
957 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
958 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
959 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
960 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
961 | STRATEGIC SOLAR 1 |  | STRATEGC_UNIT1 | ELLIS | SOLAR | NORTH | 2022 | 135 | 118.3 | 118.3 | 118.3 | 118.3 | 118.3 | 118.3 | 118.3 | 118.3 | 118.3 | 118.3
962 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
963 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
964 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
965 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
966 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9
967 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9
968 | TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8
969 | TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | CULBERSON | SOLAR | WEST | 2021 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
970 | TPE ERATH SOLAR |  | DG_ERATH_ERATH21 | ERATH | SOLAR | NORTH | 2021 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
971 | VANCOURT SOLAR |  | VANCOURT_UNIT1 | CAMERON | SOLAR | COASTAL | 2023 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7
972 | VISION SOLAR 1 |  | VISION_UNIT1 | NAVARRO | SOLAR | NORTH | 2022 | 129.2 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7
973 | WAGYU SOLAR |  | WGU_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2021 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
974 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
975 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
976 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
977 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
978 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
979 | WESTORIA SOLAR U1 |  | WES_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
980 | WESTORIA SOLAR U2 |  | WES_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
981 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
982 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
983 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
984 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
985 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
986 | Operational Capacity Total (Solar) | [6 empty] | 9991.32 | 9910.9 | 9910.9 | 9910.9 | 9910.9 | 9910.9 | 9910.9 | 9910.9 | 9910.9 | 9910.9 | 9910.9
987 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 100 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
988
989 | Operational Resources (Solar) - Synchronized but not Approved for Commercial Operations
990 | BIG STAR SOLAR U1 | 21INR0413 | BIG_STAR_UNIT1 | BASTROP | SOLAR | SOUTH | 2023 | 132.27 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
991 | BIG STAR SOLAR U2 | 21INR0413 | BIG_STAR_UNIT2 | BASTROP | SOLAR | SOUTH | 2023 | 70.83 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
992 | BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | GRIMES | SOLAR | NORTH | 2023 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
993 | BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | GRIMES | SOLAR | NORTH | 2023 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
994 | BPL FILES SOLAR | 20INR0164 | FILESSLR_PV1 | HILL | SOLAR | NORTH | 2023 | 146.09 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
995 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5
996 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3
997 | CROWN SOLAR | 21INR0323 | CRWN_SLR_UNIT1 | FALLS | SOLAR | NORTH | 2023 | 101.3 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7
998 | FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 179.5 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
999 | FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 171.8 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9 | 171.9
1000 | GOLINDA SOLAR | 21INR0434 | GOLINDA_UNIT1 | FALLS | SOLAR | NORTH | 2023 | 101.1 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
1001 | GRIZZLY RIDGE SOLAR | 21INR0375 | GRIZZLY_SOLAR1 | HAMILTON | SOLAR | NORTH | 2023 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1002 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b | HOVEY_UNIT2 | PECOS | SOLAR | WEST | 2023 | 7.41 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
1003 | JADE SOLAR U1 | 22INR0360 | JADE_SLR_UNIT1 | SCURRY | SOLAR | WEST | 2023 | 158.8 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
1004 | JADE SOLAR U2 | 22INR0360 | JADE_SLR_UNIT2 | SCURRY | SOLAR | WEST | 2023 | 162.4 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
1005 | MCLEAN (SHAKES) SOLAR | 19INR0073 | MCLNSLR_UNIT1 | DIMMIT | SOLAR | SOUTH | 2023 | 207.4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1006 | MUSTANG CREEK SOLAR U1 | 18INR0050 | MUSTNGCK_SOLAR1 | JACKSON | SOLAR | SOUTH | 2023 | 60.2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1007 | MUSTANG CREEK SOLAR U2 | 18INR0050 | MUSTNGCK_SOLAR2 | JACKSON | SOLAR | SOUTH | 2023 | 90.3 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
1008 | MYRTLE SOLAR U1 | 19INR0041 | MYR_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 171.6 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2
1009 | MYRTLE SOLAR U2 | 19INR0041 | MYR_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 149.6 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8
1010 | PISGAH RIDGE SOLAR U1 | 22INR0254 | PISGAH_SOLAR1 | NAVARRO | SOLAR | NORTH | 2023 | 189.4 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5
1011 | PISGAH RIDGE SOLAR U2 | 22INR0254 | PISGAH_SOLAR2 | NAVARRO | SOLAR | NORTH | 2023 | 64.4 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
1012 | PLAINVIEW SOLAR (RAMSEY SOLAR) U1 | 20INR0130 | PLN_UNIT1 | WHARTON | SOLAR | SOUTH | 2023 | 270 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
1013 | PLAINVIEW SOLAR (RAMSEY SOLAR) U2 | 20INR0130 | PLN_UNIT2 | WHARTON | SOLAR | SOUTH | 2023 | 270 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
1014 | RADIAN SOLAR U1 | 21INR0205 | RADN_SLR_UNIT1 | BROWN | SOLAR | NORTH | 2023 | 161.41 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9
1015 | RADIAN SOLAR U2 | 21INR0205 | RADN_SLR_UNIT2 | BROWN | SOLAR | NORTH | 2023 | 166.02 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9
1016 | RATLIFF SOLAR (CONCHO VALLEY SOLAR) | 21INR0384 | RATLIFF_SOLAR1 | TOM GREEN | SOLAR | WEST | 2023 | 162.43 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8
1017 | ROSELAND SOLAR U1 | 20INR0205 | ROSELAND_SOLAR1 | FALLS | SOLAR | NORTH | 2023 | 254 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
1018 | ROSELAND SOLAR U2 | 20INR0205 | ROSELAND_SOLAR2 | FALLS | SOLAR | NORTH | 2023 | 167.9 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3 | 165.3
1019 | ROSELAND SOLAR U3 | 22INR0506 | ROSELAND_SOLAR3 | FALLS | SOLAR | NORTH | 2023 | 86.1 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7 | 84.7
1020 | ROWLAND SOLAR I | 19INR0131 | ROW_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1021 | TAYGETE II SOLAR U1 | 21INR0233 | TAYGETE2_UNIT1 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
1022 | TAYGETE II SOLAR U2 | 21INR0233 | TAYGETE2_UNIT2 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
1023 | TAVENER (FORT BEND SOLAR) | 18INR0053 | TAV_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 143.61 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6
1024 | SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1025 | SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1026 | SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1027 | SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | LAMAR | SOLAR | NORTH | 2023 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1028 | SUN VALLEY U1 | 19INR0169 | SUNVASLR_UNIT1 | HILL | SOLAR | NORTH | 2023 | 165.75 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8
1029 | SUN VALLEY U2 | 19INR0169 | SUNVASLR_UNIT2 | HILL | SOLAR | NORTH | 2023 | 86.19 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2
1030 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Solar) | [6 empty] | 5667.49 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9 | 5581.9
1031 | Solar Peak Average Capacity Percentage |  | SOLAR_SYNC_PEAK_PCT | % |  |  |  | 100 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
1032
1033 | Operational Resources (Storage)
1034 | AZURE SKY BESS |  | AZURE_BESS1 | HASKELL | STORAGE | WEST | 2022 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6
1035 | BAT CAVE |  | BATCAVE_BES1 | MASON | STORAGE | SOUTH | 2021 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
1036 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
1037 | BRP ALVIN (DGR) |  | ALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1038 | BRP ANGELTON (DGR) |  | ANGLETON_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1039 | BRP BRAZORIA |  | BRAZORIA_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1040 | BRP DICKINSON (DGR) |  | DICKNSON_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1041 | BRP HEIGHTS (DGR) |  | HEIGHTTN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1042 | BRP LOOP 463 (DGR) |  | L_463S_UNIT1 | VICTORIA | STORAGE | SOUTH | 2023 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1043 | BRP LOPENO (DGR) |  | BRP_LOP1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1044 | BRP MAGNOLIA (DGR) |  | MAGNO_TN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1045 | BRP ODESSA SW (DGR) |  | ODESW_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1046 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1047 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1048 | BRP RANCHTOWN (DGR) |  | BRP_RNC1_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1049 | BRP SWEENY (DGR) |  | SWEENY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1050 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1051 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1052 | BYRD RANCH STORAGE |  | BYRDR_ES_BESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 50.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1053 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1054 | CATARINA BESS (DGR) |  | CATARINA_BESS | DIMMIT | STORAGE | SOUTH | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1055 | CEDARVALE BESS (DGR) |  | CEDRVALE_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1056 | CHISHOLM GRID |  | CHISMGRD_BES1 | TARRANT | STORAGE | NORTH | 2021 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1057 | COMMERCE ST ESS (DGR) |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1058 | COYOTE SPRINGS BESS (DGR) |  | COYOTSPR_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1059 | CROSSETT POWER U1 |  | CROSSETT_BES1 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1060 | CROSSETT POWER U2 |  | CROSSETT_BES2 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1061 | DECORDOVA BESS U1 |  | DCSES_BES1 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
1062 | DECORDOVA BESS U2 |  | DCSES_BES2 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
1063 | DECORDOVA BESS U3 |  | DCSES_BES3 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
1064 | DECORDOVA BESS U4 |  | DCSES_BES4 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
1065 | ENDURANCE PARK STORAGE |  | ENDPARKS_ESS1 | SCURRY | STORAGE | WEST | 2022 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1066 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2021 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
1067 | FAULKNER BESS (DGR) |  | FAULKNER_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1068 | FLAT TOP BATTERY (DGR) |  | FLAT_TOP_BESS1 | REEVES | STORAGE | WEST | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1069 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2021 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1070 | FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | REEVES | STORAGE | WEST | 2022 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1071 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 102.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1072 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2020 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
1073 | HOLCOMB BESS (DGR) |  | HOLCOMB_BESS | LA SALLE | STORAGE | SOUTH | 2023 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1074 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1075 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.25 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
1076 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
1077 | LILY STORAGE |  | LILY_BESS1 | KAUFMAN | STORAGE | NORTH | 2021 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7
1078 | LONESTAR BESS (DGR) |  | LONESTAR_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1079 | MADERO GRID U1 |  | MADERO_UNIT1 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1080 | MADERO GRID U2 (IGNACIO GRID) |  | MADERO_UNIT2 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1081 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
1082 | NOBLE STORAGE U1 |  | NOBLESLR_BESS1 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
1083 | NOBLE STORAGE U2 |  | NOBLESLR_BESS2 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
1084 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 36 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
1085 | NORTH COLUMBIA (ROUGHNECK STORAGE) |  | NCO_ESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 51.75 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1086 | NORTH FORK |  | NF_BRP_BES1 | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
1087 | PORT LAVACA BATTERY (DGR) |  | PRTLAVS_BESS1 | CALHOUN | STORAGE | COASTAL | 2020 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1088 | PROSPECT STORAGE (DGR) |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1089 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1090 | RABBIT HILL ENERGY STORAGE PROJECT (DGR) |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1091 | RATTLESNAKE BESS (DGR) |  | RTLSNAKE_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1092 | REPUBLIC ROAD STORAGE |  | RPUBRDS_ESS1 | ROBERTSON | STORAGE | NORTH | 2022 | 51.75 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1093 | SADDLEBACK BESS (DGR) |  | SADLBACK_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1094 | SARAGOSA BESS (DGR) |  | SGSA_BESS1 | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1095 | SCREWBEAN BESS (DGR) |  | SBEAN_BESS | CULBERSON | STORAGE | WEST | 2023 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1096 | SILICON HILL STORAGE U1 |  | SLCNHLS_ESS1 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1097 | SILICON HILL STORAGE U2 |  | SLCNHLS_ESS2 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1098 | SNYDER (DGR) |  | SNY_BESS_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1099 | SWEETWATER BESS (DGR) |  | SWT_BESS_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1100 | SWOOSE BATTERY (PYOTE) (DGR) |  | SWOOSE1_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1101 | SWOOSE II |  | SWOOSEII_BESS1 | WARD | STORAGE | WEST | 2022 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1102 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
1103 | TOYAH POWER STATION (DGR) |  | TOYAH_BESS | REEVES | STORAGE | WEST | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1104 | TRIPLE BUTTE (DGR) |  | TRIPBUT1_BELU1 | PECOS | STORAGE | WEST | 2021 | 9.18 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
1105 | WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1106 | WORSHAM BATTERY (DGR) |  | WORSHAM_BESS1 | REEVES | STORAGE | WEST | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1107 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
1108 | Operational Capacity Total (Storage) | [6 empty] | 2364.46 | 2335.1 | 2335.1 | 2335.1 | 2335.1 | 2335.1 | 2335.1 | 2335.1 | 2335.1 | 2335.1 | 2335.1
1109 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1110
1111 | Operational Resources (Storage) - Synchronized but not Approved for Commercial Operations
1112 | ANCHOR BESS U1 | 21INR0474 | ANCHOR_BESS1 | CALLAHAN | STORAGE | WEST | 2023 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2
1113 | ANCHOR BESS U2 | 21INR0474 | ANCHOR_BESS2 | CALLAHAN | STORAGE | WEST | 2023 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
1114 | BLUE JAY BESS | 23INR0019 | BLUEJAY_BESS1 | GRIMES | STORAGE | NORTH | 2023 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1115 | GOMEZ BESS (DGR) | 23INR0519 | GOMZ_BESS | REEVES | STORAGE | WEST | 2023 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1116 | HIGH LONESOME BESS | 20INR0280 | HI_LONEB_BESS1 | CROCKETT | STORAGE | WEST | 2023 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1117 | OLNEY BESS (DGR) | 22INR0603 | OLNEYTN_BESS | YOUNG | STORAGE | WEST | 2023 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1118 | PYRON BESS 2A | 20INR0268 | PYR_ESS2A | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
1119 | PYRON BESS 2B | 20INR0268 | PYR_ESS2B | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
1120 | QUEEN BESS | 20INR0281 | QUEEN_BA_BESS1 | UPTON | STORAGE | WEST | 2023 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1121 | RIVER VALLEY STORAGE U1 | 20INR0290 | RVRVLYS_ESS1 | WILLIAMSON | STORAGE | SOUTH | 2023 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1122 | RIVER VALLEY STORAGE U2 | 20INR0293 | RVRVLYS_ESS2 | WILLIAMSON | STORAGE | SOUTH | 2023 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1123 | ROSELAND STORAGE | 22INR0280 | ROSELAND_BESS1 | FALLS | STORAGE | NORTH | 2023 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1124 | SP TX-12B BESS | 21INR0357 | SPTX12B_BES1 | UPTON | STORAGE | WEST | 2023 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7 | 22.7
1125 | TURQUOISE STORAGE | 22INR0509 | TURQBESS_BESS1 | HUNT | STORAGE | NORTH | 2023 | 196.2 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
1126 | VORTEX BESS | 21INR0473 | VORTEX_BESS1 | THROCKMORTON | STORAGE | WEST | 2023 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8
1127 | WOLF TANK STORAGE | 22INR0551 | WFTANK_ESS1 | WEBB | STORAGE | SOUTH | 2023 | 150.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
1128 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Storage) | [6 empty] | 921.1 | 906 | 906 | 906 | 906 | 906 | 906 | 906 | 906 | 906 | 906
1129 | Storage Peak Average Capacity Percentage |  | STORAGE_SYNC_PEAK_PCT | % |  |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1130
1131 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1132
1133 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1134
1135 | Non-Synchronous Tie Resources
1136 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
1137 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
1138 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1139 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1140 | Non-Synchronous Ties Total | [6 empty] | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220
1141 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 100 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
1142
1143 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
1144 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2023 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1145 | BEACHWOOD II POWER STATION (U7-U8) | 23INR0506 |  | BRAZORIA | GAS-GT | COASTAL | 2024 | 121 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6
1146 | BROTMAN POWER STATION (U1 - U2) | 23INR0613 |  | BRAZORIA | GAS-GT | COASTAL | 2024 | 121 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6
1147 | BROTMAN II POWER STATION (U7- U8) | 23INR0551 |  | BRAZORIA | GAS-GT | COASTAL | 2023 | 121 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6 | 99.6
1148 | FRONTERA ENERGY CENTER | 23INR0472 |  | HIDALGO | GAS-CC | SOUTH | 2023 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5 | 538.5
1149 | MIRAGE CTG 1 | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2023 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
1150 | REMY JADE POWER STATION | 23INR0339 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408
1151 | REMY JADE II POWER STATION | 24INR0382 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7
1152 | SKY SEALY | 21INR0500 |  | AUSTIN | GAS-IC | SOUTH | 2025 | 149.4 | 0 | 149.4 | 149.4 | 149.4 | 149.4 | 149.4 | 149.4 | 149.4 | 149.4 | 149.4
1153 | TECO GTG2 | 23INR0408 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1154 | Planned Thermal Resources Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 1683.6 | 1470 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4 | 1619.4
1155
1156 | Planned Wind Resources with Executed SGIA
1157 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2024 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
1158 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2023 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1 | 309.1
1159 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2024 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7 | 165.7
1160 | CRAWFISH | 19INR0177 |  | WHARTON | WIND-O | SOUTH | 2023 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2
1161 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2023 | 531 | 531 | 531 | 531 | 531 | 531 | 531 | 531 | 531 | 531 | 531
1162 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2024 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
1163 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2024 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
1164 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2025 | 351 | 0 | 351 | 351 | 351 | 351 | 351 | 351 | 351 | 351 | 351
1165 | MONTE ALTO 2 WIND | 19INR0023 |  | WILLACY | WIND-C | COASTAL | 2024 | 272.8 | 0 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8 | 272.8
1166 | MONTE ALTO I WIND | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2024 | 189 | 0 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189
1167 | MONTGOMERY RANCH WIND | 20INR0040 |  | FOARD | WIND-O | WEST | 2023 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2
1168 | PIONEER DJ WIND | 23INR0387 |  | MIDLAND | WIND-O | WEST | 2024 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3 | 140.3
1169 | RAY GULF WIND | 22INR0517 |  | WHARTON | WIND-O | SOUTH | 2023 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207
1170 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2023 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128
1171 | SHAMROCK | 22INR0502 |  | CROCKETT | WIND-O | WEST | 2024 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9 | 223.9
1172 | SHEEP CREEK WIND | 21INR0325 |  | CALLAHAN | WIND-O | WEST | 2023 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
1173 | SIETE | 20INR0047 |  | WEBB | WIND-O | SOUTH | 2024 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1 | 375.1
1174 | Planned Capacity Total (Wind) | [6 empty] | 4106.3 | 3293.5 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3 | 4106.3
1175
1176 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 461.8 | 0 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8 | 461.8
1177 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 100 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
1178
1179 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7 | 696.7
1180 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 100 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
1181
1182 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 2947.8 | 2596.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8 | 2947.8
1183 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 100 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
1184
1185 | Planned Solar Resources with Executed SGIA
1186 | 7V SOLAR | 21INR0351 |  | FAYETTE | SOLAR | SOUTH | 2024 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6 | 240.6
1187 | ADAMSTOWN SOLAR | 21INR0210 |  | WICHITA | SOLAR | WEST | 2025 | 254.1 | 0 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1 | 254.1
1188 | ALILA SOLAR | 23INR0093 |  | SAN PATRICIO | SOLAR | COASTAL | 2024 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5 | 256.5
1189 | AMSTERDAM SOLAR | 21INR0256 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9 | 509.9
1190 | ANDROMEDA SOLAR | 22INR0412 |  | SCURRY | SOLAR | WEST | 2023 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
1191 | ANGELO SOLAR | 19INR0203 |  | TOM GREEN | SOLAR | WEST | 2024 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4 | 195.4
1192 | ANGUS SOLAR | 20INR0035 |  | BOSQUE | SOLAR | NORTH | 2024 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
1193 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2024 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
1194 | ARROYO SOLAR | 20INR0086 |  | CAMERON | SOLAR | COASTAL | 2024 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
1195 | ASH CREEK SOLAR | 21INR0379 |  | HILL | SOLAR | NORTH | 2024 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9 | 408.9
1196 | BAKER BRANCH SOLAR | 23INR0026 |  | LAMAR | SOLAR | NORTH | 2024 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4 | 469.4
1197 | BIG ELM SOLAR | 21INR0353 |  | BELL | SOLAR | NORTH | 2024 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.2
1198 | BLUE SKY SOL | 22INR0455 |  | CROCKETT | SOLAR | WEST | 2024 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
1199 | BRASS FORK SOLAR | 22INR0270 |  | HASKELL | SOLAR | WEST | 2025 | 304.8 | 0 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8
1200 | BRIGHT ARROW SOLAR | 22INR0242 |  | HOPKINS | SOLAR | NORTH | 2023 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1201 | BUCKEYE CORPUS FUELS SOLAR | 22INR0397 |  | NUECES | SOLAR | COASTAL | 2025 | 57.6 | 0 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6
1202 | CACHENA SOLAR | 23INR0027 |  | WILSON | SOLAR | SOUTH | 2025 | 600 | 0 | 0 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
1203 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2025 | 223.2 | 0 | 0 | 223.2 | 223.2 | 223.2 | 223.2 | 223.2 | 223.2 | 223.2 | 223.2
1204 | CASTRO SOLAR | 20INR0050 |  | CASTRO | SOLAR | PANHANDLE | 2025 | 222.9 | 0 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9
1205 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2025 | 406.8 | 0 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8
1206 | CLUTCH CITY SOLAR | 22INR0279 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 204.2 | 0 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2
1207 | COMPADRE SOLAR | 24INR0023 |  | HILL | SOLAR | NORTH | 2024 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3 | 405.3
1208 | CORAL SOLAR | 22INR0295 |  | FALLS | SOLAR | NORTH | 2023 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6 | 151.6
1209 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2025 | 202.6 | 0 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
1210 | COTTONWOOD BAYOU SOLAR I | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4 | 351.4
1211 | CRADLE SOLAR | 23INR0150 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 225 | 0 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
1212 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2025 | 217.6 | 0 | 0 | 217.6 | 217.6 | 217.6 | 217.6 | 217.6 | 217.6 | 217.6 | 217.6
1213 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2025 | 188.8 | 0 | 0 | 188.8 | 188.8 | 188.8 | 188.8 | 188.8 | 188.8 | 188.8 | 188.8
1214 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2023 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8 | 602.8
1215 | DAWN SOLAR | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2024 | 515.7 | 0 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7 | 515.7
1216 | DELILAH SOLAR 1 | 22INR0202 |  | LAMAR | SOLAR | NORTH | 2024 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1217 | DELILAH SOLAR 2 | 22INR0203 |  | LAMAR | SOLAR | NORTH | 2024 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6 | 317.6
1218 | DELILAH SOLAR 3 | 23INR0042 |  | LAMAR | SOLAR | NORTH | 2023 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1219 | DELILAH SOLAR 4 | 23INR0060 |  | LAMAR | SOLAR | NORTH | 2023 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
1220 | DESERT VINE SOLAR | 22INR0307 |  | ZAPATA | SOLAR | SOUTH | 2024 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3
1221 | DILEO SOLAR | 22INR0359 |  | BOSQUE | SOLAR | NORTH | 2023 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
1222 | DONEGAL SOLAR | 23INR0089 |  | DICKENS | SOLAR | PANHANDLE | 2024 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2 | 204.2
1223 | DORI BQ SOLAR | 23INR0040 |  | HARRIS | SOLAR | HOUSTON | 2024 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
1224 | DR SOLAR | 22INR0454 |  | CULBERSON | SOLAR | WEST | 2024 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
1225 | EASTBELL MILAM SOLAR | 21INR0203 |  | MILAM | SOLAR | SOUTH | 2023 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9 | 244.9
1226 | EIFFEL SOLAR | 22INR0223 |  | LAMAR | SOLAR | NORTH | 2023 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241
1227 | ELIZA SOLAR | 21INR0368 |  | KAUFMAN | SOLAR | NORTH | 2024 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9
1228 | ELLIS SOLAR | 21INR0493 |  | ELLIS | SOLAR | NORTH | 2023 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
1229 | EQUINOX SOLAR 1 | 21INR0226 |  | STARR | SOLAR | SOUTH | 2026 | 200 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1230 | ESTONIAN SOLAR FARM | 22INR0335 |  | DELTA | SOLAR | NORTH | 2024 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5
1231 | FAGUS SOLAR PARK (MISAE SOLAR II) | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2024 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5 | 519.5
1232 | FENCE POST SOLAR | 22INR0404 |  | NAVARRO | SOLAR | NORTH | 2024 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236
1233 | FIVE WELLS SOLAR | 24INR0015 |  | BELL | SOLAR | NORTH | 2023 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8 | 322.8
1234 | FRYE SOLAR | 20INR0080 |  | SWISHER | SOLAR | PANHANDLE | 2024 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1 | 514.1
1235 | GALACTIC SOLAR | 23INR0144 |  | GRAYSON | SOLAR | NORTH | 2024 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2
1236 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2023 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9 | 113.9
1237 | GARCITAS CREEK SOLAR | 23INR0223 |  | JACKSON | SOLAR | SOUTH | 2024 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9 | 201.9
1238 | GP SOLAR | 23INR0045 |  | VAN ZANDT | SOLAR | NORTH | 2024 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
1239 | GRANDSLAM SOLAR | 21INR0391 |  | ATASCOSA | SOLAR | SOUTH | 2024 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
1240 | GRANSOLAR TEXAS ONE | 22INR0511 |  | MILAM | SOLAR | SOUTH | 2024 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1241 | GREATER BRYANT G SOLAR | 23INR0300 |  | MIDLAND | SOLAR | WEST | 2024 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6
1242 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2024 | 413.6 | 0 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6 | 413.6
1243 | GREYHOUND SOLAR | 21INR0268 |  | ECTOR | SOLAR | WEST | 2025 | 608.7 | 0 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7 | 608.7
1244 | GRIMES COUNTY SOLAR | 23INR0160 |  | GRIMES | SOLAR | NORTH | 2025 | 210 | 0 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
1245 | GULF STAR SOLAR SLF (G-STAR SOLAR) | 23INR0111 |  | WHARTON | SOLAR | SOUTH | 2024 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6 | 451.6
1246 | HALO SOLAR | 21INR0304 |  | BELL | SOLAR | NORTH | 2023 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254
1247 | HAYHURST TEXAS SOLAR | 22INR0363 |  | CULBERSON | SOLAR | WEST | 2023 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8
1248 | HOPKINS SOLAR | 20INR0210 |  | HOPKINS | SOLAR | NORTH | 2023 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1 | 253.1
1249 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2023 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5
1250 | HORNET SOLAR | 23INR0021 |  | SWISHER | SOLAR | PANHANDLE | 2024 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 611
1251 | HOWLE SOLAR | 20INR0075 |  | ELLIS | SOLAR | NORTH | 2024 | 60 | 0 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1252 | HOYTE SOLAR | 23INR0235 |  | MILAM | SOLAR | SOUTH | 2024 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
1253 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2024 | 125 | 0 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1254 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2025 | 202.4 | 0 | 0 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4
1255 | JACKALOPE SOLAR | 23INR0180 |  | SAN PATRICIO | SOLAR | COASTAL | 2024 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4 | 156.4
1256 | JUNGMANN SOLAR | 22INR0356 |  | MILAM | SOLAR | SOUTH | 2024 | 40 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
1257 | LAVACA BAY SOLAR | 23INR0084 |  | MATAGORDA | SOLAR | COASTAL | 2024 | 243.5 | 0 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5 | 243.5
1258 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3
1259 | LUNIS CREEK SOLAR 1 | 21INR0344 |  | JACKSON | SOLAR | SOUTH | 2024 | 617.1 | 0 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1 | 617.1
1260 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2024 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9
1261 | MARKUM SOLAR | 20INR0230 |  | MCLENNAN | SOLAR | NORTH | 2024 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5
1262 | MATAGORDA SOLAR | 22INR0342 |  | MATAGORDA | SOLAR | COASTAL | 2023 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101
1263 | MERCURY I SOLAR | 21INR0257 |  | HILL | SOLAR | NORTH | 2024 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5 | 203.5
1264 | MERCURY II SOLAR | 23INR0153 |  | HILL | SOLAR | NORTH | 2024 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2
1265 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2024 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
1266 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2025 | 365.7 | 0 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7 | 365.7
1267 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2025 | 204 | 0 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
1268 | NEPTUNE SOLAR | 21INR0499 |  | JACKSON | SOLAR | SOUTH | 2023 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3
1269 | NORIA SOLAR DCC | 23INR0061 |  | NUECES | SOLAR | COASTAL | 2024 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
1270 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2024 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
1271 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2025 | 225.7 | 0 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7
1272 | ORIANA SOLAR | 24INR0093 |  | VICTORIA | SOLAR | SOUTH | 2024 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3
1273 | OUTPOST SOLAR | 23INR0007 |  | WEBB | SOLAR | SOUTH | 2024 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7 | 513.7
1274 | OYSTERCATCHER SOLAR | 21INR0362 |  | ELLIS | SOLAR | NORTH | 2024 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
1275 | PEREGRINE SOLAR | 22INR0283 |  | GOLIAD | SOLAR | SOUTH | 2024 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4 | 303.4
1276 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2024 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305
1277 | PINK SOLAR | 22INR0281 |  | HUNT | SOLAR | NORTH | 2023 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
1278 | PITTS DUDIK SOLAR | 20INR0074 |  | HILL | SOLAR | NORTH | 2023 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6
1279 | PORTER SOLAR | 21INR0458 |  | DENTON | SOLAR | NORTH | 2024 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245
1280 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2024 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260
1281 | REDONDA SOLAR | 23INR0162 |  | ZAPATA | SOLAR | SOUTH | 2024 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2 | 253.2
1282 | RED-TAILED HAWK SOLAR | 21INR0389 |  | WHARTON | SOLAR | SOUTH | 2024 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4 | 353.4
1283 | ROCINANTE SOLAR | 23INR0231 |  | GONZALES | SOLAR | SOUTH | 2024 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
1284 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2025 | 200 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1285 | ROWLAND SOLAR II | 22INR0482 |  | FORT BEND | SOLAR | HOUSTON | 2024 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8 | 202.8
1286 | SAMSON SOLAR 2 | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2024 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
1287 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2024 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5
1288 | SCHOOLHOUSE SOLAR | 22INR0211 |  | LEE | SOLAR | SOUTH | 2025 | 150.8 | 0 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8
1289 | SECOND DIVISION SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
1290 | SHAULA I SOLAR | 22INR0251 |  | DEWITT | SOLAR | SOUTH | 2025 | 205.2 | 0 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2
1291 | SHAULA II SOLAR | 22INR0267 |  | DEWITT | SOLAR | SOUTH | 2026 | 205.2 | 0 | 0 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2
1292 | SIGNAL SOLAR | 20INR0208 |  | HUNT | SOLAR | NORTH | 2024 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8
1293 | SODA LAKE SOLAR 1 SLF | 20INR0143 |  | CRANE | SOLAR | WEST | 2024 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
1294 | SODA LAKE SOLAR 2 SLF | 23INR0080 |  | CRANE | SOLAR | WEST | 2023 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
1295 | SP JAGUAR SOLAR | 24INR0038 |  | MCLENNAN | SOLAR | NORTH | 2024 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1296 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2025 | 609.7 | 0 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7 | 609.7
1297 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2023 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
1298 | STAMPEDE SOLAR | 22INR0409 |  | HOPKINS | SOLAR | NORTH | 2023 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
1299 | STARLING SOLAR | 23INR0035 |  | GONZALES | SOLAR | SOUTH | 2024 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
1300 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2024 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7 | 136.7
1301 | SUNRAY | 21INR0395 |  | UVALDE | SOLAR | SOUTH | 2024 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1
1302 | TALITHA SOLAR | 21INR0393 |  | JIM WELLS | SOLAR | SOUTH | 2024 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131
1303 | TANGLEWOOD SOLAR | 23INR0054 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 257 | 0 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
1304 | TEXANA SOLAR | 18INR0058 |  | WHARTON | SOLAR | SOUTH | 2024 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
1305 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2023 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5 | 253.5
1306 | TEXAS SOLAR NOVA 2 | 20INR0269 |  | KENT | SOLAR | WEST | 2023 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1
1307 | TIERRA BONITA SOLAR | 21INR0424 |  | PECOS | SOLAR | WEST | 2024 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7 | 309.7
1308 | TRES BAHIAS SOLAR | 20INR0266 |  | CALHOUN | SOLAR | COASTAL | 2023 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 198.4
1309 | TROJAN SOLAR | 23INR0296 |  | COOKE | SOLAR | NORTH | 2024 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1 | 206.1
1310 | TULSITA SOLAR | 21INR0223 |  | GOLIAD | SOLAR | SOUTH | 2024 | 261 | 0 | 261 | 261 | 261 | 261 | 261 | 261 | 261 | 261 | 261
1311 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2024 | 90 | 0 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
1312 | ULYSSES SOLAR | 21INR0253 |  | COKE | SOLAR | WEST | 2024 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
1313 | UMBRA (STOCKYARD) SOLAR | 23INR0155 |  | FRANKLIN | SOLAR | NORTH | 2024 | 210 | 0 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
1314 | XE MURAT SOLAR | 22INR0354 |  | HARRIS | SOLAR | HOUSTON | 2024 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4
1315 | ZIER SOLAR | 21INR0019 |  | KINNEY | SOLAR | SOUTH | 2023 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
1316 | Planned Capacity Total (Solar) | [6 empty] | 30232.7 | 20854.8 | 28395.5 | 30032.7 | 30232.7 | 30232.7 | 30232.7 | 30232.7 | 30232.7 | 30232.7 | 30232.7
1317 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 100 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
1318
1319 | Planned Storage Resources with Executed SGIA
1320 | ADAMSTOWN STORAGE | 21INR0209 |  | WICHITA | STORAGE | WEST | 2025 | 116.9 | 0 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9 | 116.9
1321 | AEP_N_ALAMO_LD02(SMT ALAMO) | 23INR0477 |  | HIDALGO | STORAGE | SOUTH | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1322 | AL PASTOR BESS | 24INR0273 |  | DAWSON | STORAGE | WEST | 2024 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
1323 | AMSTERDAM STORAGE | 22INR0417 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1
1324 | ANEMOI ENERGY STORAGE | 23INR0369 |  | HIDALGO | STORAGE | SOUTH | 2023 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205
1325 | ARROYO STORAGE SLF | 24INR0306 |  | CAMERON | STORAGE | COASTAL | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1326 | BIG STAR STORAGE | 21INR0469 |  | BASTROP | STORAGE | SOUTH | 2023 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
1327 | BOCO BESS | 23INR0470 |  | BORDEN | STORAGE | WEST | 2024 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3
1328 | BORDERTOWN BESS | 23INR0354 |  | STARR | STORAGE | SOUTH | 2025 | 106.2 | 0 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2
1329 | BRAZOS BEND BESS | 23INR0363 |  | FORT BEND | STORAGE | HOUSTON | 2024 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
1330 | BRIGHT ARROW STORAGE | 22INR0302 |  | HOPKINS | STORAGE | NORTH | 2023 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6 | 103.6
1331 | BRP ANTLIA BESS | 22INR0349 |  | VAL VERDE | STORAGE | WEST | 2023 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9
1332 | BRP AVILA BESS | 23INR0287 |  | PECOS | STORAGE | WEST | 2024 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9
1333 | BRP CACHI BESS | 22INR0388 |  | GUADALUPE | STORAGE | SOUTH | 2024 | 202.5 | 0 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5 | 202.5
1334 | BRP CARINA BESS | 22INR0353 |  | NUECES | STORAGE | COASTAL | 2024 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9 | 151.9
1335 | BRP DICKENS BESS | 22INR0325 |  | DICKENS | STORAGE | PANHANDLE | 2023 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3
1336 | BRP HYDRA BESS | 22INR0372 |  | PECOS | STORAGE | WEST | 2023 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3 | 202.3
1337 | BRP LIBRA BESS | 22INR0366 |  | GUADALUPE | STORAGE | SOUTH | 2023 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2 | 206.2
1338 | BRP PALEO BESS | 22INR0322 |  | HALE | STORAGE | PANHANDLE | 2023 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4 | 202.4
1339 | BRP PAVO BESS | 22INR0384 |  | PECOS | STORAGE | WEST | 2023 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9 | 176.9
1340 | BRP TORTOLAS BESS | 23INR0072 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7
1341 | BRP ZEYA BESS | 23INR0290 |  | GALVESTON | STORAGE | HOUSTON | 2024 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8 | 256.8
1342 | CALLISTO I ENERGY CENTER | 22INR0490 |  | HARRIS | STORAGE | HOUSTON | 2024 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
1343 | CITADEL BESS | 24INR0147 |  | HARRIS | STORAGE | HOUSTON | 2024 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3 | 201.3
1344 | CONNOLLY STORAGE | 23INR0403 |  | WISE | STORAGE | NORTH | 2024 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
1345 | CORAL STORAGE | 23INR0124 |  | FALLS | STORAGE | NORTH | 2023 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
1346 | COTTONWOOD BAYOU STORAGE | 21INR0443 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8 | 150.8
1347 | DAMON STORAGE | 23INR0523 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
1348 | DANISH FIELDS STORAGE | 21INR0450 |  | WHARTON | STORAGE | SOUTH | 2023 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4 | 152.4
1349 | DIBOLL BESS (DGR) | 23INR0522 |  | ANGELINA | STORAGE | NORTH | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1350 | EBONY ENERGY STORAGE | 23INR0154 |  | COMAL | STORAGE | SOUTH | 2024 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205
1351 | ELIZA STORAGE | 22INR0260 |  | KAUFMAN | STORAGE | NORTH | 2024 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
1352 | ESTONIAN ENERGY STORAGE | 22INR0336 |  | DELTA | STORAGE | NORTH | 2024 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
1353 | EVAL STORAGE | 22INR0401 |  | CAMERON | STORAGE | COASTAL | 2024 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
1354 | FENCE POST BESS | 22INR0405 |  | NAVARRO | STORAGE | NORTH | 2023 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
1355 | FERDINAND GRID BESS | 22INR0422 |  | BEXAR | STORAGE | SOUTH | 2025 | 202.6 | 0 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
1356 | FIVE WELLS STORAGE | 23INR0159 |  | BELL | STORAGE | NORTH | 2023 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8
1357 | FORT DUNCAN BESS | 23INR0350 |  | MAVERICK | STORAGE | SOUTH | 2025 | 106.2 | 0 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2 | 106.2
1358 | GIGA TEXAS ENERGY STORAGE | 23INR0239 |  | TRAVIS | STORAGE | SOUTH | 2023 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
1359 | GREAT KISKADEE STORAGE | 23INR0166 |  | HIDALGO | STORAGE | SOUTH | 2024 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1 | 103.1
1360 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2024 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1361 | GRIZZLY RIDGE BESS (DGR) | 22INR0596 |  | HAMILTON | STORAGE | NORTH | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1362 | GUAJILLO ENERGY STORAGE | 23INR0343 |  | WEBB | STORAGE | SOUTH | 2024 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1
1363 | HOUSE MOUNTAIN 2 BATT | 22INR0485 |  | BREWSTER | STORAGE | WEST | 2023 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1364 | HUMMINGBIRD STORAGE | 22INR0327 |  | DENTON | STORAGE | NORTH | 2023 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
1365 | INERTIA BESS | 22INR0328 |  | HASKELL | STORAGE | WEST | 2023 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
1366 | INERTIA BESS 2 | 22INR0375 |  | HASKELL | STORAGE | WEST | 2025 | 100.8 | 0 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
1367 | IRON BELT ENERGY STORAGE | 25INR0208 |  | DAWSON | STORAGE | WEST | 2025 | 401.9 | 0 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9 | 401.9
1368 | JUNCTION BESS (DGR) | 23INR0521 |  | KIMBLE | STORAGE | SOUTH | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1369 | LARKSPUR ENERGY STORAGE | 23INR0340 |  | UPTON | STORAGE | WEST | 2025 | 307.5 | 0 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5
1370 | LIMOUSIN OAK STORAGE | 22INR0338 |  | GRIMES | STORAGE | NORTH | 2023 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6
1371 | MUSTANG CREEK STORAGE | 21INR0484 |  | JACKSON | STORAGE | SOUTH | 2023 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5
1372 | MYRTLE STORAGE | 21INR0442 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
1373 | NORIA STORAGE | 23INR0062 |  | NUECES | STORAGE | COASTAL | 2024 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
1374 | ORIANA BESS | 24INR0109 |  | VICTORIA | STORAGE | SOUTH | 2024 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4
1375 | PADUA GRID BESS | 22INR0368 |  | BEXAR | STORAGE | SOUTH | 2024 | 202.6 | 0 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
1376 | PLATINUM STORAGE | 22INR0554 |  | FANNIN | STORAGE | NORTH | 2024 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5 | 303.5
1377 | RAMSEY STORAGE | 21INR0505 |  | WHARTON | STORAGE | SOUTH | 2024 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4 | 510.4
1378 | RED HOLLY STORAGE | 21INR0033 |  | DAWSON | STORAGE | WEST | 2024 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1379 | ROCINANTE BESS | 23INR0232 |  | GONZALES | STORAGE | SOUTH | 2024 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
1380 | RODEO RANCH ENERGY STORAGE | 23INR0371 |  | REEVES | STORAGE | WEST | 2023 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5
1381 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2024 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
1382 | SABAL STORAGE | 22INR0398 |  | CAMERON | STORAGE | COASTAL | 2023 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4
1383 | SMT ALAMO (DGR) | 23INR0477 |  | HIDALGO | STORAGE | SOUTH | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1384 | SMT LOS FRESNOS (DGR) | 23INR0508 |  | CAMERON | STORAGE | COASTAL | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1385 | SMT MISSION (DGR) | 23INR0511 |  | CAMERON | STORAGE | COASTAL | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1386 | SMT RIO GRANDE (DGR) | 23INR0509 |  | STARR | STORAGE | SOUTH | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1387 | SMT RIO GRANDE II (DGR) | 23INR0510 |  | STARR | STORAGE | SOUTH | 2023 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1388 | SOHO BESS | 23INR0419 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3 | 206.3
1389 | SOWERS STORAGE | 22INR0552 |  | KAUFMAN | STORAGE | NORTH | 2024 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
1390 | SP JAGUAR BESS | 24INR0039 |  | MCLENNAN | STORAGE | NORTH | 2024 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
1391 | ST. GALL I ENERGY STORAGE | 22INR0524 |  | PECOS | STORAGE | WEST | 2023 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
1392 | STAMPEDE BESS | 22INR0410 |  | HOPKINS | STORAGE | NORTH | 2023 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
1393 | STOCKYARD GRID BATT | 21INR0492 |  | TARRANT | STORAGE | NORTH | 2023 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
1394 | SUN VALLEY BESS | 22INR0429 |  | HILL | STORAGE | NORTH | 2023 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4
1395 | TALITHA BESS | 23INR0331 |  | JIM WELLS | STORAGE | SOUTH | 2024 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4
1396 | TANZANITE STORAGE | 22INR0549 |  | HENDERSON | STORAGE | NORTH | 2024 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7 | 257.7
1397 | TIDWELL PRAIRIE STORAGE 1 | 21INR0517 |  | ROBERTSON | STORAGE | NORTH | 2024 | 304.8 | 0 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8 | 304.8
1398 | TIMBERWOLF BESS 2 | 22INR0495 |  | CRANE | STORAGE | WEST | 2023 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
1399 | UMBRA (STOCKYARD) BESS | 23INR0156 |  | FRANKLIN | STORAGE | NORTH | 2024 | 73 | 0 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
1400 | ZIER STORAGE | 21INR0027 |  | KINNEY | STORAGE | SOUTH | 2023 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4
1401 | SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * | [6 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
1402 | Planned Capacity Total (Storage) | [6 empty] | 10788.2 | 8663.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2 | 10788.2
1403 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1404
1405 | Inactive Planned Resources
1406 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
1407 | CHILLINGHAM SOLAR | 23INR0070 |  | BELL | SOLAR | NORTH | 2023 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4 | 359.4
1408 | CHILLINGHAM STORAGE | 23INR0079 |  | BELL | STORAGE | NORTH | 2023 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8
1409 | DONEGAL BESS | 23INR0103 |  | DICKENS | STORAGE | PANHANDLE | 2024 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3 | 101.3
1410 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2026 | 165 | 0 | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
1411 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1
1412 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1 | 250.1
1413 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
1414 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
1415 | PARLIAMENT SOLAR | 23INR0044 |  | WALLER | SOLAR | HOUSTON | 2024 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7 | 482.7
1416 | PLEASANTON BESS (DGR) | 23INR0520 |  | ATASCOSA | STORAGE | SOUTH | 2023 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
1417 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2025 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
1418 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2024 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
1419 | Inactive Planned Capacity Total | [6 empty] | 2364.8 | 1999.8 | 1999.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8 | 2364.8
1420
1421 | Seasonal Mothballed Resources
1422 | MOUNTAIN CREEK STG 8 (AS OF 3/1/2023, AVAILABLE 6/1 THROUGH 9/30) |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568
1423 | POWERLANE PLANT STG 1 (AS OF 10/1/2022, AVAILABLE 6/1 THROUGH 9/30) |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 18.75 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
1424 | SPENCER STG U4 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 61 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
1425 | SPENCER STG U5 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 65 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
1426 | Total Seasonal Mothballed Capacity | [6 empty] | 712.75 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5 | 703.5
1427
1428 | Mothballed Resources
1429 | RAY OLINGER STG 1 (AS OF 4/5/22) |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
1430 | CALENERGY-FALCON SEABOARD STG 3 (AS OF 7/8/22, DUE TO FORCED OUTAGE) |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62
1431 | Total Mothballed Capacity | [6 empty] | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
1432
1433 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
1434 | J T DEELY U1 (INDEFINITE MOTHBALL AS OF 12/31/2018, RETIRING ON 7/7/23) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 415 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430
1435 | J T DEELY U2 (INDEFINITE MOTHBALL AS OF 12/31/2018, RETIRING ON 7/7/23) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 415 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
1436 | Total Retiring Capacity | [6 empty] | 830 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide Ancillary Services rather than sustained capacity available to meet system peak loads.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Reources Services (RIOO-RS) system.
Note on J443: Extended outages: GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE (3.6 MW) and 2.4 MW of the 4.8 MW GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP Hydro unit.

## Fuel Type Capacity Mix
Summer Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacity contribution of the wind resources is included at 60% for Coastal counties, 30% for Panhandle counties, and 21% for all other counties, while the solar capacity contribution is 79%. Private Use Network, and Hydro are included based on the three-year average historical capability for each Summer Season's 20 peak load hours. Non-Synchronous Tie resources import forecast is based on flows seen during Energy Emergency Alert (EEA) periods in the most recent summer of occurrence. Non-Synchronous Tie resources are categorized as Other. Mothballed resource capacity is excluded except for Available Mothball Capacity based on a Seasonal Availability Schedule or Owner's reported Return Probability. Private Use Network generator capacity is categorized as gas.
In MW
Fuel_Type | Capacity_Pct | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
Biomass | 100% | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8
Coal | 100% | 13567.6 | 13567.6 | 13567.6 | 13567.6 | 13567.6 | 13567.6 | 13567.6 | 13567.6 | 13567.6 | 13567.6
Gas | 100% | 54093.225 | 54325.925 | 54325.925 | 54470.925 | 54470.925 | 54470.925 | 54470.925 | 54470.925 | 54470.925 | 54470.925
Nuclear | 100% | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2 | 4973.2
Other | 69.67% | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974 | 849.974
Hydro | 84% | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044 | 475.4044
Wind-C | 60% | 2949.66 | 3228.54 | 3228.54 | 3228.54 | 3228.54 | 3228.54 | 3228.54 | 3228.54 | 3228.54 | 3228.54
Wind-P | 30% | 1481.61 | 1531.32 | 1531.32 | 1531.32 | 1531.32 | 1531.32 | 1531.32 | 1531.32 | 1531.32 | 1531.32
Wind-O | 21% | 6229.209 | 6465.69 | 6465.69 | 6465.69 | 6465.69 | 6465.69 | 6465.69 | 6465.69 | 6465.69 | 6465.69
Solar | 79% | 24424.351 | 34012.897 | 35989.635 | 36147.635 | 36147.635 | 36147.635 | 36147.635 | 36147.635 | 36147.635 | 36147.635
Storage | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 109207.0334 | 119593.3504 | 121570.0884 | 121873.0884 | 121873.0884 | 121873.0884 | 121873.0884 | 121873.0884 | 121873.0884 | 121873.0884
In Percentages
Fuel_Type |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
Biomass |  | 0.1491% | 0.1361% | 0.1339% | 0.1336% | 0.1336% | 0.1336% | 0.1336% | 0.1336% | 0.1336% | 0.1336%
Coal |  | 12.42% | 11.34% | 11.16% | 11.13% | 11.13% | 11.13% | 11.13% | 11.13% | 11.13% | 11.13%
Natural Gas |  | 49.53% | 45.43% | 44.69% | 44.69% | 44.69% | 44.69% | 44.69% | 44.69% | 44.69% | 44.69%
Nuclear |  | 4.554% | 4.158% | 4.091% | 4.081% | 4.081% | 4.081% | 4.081% | 4.081% | 4.081% | 4.081%
Other |  | 0.7783% | 0.7107% | 0.6992% | 0.6974% | 0.6974% | 0.6974% | 0.6974% | 0.6974% | 0.6974% | 0.6974%
Hydro |  | 0.4353% | 0.3975% | 0.3911% | 0.3901% | 0.3901% | 0.3901% | 0.3901% | 0.3901% | 0.3901% | 0.3901%
Wind-C |  | 2.701% | 2.7% | 2.656% | 2.649% | 2.649% | 2.649% | 2.649% | 2.649% | 2.649% | 2.649%
Wind-P |  | 1.357% | 1.28% | 1.26% | 1.256% | 1.256% | 1.256% | 1.256% | 1.256% | 1.256% | 1.256%
Wind-O |  | 5.704% | 5.406% | 5.318% | 5.305% | 5.305% | 5.305% | 5.305% | 5.305% | 5.305% | 5.305%
Solar |  | 22.37% | 28.44% | 29.6% | 29.66% | 29.66% | 29.66% | 29.66% | 29.66% | 29.66% | 29.66%
Storage | bar: 2024 to 2033
Total |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Winter Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacity contribution of the wind resources is included at 56% for Coastal counties, 37% for Panhandle counties, and 26% for all other counties, while the solar capacity contribution is 14%. Private Use Network, and Hydro are included based on the three-year average historical capability for each Winter Season's 20 peak load hours. Non-Synchronous Tie resources import forecast is based on flows seen during Energy Emergency Alert (EEA) periods in the most recent winter of occurrence. Non-Synchronous Tie resources are categorized as Other. Mothballed resource capacity is excluded except for Available Mothball Capacity based on a Seasonal Availability Schedule or Owner's reported Return Probability. Private Use Network generator capacity is categorized as gas.
In MW
Fuel_Type | Capacity_Pct | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032/2033 | 2033/2034
Biomass | 100% | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8
Coal | 100% | 13629.6 | 13629.6 | 13629.6 | 13629.6 | 13629.6 | 13629.6 | 13629.6 | 13629.6 | 13629.6 | 13629.6
Gas | 100% | 58529.425 | 58678.825 | 58678.825 | 58858.825 | 58858.825 | 58858.825 | 58858.825 | 58858.825 | 58858.825 | 58858.825
Nuclear | 100% | 5153.2 | 5153.2 | 5153.2 | 5153.2 | 5153.2 | 5153.2 | 5153.2 | 5153.2 | 5153.2 | 5153.2
Other | 59% | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8
Hydro | 72.66% | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543 | 414.9543
Wind-C | 56% | 2750.776 | 3009.384 | 3009.384 | 3009.384 | 3009.384 | 3009.384 | 3009.384 | 3009.384 | 3009.384 | 3009.384
Wind-P | 37% | 1888.628 | 1888.628 | 1888.628 | 1888.628 | 1888.628 | 1888.628 | 1888.628 | 1888.628 | 1888.628 | 1888.628
Wind-O | 26% | 7913.88 | 8005.14 | 8005.14 | 8005.14 | 8005.14 | 8005.14 | 8005.14 | 8005.14 | 8005.14 | 8005.14
Solar | 14% | 5088.664 | 6144.362 | 6373.57 | 6401.57 | 6401.57 | 6401.57 | 6401.57 | 6401.57 | 6401.57 | 6401.57
Storage | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 96251.7273 | 97806.6933 | 98035.9013 | 98243.9013 | 98243.9013 | 98243.9013 | 98243.9013 | 98243.9013 | 98243.9013 | 98243.9013
In Percentages
Fuel_Type |  | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032/2033 | 2033/2034
Biomass |  | 0.1691% | 0.1665% | 0.1661% | 0.1657% | 0.1657% | 0.1657% | 0.1657% | 0.1657% | 0.1657% | 0.1657%
Coal |  | 14.16% | 13.94% | 13.9% | 13.87% | 13.87% | 13.87% | 13.87% | 13.87% | 13.87% | 13.87%
Natural Gas |  | 60.81% | 59.99% | 59.85% | 59.91% | 59.91% | 59.91% | 59.91% | 59.91% | 59.91% | 59.91%
Nuclear |  | 5.354% | 5.269% | 5.256% | 5.245% | 5.245% | 5.245% | 5.245% | 5.245% | 5.245% | 5.245%
Other |  | 0.7478% | 0.7359% | 0.7342% | 0.7327% | 0.7327% | 0.7327% | 0.7327% | 0.7327% | 0.7327% | 0.7327%
Hydro |  | 0.4311% | 0.4243% | 0.4233% | 0.4224% | 0.4224% | 0.4224% | 0.4224% | 0.4224% | 0.4224% | 0.4224%
Wind-C |  | 2.858% | 3.077% | 3.07% | 3.063% | 3.063% | 3.063% | 3.063% | 3.063% | 3.063% | 3.063%
Wind-P |  | 1.962% | 1.931% | 1.926% | 1.922% | 1.922% | 1.922% | 1.922% | 1.922% | 1.922% | 1.922%
Wind-O |  | 8.222% | 8.185% | 8.166% | 8.148% | 8.148% | 8.148% | 8.148% | 8.148% | 8.148% | 8.148%
Solar |  | 5.287% | 6.282% | 6.501% | 6.516% | 6.516% | 6.516% | 6.516% | 6.516% | 6.516% | 6.516%
Storage | bar: 2024 to 2033
Total |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## Unconfirmed Retirement Capacity
Unconfirmed Retirement Capacity
Cumulative Summer-Rated Capacity Contribution (in MW) of Unconfirmed Retirements Not Available as of July 1 of the Reporting Year
| 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Unit Name
V H BRAUNIG STG 1 | 0 | 217 | 217 | 217 | 217 | 217
V H BRAUNIG STG 2 | 0 | 230 | 230 | 230 | 230 | 230
V H BRAUNIG STG 3 | 0 | 412 | 412 | 412 | 412 | 412
COLETO CREEK * | 0 | 0 | 0 | 655 | 655 | 655
O W SOMMERS STG 1 | 0 | 0 | 0 | 420 | 420 | 420
O W SOMMERS STG 2 | 0 | 0 | 0 | 0 | 0 | 410
J K SPRUCE U1 | 0 | 0 | 0 | 0 | 0 | 560
J K SPRUCE U2** | 0 | 0 | 0 | 0 | 785 | 785
TOTAL | 0 | 859 | 859 | 1934 | 2719 | 3689
Reserve Margin Excluding Unconfirmed Retirement Capacity | 34.14% | 44.36% | 44.32% | 42.34% | 41.4% | 40.53%
Reserve Margin Including Unconfirmed Retirement Capacity | 34.14% | 43.32% | 43.3% | 40.09% | 38.25% | 36.29%
Difference | 0% | -1.034% | -1.017% | -2.253% | -3.147% | -4.243%
__________________________________________________
Notes: (1) An "Unconfirmed Retirement" is defined as a generation unit for which a public announcement of the intent to permanently shut the unit down has been released, but a Notice of Suspension of Operations for the unit has not been received by ERCOT. (2) The criteria for listing a unit as an Unconfirmed Retirement include the following: a. A specific retirement date is cited in the announcement, or other timing information is given that indicates the unit will be unavailable as of June 1 of a CDR Reporting Year. b. The announcement, with follow-up inquiry by ERCOT, does not indicate that retirement timing is highly speculative.
* Vistra notified the U.S. Environmental Protection Agency on November 20, 2020 that Coleto Creek's Primary Ash Pond will be closed to meet requirements of EPA’s coal combustion residual (CCR) rule, and that boiler operations will cease no later than July 17, 2027. The notification is available on Vistra’s public website, https://www.luminant.com/ccr/. **CPS Energy is expecting to covert the J K SPRUCE unit 2 from coal-fired to natural gas-fired.

## Fossil Fuel SODG Capacities
Fossil Fuel Settlement Only Distributed Generator (SODG) Capacities
The following is a list of operating fossil fuel Settlement Only Distribution Generators (SODGs) being provided for informational purposes. (The reported capacities are not included in the reserve margin calculations.) As of 4/1/23, there are 627.2 MW of fossil fuel SODG capacity (255.0 MW fired by diesel fuel and 372.24 MW by natural gas). These resources have not been included in past CDR reports due to the difficulty in determining their capacity contributions during peak load periods, and because many are intended as emergency standby generators and are not available to ERCOT for dispatch when needed to address capacity scarcity conditions. Another complication is that such standby generators may be used to reduce on-site loads in order to participate in Demand Response programs such as "4 Coincident Peak" (4CP) and Emergency Response Service (ERS). As a result, historical load reduction impacts would be accounted for in the peak demand forecast, while the capacity of SODGs participating in ERS would already be accounted for in the CDR's ERS line items. The formal incorporation of fossil-fueled SODGs into future CDR reports has been a discussion topic at Supply Analysis Working Group meetings. Since SODG capacity accounting is not currently addressed in the ERCOT Nodal Protocols, a Nodal Protocol Revision Request (NPRR) is needed to address capacity double-counting, peak average capacity contributions, and other Distribution Generator (DG) accounting issues.
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN-SERVICE DATE | MW CAPACITY
NFG WATER AUTH AB | NFBWAB_CLODINE | FORT BEND | GAS | HOUSTON | 2023-03-01 | 0.8
NFG WATER AUTH AC | NFBWAC_CLODINE | FORT BEND | GAS | HOUSTON | 2023-03-01 | 0.8
BROOKSHIRES GROCERY | BRKSHR_G1 | SMITH | DIESEL | NORTH | 2023-02-01 | 5.4
SUNRIDER1 | SUNRIDE1_VENSW | ELLIS | GAS | NORTH | 2023-02-01 | 2
SUNRIDER2 | SUNRIDE2_VENSW | ELLIS | GAS | NORTH | 2023-02-01 | 2
SUNRIDER3 | SUNRIDE3_VENSW | ELLIS | GAS | NORTH | 2023-02-01 | 0.8
TRADITION BUFFALO SPEEDWAY | TRADBUFF_BRAYS | HARRIS | GAS | HOUSTON | 2023-01-05 | 1.2
WAL STORE 7361 | WAL7361_SOUT7361 | BRAZORIA | GAS | COASTAL | 2022-12-14 | 0.4
WAL STORE 5959 | WAL5959_HEIG5959 | HARRIS | GAS | HOUSTON | 2022-12-14 | 1.2
WAL STORE 3296 | WAL3296_WEST3296 | HARRIS | GAS | HOUSTON | 2022-12-14 | 1.2
WAL STORE 5246 | WAL5246_WHAR5246 | WHARTON | GAS | SOUTH | 2022-12-14 | 0.8
WAL STORE 5045 | WAL504_MOOD504 | GALVESTON | GAS | HOUSTON | 2022-12-01 | 1.2
HEB STORE 767 | HEB00767_PINEHU | MONTGOMERY | GAS | HOUSTON | 2022-12-01 | 1.2
WAL STORE 5147 | WAL5147_WEST5147 | DALLAS | GAS | NORTH | 2022-12-01 | 1.2
WAL STORE 791 | WAL791_STAD791 | JIM WELLS | GAS | SOUTH | 2022-12-01 | 1.2
RCM TANGLEWOOD | RCMTANGL_ULRICH | HARRIS | GAS | HOUSTON | 2022-11-09 | 0.8
NFG WATER AUTH A | NFBWA_CLODINE | FORT BEND | GAS | HOUSTON | 2022-11-02 | 2.4
RAVEN CHEMICAL | RAVECHEM_JORDAN | HARRIS | GAS | HOUSTON | 2022-11-02 | 3.2
TRADITION SENIOR LIVING CLEARFORK | TRADCF_TRADSLCF | TARRANT | GAS | NORTH | 2022-11-02 | 1.2
WAL STORE 5479 | WAL5479_PFLU5479 | TRAVIS | GAS | SOUTH | 2022-11-02 | 1.2
WAL STORE 561 | WAL561_EAST561 | EASTLAND | GAS | NORTH | 2022-10-05 | 1.3
WAL STORE 565 | WAL565_CORS565 | NAVARRO | GAS | NORTH | 2022-09-28 | 1.2
WAL STORE 5080 | WAL5080_SMIT5080 | TARRANT | GAS | NORTH | 2022-09-28 | 1.2
WAL STORE 407 | WAL407_KILL407 | BELL | GAS | NORTH | 2022-09-28 | 1.2
WAL STORE 3406 | WAL3406_KNOL3406 | DALLAS | GAS | NORTH | 2022-09-28 | 1.2
WAL STORE 2765 | WAL2765_LOSF2765 | CAMERON | GAS | COASTAL | 2022-09-28 | 0.8
WAL STORE 896 | WAL896_MAYF896 | TARRANT | GAS | NORTH | 2022-09-21 | 1.2
WAL STORE 456 | WAL456_OLMI456 | CAMERON | GAS | COASTAL | 2022-09-21 | 1.2
WAL STORE 2980 | WAL2980_KELL2980 | TARRANT | GAS | NORTH | 2022-09-21 | 1.2
WAL STORE 266 | WAL266_KIMB266 | TARRANT | GAS | NORTH | 2022-09-21 | 1.2
WAL STORE 5312 | WAL5312_SPRI5312 | TARRANT | GAS | NORTH | 2022-09-14 | 1.2
WAL STORE 452 | WAL452_NORT452 | HIDALGO | GAS | SOUTH | 2022-09-14 | 1.2
WAL STORE 447 | WAL447_DELR447 | VAL VERDE | GAS | WEST | 2022-09-14 | 1.2
WAL STORE 2883 | WAL2883_MCDE2883 | COLLIN | GAS | NORTH | 2022-09-14 | 1.6
WAL STORE 5713 | WAL5713_UNIV5713 | WEBB | GAS | SOUTH | 2022-09-01 | 1.2
WAL STORE 536 | WAL536_ABIL536 | TAYLOR | GAS | WEST | 2022-09-01 | 1.2
WAL STORE 3518 | WAL3518_GATE3518 | WEBB | GAS | SOUTH | 2022-09-01 | 1.2
WAL STORE 344 | WAL344_ELCA344 | WHARTON | GAS | SOUTH | 2022-09-01 | 0.8
WAL STORE 3224 | WAL3224_MESQ3224 | DALLAS | GAS | NORTH | 2022-07-13 | 1.2
WAL STORE 1062 | WAL1062_PILG1062 | HARRIS | GAS | HOUSTON | 2022-07-13 | 1.2
WAL STORE 5480 | WAL5480_HUTT5480 | WILLIAMSON | GAS | SOUTH | 2022-06-02 | 1.2
WAL STORE 3432 | WAL3432_PARK3432 | DALLAS | GAS | NORTH | 2022-06-02 | 1.2
WAL STORE 3285 | WAL3285_CEDA3285 | DALLAS | GAS | NORTH | 2022-06-02 | 1.2
WAL STORE 2993 | WAL2993_IMPE2993 | FORT BEND | GAS | HOUSTON | 2022-06-02 | 1.2
CITY OF VICTORIA - SURFACE WATER TREATMENT PLANT | SWTP_1_SWTP_1 | VICTORIA | DIESEL | SOUTH | 2022-05-25 | 1.25
WAL STORE 3584 | WAL3584_BELL3584 | HARRIS | GAS | HOUSTON | 2022-05-25 | 1.2
WAL STORE 284 | WAL284_MANS284 | TARRANT | GAS | NORTH | 2022-05-25 | 1.2
WAL STORE 5612 | WAL5612_UNIV5612 | HARRIS | GAS | HOUSTON | 2022-05-18 | 1.2
WAL STORE 4526 | WAL4526_AIRL4526 | HARRIS | GAS | HOUSTON | 2022-05-18 | 1.2
WAL STORE 4298 | WAL4298_LOCK4298 | HARRIS | GAS | HOUSTON | 2022-05-18 | 1.2
WAL STORE 3500 | WAL3500_UVAL3500 | HARRIS | GAS | HOUSTON | 2022-05-11 | 1.2
WAL STORE 3425 | WAL3425_SOUT3425 | HARRIS | GAS | HOUSTON | 2022-05-11 | 1.2
WAL STORE 2257 | WAL2257_FAIR2257 | HARRIS | GAS | HOUSTON | 2022-05-11 | 1.2
WAL STORE 772 | WAL772_BARK772 | HARRIS | GAS | HOUSTON | 2022-05-04 | 1.2
HEB STORE 769 | HEB769_ELDOR769 | GALVESTON | GAS | HOUSTON | 2021-12-16 | 1.2
WAL STORE 5165 | WAL5165_NORT5165 | HIDALGO | GAS | SOUTH | 2021-09-17 | 1.2
WAL STORE 3320 | WAL3320_PALM3320 | HIDALGO | GAS | SOUTH | 2021-09-17 | 1.2
WAL STORE 3886 | WAL3886_MCCO3886 | HIDALGO | GAS | SOUTH | 2021-09-03 | 1.2
WAL STORE 461 | WAL461_ESCO461 | MAVERICK | GAS | SOUTH | 2021-07-29 | 1.2
WAL STORE 1494 | WAL1494_SOUT1494 | NUECES | GAS | COASTAL | 2021-07-12 | 1.3
HEB SA DC | HEBDC2_ADDICDCB | HARRIS | GAS | HOUSTON | 2021-07-07 | 4.8
WAL STORE 490 | WAL490_NAVA490 | NUECES | GAS | COASTAL | 2021-06-14 | 1.3
WAL STORE 3225 | WAL3225_ROWL3225 | DALLAS | GAS | NORTH | 2021-06-01 | 1.2
WAL STORE 3284 | WAL3284_KENN3284 | TARRANT | GAS | NORTH | 2021-05-25 | 1.2
HEB STORE 419 | HEB419_EPASS419 | MAVERICK | GAS | SOUTH | 2021-05-19 | 0.8
HEB STORE 418 | HEB418_DELRI418 | VAL VERDE | GAS | WEST | 2021-05-14 | 0.8
WAL STORE 414 | WAL414_SIKE414 | WICHITA | GAS | WEST | 2021-05-06 | 1.2
HEB DISTRIBUTION CENTER 1 | HEBDC1_ADDICDCA | HARRIS | GAS | HOUSTON | 2021-05-06 | 8
WAL STORE 5764 | WAL5764_JOHN5764 | TARRANT | GAS | NORTH | 2021-04-30 | 1.2
WAL STORE 1272 | WAL1272_DEEP1272 | SCURRY | GAS | WEST | 2021-04-28 | 1.2
WAL STORE 5460 | WAL5460_GREG5460 | SAN PATRICIO | GAS | COASTAL | 2021-04-21 | 1.3
WAL STORE 4194 | WAL4194_VICT4194 | VICTORIA | GAS | SOUTH | 2021-04-21 | 1.3
WAL STORE 440 | WAL440_FULT440 | ARANSAS | GAS | COASTAL | 2021-04-16 | 1.3
WAL STORE 463 | WAL463_BEEV463 | BEE | GAS | SOUTH | 2021-04-14 | 1.3
FT BEND LID 2 B | FTBL2B_IMPERIAL | HARRIS | GAS | HOUSTON | 2021-04-13 | 5.6
FT BEND LID 2 A | FTBL2A_IMPERIAL | HARRIS | GAS | HOUSTON | 2021-04-13 | 5.6
HEB STORE 441 | HEB441_UVALD441 | HIDALGO | GAS | SOUTH | 2021-04-08 | 0.8
WAL STORE 897 | WAL897_AIR897 | PECOS | GAS | WEST | 2021-04-01 | 1.3
HEB STORE 696 | HEB696_HUTTO696 | WILLIAMSON | GAS | SOUTH | 2021-02-01 | 1.2
WAL STORE 1249 | WAL1249_LAKE1249 | TOM GREEN | GAS | WEST | 2021-01-29 | 1.3
WAL STORE 601 | WAL601_BLUF601 | TOM GREEN | GAS | WEST | 2021-01-28 | 1.3
WAL STORE 5311 | WAL5311_ROCK5311 | COLLIN | DIESEL | NORTH | 2020-12-31 | 1.25
WAL STORE 4509 | WAL4509_BENB4509 | TARRANT | GAS | NORTH | 2020-11-23 | 1.2
WAL STORE 6929 | WAL6929_TEMP6929 | BELL | GAS | NORTH | 2020-10-22 | 1.2
WAL STORE 972 | WAL972_ROSE972 | TARRANT | GAS | NORTH | 2020-10-15 | 1.2
WAL STORE 947 | WAL947_SHER947 | GRAYSON | GAS | NORTH | 2020-10-15 | 1.2
WAL STORE 940 | WAL940_CALM940 | TARRANT | GAS | NORTH | 2020-10-15 | 1.2
WAL STORE 5316 | WAL5316_WAGL5316 | TARRANT | GAS | NORTH | 2020-10-15 | 1.2
LAKESIDE COUNTRY CLUB | LKSDECC_HAYESLCC | HARRIS | GAS | HOUSTON | 2020-10-07 | 1.2
HEB STORE 771 | CHEB771_DG_V3_1 | BEXAR | GAS | SOUTH | 2020-10-07 | 1.2
HEB STORE 713 | HEB713_CLELK713 | HARRIS | GAS | HOUSTON | 2020-10-01 | 0.8
HEB STORE 732 | CHEB732_DG_SK_1 | BEXAR | GAS | SOUTH | 2020-10-01 | 1.2
WAL STORE 1232 | WAL1232_BELT1232 | BELL | GAS | NORTH | 2020-09-29 | 1.2
WAL STORE 3773 | WAL3773_WEST3773 | TARRANT | GAS | NORTH | 2020-09-11 | 1.2
WAL STORE 3631 | WAL3631_SYCA3631 | TARRANT | GAS | NORTH | 2020-09-11 | 1.2
WAL STORE 849 | WAL849_SPRG849 | HARRIS | GAS | HOUSTON | 2020-09-01 | 1.2
WAL STORE 752 | WAL752_CARD752 | HARRIS | GAS | HOUSTON | 2020-09-01 | 1.2
HEB STORE 711 | HEB711_ODNTH711 | ECTOR | GAS | WEST | 2020-08-21 | 0.8
HEB STORE 717 | HEB717_MDESA717 | MIDLAND | GAS | WEST | 2020-08-19 | 1.2
HEB STORE 674 | HEB674_PALMH674 | HIDALGO | GAS | SOUTH | 2020-08-12 | 0.8
WAL STORE 3298 | WAL3298_KEMA3298 | GALVESTON | GAS | HOUSTON | 2020-08-11 | 1.2
WAL STORE 4512 | WAL4512_FRAN4512 | HARRIS | GAS | HOUSTON | 2020-08-10 | 1.2
WAL STORE 5045 | WAL5045_KLEI5045 | HARRIS | GAS | HOUSTON | 2020-08-06 | 1.2
TRADITION WOODWAY | TRDWDY_ULRICHTW | HARRIS | GAS | HOUSTON | 2020-08-06 | 1.2
WAL STORE 522 | WAL522_NEWP522 | HARRIS | GAS | HOUSTON | 2020-08-05 | 1.2
HEB STORE 593 | HEB593_TLRWT593 | WILLIAMSON | GAS | SOUTH | 2020-08-04 | 0.8
WAL STORE 602 | WAL602_RAYF602 | MONTGOMERY | GAS | HOUSTON | 2020-08-03 | 1.2
HEB STORE 725 | HEB725_KLEIN725 | HARRIS | GAS | HOUSTON | 2020-08-03 | 0.8
WAL STORE 2439 | WAL2439_MT_B2439 | CHAMBERS | GAS | HOUSTON | 2020-07-30 | 1.2
HEB STORE 444 | CHEB444_DG_V2_1 | BEXAR | GAS | SOUTH | 2020-07-30 | 1.2
WAL STORE 3297 | WAL3297_SATS3297 | HARRIS | GAS | HOUSTON | 2020-07-29 | 1.2
WAL STORE 872 | WAL872_TELP872 | BRAZORIA | GAS | COASTAL | 2020-07-24 | 1.2
WAL STORE 744 | WAL744_HUMB744 | HARRIS | GAS | HOUSTON | 2020-07-22 | 1.2
WAL STORE 546 | WAL546_READ546 | FORT BEND | GAS | HOUSTON | 2020-07-22 | 1.2
HEB STORE 749 | HEB749_FLEWE749 | FORT BEND | GAS | HOUSTON | 2020-07-22 | 1.2
WAL STORE 5287 | WAL5287_KUYD5287 | HARRIS | GAS | HOUSTON | 2020-07-21 | 1.2
WAL STORE 3390 | WAL3390_TOMB3390 | MONTGOMERY | GAS | HOUSTON | 2020-07-21 | 1.2
WAL STORE 5091 | WAL5091_CYFA5091 | HARRIS | GAS | HOUSTON | 2020-07-17 | 1.2
WAL STORE 3827 | WAL3827_FLEW3827 | FORT BEND | GAS | HOUSTON | 2020-07-14 | 1.2
WAL STORE 194 | WAL194_GART194 | HARRIS | GAS | HOUSTON | 2020-07-14 | 1.2
WAL STORE 5116 | WAL5116_FAIR5116 | HARRIS | GAS | HOUSTON | 2020-07-13 | 1.2
WAL STORE 2724 | WAL2724_PASD2724 | HARRIS | GAS | HOUSTON | 2020-07-13 | 1.2
HEB STORE 715 | HEB715_FRMNT715 | HARRIS | GAS | HOUSTON | 2020-07-13 | 0.8
CNP CYPRESS STATION | CNPMUD_WESFDMUD | HARRIS | GAS | HOUSTON | 2020-07-10 | 0.8
HEB STORE 016 | HEB016_CRWLY016 | JOHNSON | GAS | NORTH | 2020-06-18 | 0.8
HEB STORE 756 | HEB756_BLGET756 | HARRIS | GAS | HOUSTON | 2020-06-09 | 1.2
HEB STORE 475 | HEB475_ELGIN475 | BASTROP | GAS | SOUTH | 2020-06-09 | 0.8
HEB STORE 745 | HEB745_SHARP745 | HARRIS | GAS | HOUSTON | 2020-06-08 | 1.2
HEB STORE 485 | HEB485_WESLA485 | HIDALGO | GAS | SOUTH | 2020-05-19 | 0.8
HEB STORE 434 | HEB434_BRKHL434 | CALHOUN | GAS | COASTAL | 2020-05-13 | 0.8
HEB STORE 172 | HEB172_SEDNB172 | HIDALGO | GAS | SOUTH | 2020-05-06 | 0.8
WAL STORE 5388 | WAL5388_LEA5388 | GALVESTON | GAS | HOUSTON | 2020-05-01 | 1.3
WAL STORE 529 | WAL529_LAM529 | GALVESTON | GAS | HOUSTON | 2020-05-01 | 1.3
WAL STORE 0462 | WAL462_ALV462 | BRAZORIA | GAS | COASTAL | 2020-05-01 | 1.3
HEB STORE 448 | HEB448_PLMVW448 | HIDALGO | GAS | SOUTH | 2020-04-30 | 0.8
CITIZENS MEDICAL CENTER | CTZSMC_NVICTCTZ | VICTORIA | GAS | SOUTH | 2020-04-26 | 2.8
HEB STORE 747 | HEB747_LKMNT747 | DALLAS | GAS | NORTH | 2020-03-27 | 0.8
HEB STORE 383 | HEB383_CAUSE383 | CAMERON | GAS | COASTAL | 2020-03-11 | 0.8
HEB SA DC | CHEBDC_DG_L2_1 | BEXAR | GAS | SOUTH | 2020-03-03 | 6.4
HEB STORE 084 | CHEB084_DG_J0_1 | BEXAR | GAS | SOUTH | 2020-02-26 | 1.2
WAL STORE 3510 | WAL3510_PRL3510 | BRAZORIA | GAS | COASTAL | 2020-02-25 | 1.3
WAL STORE 5211 | WAL5211_CRAI5211 | COLLIN | DIESEL | NORTH | 2020-01-31 | 1.25
WAL STORE 3777 | WAL3777_PANT3777 | DENTON | DIESEL | NORTH | 2020-01-31 | 1.25
HEB STORE 026 | CHEB026_DG_Q5_1 | COMAL | GAS | SOUTH | 2019-12-19 | 1.2
HEB STORE 658 | CHEB658_DG_V5_1 | BEXAR | GAS | SOUTH | 2019-12-10 | 1.2
WAL STORE 768 | WAL768_FRAN768 | HARRIS | GAS | HOUSTON | 2019-12-02 | 1.2
STANDARD MEAT | ST_MEAT_CKRHLSTM | DALLAS | GAS | NORTH | 2019-11-30 | 1.2
HEB STORE 545 | HEB545_FARON545 | TARRANT | GAS | NORTH | 2019-11-30 | 1.2
BUC-EES STORE 048 | BUC048_ENSSO048 | ELLIS | GAS | NORTH | 2019-11-30 | 1.2
HEB STORE 552 | HEB552_GAVSW552 | DALLAS | GAS | NORTH | 2019-10-30 | 1.2
WAL STORE 3226 | WAL3226_KTY3226 | HARRIS | GAS | HOUSTON | 2019-10-07 | 1.2
WAL STORE 1040 | WAL1040_GERT1040 | HARRIS | GAS | HOUSTON | 2019-09-20 | 1.2
WAL STORE 1103 | WAL1103_BAM1103 | HARRIS | GAS | HOUSTON | 2019-09-10 | 1.2
HEB CC BAKERY | HEBCCB_HWY9CCB | NUECES | GAS | COASTAL | 2019-09-10 | 3.2
SILVER EAGLE | TBFY_U1 | HARRIS | DIESEL | HOUSTON | 2019-08-27 | 1.5
WAL STORE 4538 | WAL4538_FRAN4538 | HARRIS | GAS | HOUSTON | 2019-08-21 | 1.2
HEB STORE 085 | CHEB085_DG_P5_1 | BEXAR | GAS | SOUTH | 2019-08-20 | 1.6
HEB STORE 574 | HEB574_TOMBA574 | HARRIS | GAS | HOUSTON | 2019-07-11 | 1.2
HEB STORE 559 | HEB559_BLUER559 | HARRIS | GAS | HOUSTON | 2019-07-10 | 0.8
HEB STORE 564 | HEB564_RAFRD564 | MONTGOMERY | GAS | HOUSTON | 2019-07-03 | 0.8
POWERSECURE NORBORD TEXAS INC 2 | NOR2_NORBORD_2 | NACOGDOCHES | DIESEL | NORTH | 2019-04-09 | 2.5
POWERSECURE NORBORD TEXAS INC 1 | NOR1_NORBORD_1 | NACOGDOCHES | DIESEL | NORTH | 2019-04-09 | 5
HEB SNACK PLANT | HEBSP_TANNERSP | HARRIS | GAS | HOUSTON | 2019-04-05 | 1.6
HEB STORE 586 | HEB586_STNIO586 | WEBB | GAS | SOUTH | 2019-03-28 | 1.2
HEB STORE 752 | HEB752_LGVST752 | PARKER | GAS | NORTH | 2019-02-11 | 1.2
BUC-EES STORE 044 | BUC044_ANASE044 | COLLIN | GAS | NORTH | 2019-02-11 | 1.2
BUC-EES STORE 038 | BUC038_RYSSW038 | ROCKWALL | GAS | NORTH | 2019-02-11 | 1.2
HEB STORE 563 | HEB563_CRABB563 | FORT BEND | GAS | HOUSTON | 2019-01-22 | 1.2
HEB STORE 737 | HEB737_WHTOK737 | HARRIS | GAS | HOUSTON | 2018-12-31 | 1.2
HEB STORE 753 | HEB753_DRPRK753 | HARRIS | GAS | HOUSTON | 2018-12-18 | 0.8
HEB STORE 070 | HEB070_MCMRY070 | TAYLOR | GAS | WEST | 2018-11-28 | 1.2
HEB STORE 546 | HEB546_RENSW546 | COLLIN | GAS | NORTH | 2018-11-19 | 1.2
HEB STORE 540 | HEB540_GGATE540 | HARRIS | GAS | HOUSTON | 2018-11-01 | 1.13
HEB STORE 562 | HEB562_FULTN562 | ARANSAS | GAS | COASTAL | 2018-10-31 | 0.8
HEB STORE 473 | HEB473_CARDF473 | HARRIS | GAS | HOUSTON | 2018-10-31 | 1.2
HEB STORE 738 | HEB738_SHPTN738 | HARRIS | GAS | HOUSTON | 2018-10-04 | 1.2
HEB STORE 449 | HEB449_DELMA449 | WEBB | GAS | SOUTH | 2018-09-27 | 0.8
HEB STORE 095 | HEB095_MILOA095 | WEBB | GAS | SOUTH | 2018-09-27 | 1.6
HEB STORE 054 | HEB054_HALL054 | HARRIS | GAS | HOUSTON | 2018-09-27 | 1.2
HEB STORE 599 | HEB599_KIRBY599 | HARRIS | GAS | HOUSTON | 2018-09-26 | 1.2
HEB STORE 553 | HEB553_GRTIE553 | HARRIS | GAS | HOUSTON | 2018-09-25 | 0.8
HEB STORE 581 | HEB581_KLELM581 | BELL | GAS | NORTH | 2018-08-24 | 1.2
HEB STORE 381 | HEB381_HKHTS381 | BELL | GAS | NORTH | 2018-08-24 | 1.2
HEB STORE 488 | HEB488_PTLND488 | SAN PATRICIO | GAS | COASTAL | 2018-08-21 | 0.8
HEB STORE 721 | HEB721_KLNSO721 | BELL | GAS | NORTH | 2018-08-10 | 1.2
HEB STORE 672 | HEB672_WSOTH672 | MCLENNAN | GAS | NORTH | 2018-08-10 | 1.2
HEB STORE 668 | HEB668_COVEE668 | CORYELL | GAS | NORTH | 2018-08-10 | 1.2
HEB STORE 426 | HEB426_WXNTH426 | ELLIS | GAS | NORTH | 2018-08-10 | 1.2
HEB STORE 423 | HEB423_WNTHW423 | MCLENNAN | GAS | NORTH | 2018-08-10 | 0.8
HEB STORE 236 | HEB236_RDRSE236 | TRAVIS | GAS | SOUTH | 2018-08-10 | 0.8
HEB STORE 182 | HEB182_TMSTH182 | BELL | GAS | NORTH | 2018-08-10 | 1.2
HEB STORE 495 | HEB495_RDRSE495 | WILLIAMSON | GAS | SOUTH | 2018-07-17 | 0.8
HEB STORE 640 | HEB640_UVLDE640 | HARRIS | GAS | HOUSTON | 2018-06-20 | 0.8
HEB STORE 491 | HEB491_SNFLP491 | HARRIS | GAS | HOUSTON | 2018-06-19 | 1.13
HEB STORE 109 | HEB109_ECHO109 | HARRIS | GAS | HOUSTON | 2018-06-15 | 1.13
HEB STORE 667 | HEB667_FNDRN667 | HARRIS | GAS | HOUSTON | 2018-06-12 | 0.8
RELLIS CAMPUS | TAMURE_RELLISAM | BRAZOS | GAS | NORTH | 2018-06-01 | 9.6
HEB STORE 255 | HEB255_ZACAT255 | WEBB | GAS | SOUTH | 2018-05-31 | 1.2
HEB STORE 675 | HEB675_MARCK675 | BRAZORIA | GAS | COASTAL | 2018-05-24 | 1.13
HEB STORE 720 | HEB720_KNGWD720 | HARRIS | GAS | HOUSTON | 2018-05-22 | 1.13
HEB STORE 709 | HEB709_FRYRD709 | HARRIS | GAS | HOUSTON | 2018-05-22 | 1.2
HEB STORE 748 | HEB748_LOUET748 | HARRIS | GAS | HOUSTON | 2018-05-21 | 0.8
HEB STORE 596 | HEB596_FLWEN596 | FORT BEND | GAS | HOUSTON | 2018-05-08 | 1.13
HEB STORE 707 | HEB707_LKJCK707 | BRAZORIA | GAS | COASTAL | 2018-05-02 | 1.13
HEB STORE 649 | HEB649_LTTYK649 | HARRIS | GAS | HOUSTON | 2018-04-27 | 0.8
HEB STORE 498 | HEB498_HUMBL498 | HARRIS | GAS | HOUSTON | 2018-04-27 | 1.13
HEB STORE 038 | HEB038_PHARR038 | HIDALGO | GAS | SOUTH | 2018-04-26 | 1.2
HEB STORE 741 | HEB741_MTBEL741 | CHAMBERS | GAS | HOUSTON | 2018-04-24 | 0.8
HEB STORE 648 | HEB648_BERRY648 | HARRIS | GAS | HOUSTON | 2018-04-20 | 1.13
HEB STORE 591 | HEB591_RRNES591 | WILLIAMSON | GAS | SOUTH | 2018-04-11 | 1.6
HEB STORE 479 | HEB479_PFLGV479 | TRAVIS | GAS | SOUTH | 2018-04-11 | 0.8
HEB STORE 401 | HEB401_KNGVL401 | KLEBERG | GAS | COASTAL | 2018-04-11 | 0.8
HEB STORE 373 | HEB373_RNDRK373 | WILLIAMSON | GAS | SOUTH | 2018-04-11 | 0.8
HEB STORE 223 | HEB223_STCSW223 | JIM WELLS | GAS | SOUTH | 2018-04-11 | 1.2
BUC-EES STORE 035 | BUC035_TMNTH035 | BELL | GAS | NORTH | 2018-04-11 | 1.13
HEB STORE 727 | HEB727_CRBRR727 | FORT BEND | GAS | HOUSTON | 2018-04-09 | 1.2
HEB STORE 736 | HEB736_FLWEN736 | FORT BEND | GAS | HOUSTON | 2018-04-06 | 1.2
HEB STORE 742 | HEB742_HNYRT742 | HARRIS | GAS | HOUSTON | 2018-04-03 | 1.2
HEB STORE 642 | HEB642_HAACR642 | HIDALGO | GAS | SOUTH | 2018-03-22 | 1.2
HEB STORE 431 | HEB431_MCOLL431 | HIDALGO | GAS | SOUTH | 2018-03-21 | 1.2
HEB STORE 554 | HEB554_NVICT554 | VICTORIA | GAS | SOUTH | 2018-03-14 | 1.2
HEB STORE 615 | HEB615_KATY615 | FORT BEND | GAS | HOUSTON | 2018-03-08 | 1.13
HEB STORE 334 | HEB334_WMCAL334 | HIDALGO | GAS | SOUTH | 2018-02-28 | 1.2
HEB STORE 212 | HEB212_PLKAV212 | HIDALGO | GAS | SOUTH | 2018-02-28 | 0.8
HEB STORE 231 | HEB231_WESLA231 | HIDALGO | GAS | SOUTH | 2018-02-08 | 0.8
JRABTUD | JKRBT_JRB | HARRIS | DIESEL | HOUSTON | 2018-02-01 | 1.08
HEB STORE 092 | HEB092_LEALN092 | VICTORIA | GAS | SOUTH | 2018-01-17 | 1.6
HEB STORE 291 | HEB291_WHRLG291 | CAMERON | GAS | COASTAL | 2018-01-11 | 1.2
HEB STORE 558 | HEB558_FRDSW558 | GALVESTON | GAS | HOUSTON | 2018-01-08 | 1.13
HEB STORE 136 | HEB136_EHRSN136 | CAMERON | GAS | COASTAL | 2018-01-04 | 0.8
HEB STORE 462 | HEB462_ARCIA462 | NUECES | GAS | COASTAL | 2017-12-14 | 1.2
HEB STORE 270 | HEB270_ARLN270 | NUECES | GAS | COASTAL | 2017-12-08 | 0.8
TERRANOVA WEST MUD | LU_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-12-01 | 0.32
LANGHAM CREEK | ADK_1UNIT | HARRIS | DIESEL | HOUSTON | 43070 | 0.54
HEB STORE 210 | HEB210_SOUSD210 | NUECES | GAS | COASTAL | 2017-12-01 | 0.8
HOLLY HALL | HH2000_HOLMESHH | HARRIS | GAS | HOUSTON | 2017-11-03 | 1.2
HEB STORE 139 | HEB139_HOLLY139 | NUECES | GAS | COASTAL | 2017-11-01 | 0.8
HEB STORE 069 | HEB069_AIRLN069 | NUECES | GAS | COASTAL | 2017-10-25 | 1.6
HEB STORE 57 | HEB057_LAGUN057 | NUECES | GAS | COASTAL | 2017-10-10 | 1.2
HEB STORE 734 | HEB734_BLFFS734 | TOM GREEN | GAS | WEST | 2017-09-27 | 1.2
HEB STORE 724 | HEB724_OBRN724 | FORT BEND | GAS | HOUSTON | 2017-09-18 | 1.13
HEB STORE 722 | HEB722_PINHU722 | MONTGOMERY | GAS | HOUSTON | 2017-08-23 | 1.13
UTMB WEST PLANT | UTMBWEST_CT1 | GALVESTON | GAS | HOUSTON | 2017-08-02 | 5.4
HEB STORE 697 | HEB697_SOUSH697 | GALVESTON | GAS | HOUSTON | 2017-07-27 | 1.13
OAKBEND MEDICAL CENTER | READNG_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-07-12 | 1.62
HEB STORE 610 | HEB610_LOU610 | HARRIS | GAS | HOUSTON | 2017-07-03 | 1.13
HEB STORE 110 | HEB110_SIEN110 | FORT BEND | GAS | HOUSTON | 2017-07-03 | 1.13
HEB STORE 20 | HEB020_CYFR020 | HARRIS | GAS | HOUSTON | 2017-07-03 | 1.51
HEB STORE 28 | HEB028_LGCTY028 | GALVESTON | GAS | HOUSTON | 2017-06-28 | 1.13
BUC-EES STORE 033 | BUC033_TXCTY033 | GALVESTON | GAS | HOUSTON | 2017-06-05 | 1.13
HEB STORE 645 | HEB645_CDRBY645 | HARRIS | GAS | HOUSTON | 2017-06-01 | 0.75
HEB STORE 576 | HEB576_KLEIN576 | HARRIS | GAS | HOUSTON | 2017-06-01 | 1.13
HEB STORE 575 | HEB575_BRKER575 | HARRIS | GAS | HOUSTON | 2017-06-01 | 1.13
HEB STORE 551 | HEB551_WSTCS551 | HARRIS | GAS | HOUSTON | 2017-06-01 | 1.13
HEB STORE 474 | HEB474_DWLT474 | FORT BEND | GAS | HOUSTON | 2017-06-01 | 1.13
BUC-EES STORE 040 | BUC040_KATY040 | FORT BEND | GAS | HOUSTON | 2017-05-31 | 1.13
BUC-EES STORE 030 | BUC030_WHRTN030 | WHARTON | GAS | SOUTH | 2017-05-16 | 0.75
PEPPERL FUCHS | PEPF01_WALLER01 | WALLER | GAS | HOUSTON | 2017-05-05 | 1.13
HEB STORE 627 | HEB627_IMPRL627 | FORT BEND | GAS | HOUSTON | 2017-05-01 | 1.13
HEB STORE 497 | HEB497_MASRD497 | HARRIS | GAS | HOUSTON | 2017-05-01 | 1.13
HEB STORE 99 | HEB099_KLEIN099 | HARRIS | GAS | HOUSTON | 2017-05-01 | 1.13
BUC-EES STORE 034 | BUC034_BYTWN034 | HARRIS | GAS | HOUSTON | 2017-05-01 | 1.13
BUC-EES STORE 003 | BUC003_BRZIA003 | BRAZORIA | GAS | COASTAL | 2017-04-25 | 0.38
HEB STORE 731 | HEB731_WSFLD731 | HARRIS | GAS | HOUSTON | 2017-04-06 | 0.75
HEB STORE 698 | HEB698_KLUGE698 | HARRIS | GAS | HOUSTON | 2017-04-03 | 1.13
HEB STORE 614 | HEB614_KING614 | HARRIS | GAS | HOUSTON | 2017-04-03 | 1.13
BUC-EES STORE 018 | BUC018_WALLR018 | WALLER | GAS | HOUSTON | 2017-04-03 | 1.13
WINDFERN FOREST UD | FR_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-03-31 | 0.54
REMINGTON MUD 001 | CYFAIR_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-03-31 | 0.54
HARRIS COUNTY WCID 109 | BA_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-03-29 | 0.32
HARRIS COUNTY MUD #36 | WF_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-03-24 | 0.54
NORTHAMPTON MUD | KDL_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-03-22 | 0.32
HARRIS COUNTY MUD 536 | KT_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-03-07 | 0.54
HEB STORE 705 | HEB705_SPRWD705 | MONTGOMERY | GAS | HOUSTON | 2017-03-01 | 1.13
PLANET FORD I45 | PFI45_PFORDI45 | HARRIS | GAS | HOUSTON | 2017-02-01 | 1.13
HEB STORE 686 | HEB686_KUYKL686 | HARRIS | GAS | HOUSTON | 2017-02-01 | 1.13
PANTHER PLANT | PAPL_DG1 | UPTON | GAS | WEST | 2017-01-13 | 8.28
SATSUMA | SATSUM_1UNIT | HARRIS | DIESEL | HOUSTON | 2017-01-04 | 0.63
HEB STORE 616 | HEB616_BAML616 | HARRIS | GAS | HOUSTON | 2017-01-03 | 0.75
HEB STORE 292 | HEB292_BYCTY292 | MATAGORDA | GAS | COASTAL | 2016-12-05 | 1.13
HEB STORE 656 | HEB656_HOKLE656 | HARRIS | GAS | HOUSTON | 2016-11-30 | 1.13
HEB STORE 492 | HEB492_FRANZ492 | HARRIS | GAS | HOUSTON | 2016-11-30 | 1.13
HEB STORE 63 | HEB063_SOWIK063 | BRAZORIA | GAS | COASTAL | 2016-11-30 | 1.51
HEB STORE 541 | HEB541_ROARK541 | HARRIS | GAS | HOUSTON | 2016-11-22 | 1.13
HEB STORE 687 | HEB687_ULRIC687 | HARRIS | GAS | HOUSTON | 2016-11-18 | 1.13
UTMB East Plant | UTMBEAST_CT1 | GALVESTON | GAS | HOUSTON | 2016-03-15 | 7.56
TOTAL ENERGY SOLUTIONS 2 | TES2_DGGROUPB | BRAZORIA | DIESEL | COASTAL | 2015-06-01 | 5.4
TOTAL ENERGY SOLUTIONS 1 | TES1_DGDROUPA | BRAZORIA | DIESEL | COASTAL | 2015-06-01 | 7.2
TPC POWER STATION | TPC_6UNITS | SMITH | DIESEL | NORTH | 2015-05-31 | 9.93
DGSP2 BIGCAT | ABEC2_3UNIT | TAYLOR | DIESEL | WEST | 42019 | 9.77
DGSP2 PLAZA | ABEC_2UNIT | TAYLOR | DIESEL | WEST | 41967 | 9.77
GCWAMUNI | GCWAMUNI_4UNITS | GALVESTON | DIESEL | HOUSTON | 2014-10-01 | 2.5
GCWA IPS | INTRCITY_8UNITS | GALVESTON | DIESEL | HOUSTON | 2014-08-06 | 5
DGS 5 POINTS | DG_ABEC_1UNIT | TAYLOR | DIESEL | WEST | 2014-01-10 | 9.77
POWER DEPOT - MCKEEVER | DGWAP_15UNITS | FORT BEND | DIESEL | HOUSTON | 2013-10-25 | 9.38
DGS PALO PINTO | MNWLL_1UNIT | PALO PINTO | DIESEL | NORTH | 2013-07-02 | 9.77
POWER DEPOT - WESTOVER | WOVER_15UNITS | ECTOR | DIESEL | WEST | 2013-06-15 | 9.38
POWER DEPOT - ADDICKS | WO_15UNITS | HARRIS | DIESEL | HOUSTON | 2013-06-15 | 9.38
POWER DEPOT - VILLA CAVASOS | VCAVASOS_15UNITS | CAMERON | DIESEL | COASTAL | 2013-06-15 | 9.38
POWER DEPOT - S. SANTA ROSA | S_SNROSA_15UNITS | CAMERON | DIESEL | COASTAL | 2013-06-15 | 9.38
POWER DEPOT - HAINE | HAINE_DR_15UNITS | CAMERON | DIESEL | COASTAL | 2013-06-15 | 9.38
POWER DEPOT - GOLDSMITH | GSMTH_15UNITS | ECTOR | DIESEL | WEST | 2013-06-15 | 9.38
POWER DEPOT - KATY | FL_15UNITS | WALLER | DIESEL | HOUSTON | 2013-06-15 | 9.38
POWER DEPOT - FRANKEL CITY | FKLCY_15UNITS | ANDREWS | DIESEL | WEST | 2013-06-15 | 9.38
POWER DEPOT EL GATO | ELGATO_15UNITS | HIDALGO | DIESEL | SOUTH | 2013-06-15 | 9.38
POWER DEPOT - HILMONT | ECTHM_15UNITS | ECTOR | DIESEL | WEST | 2013-06-15 | 9.38
POWER DEPOT - E HARRISON | E_HARRIS_15UNITS | CAMERON | DIESEL | COASTAL | 2013-06-15 | 9.38
POWER DEPOT - TH WHARTON | DGTHW_15UNITS | HARRIS | DIESEL | HOUSTON | 2013-06-15 | 9.38
POWER DEPOT - SOUTHWICK | DGHOC_15UNITS | HARRIS | DIESEL | HOUSTON | 2013-06-15 | 9.38
POWER DEPOT - CITRUS CITY | CITRUSCY_15UNITS | HIDALGO | DIESEL | SOUTH | 2013-06-15 | 9.38
POWER DEPOT - BAKKE | BAKKE_15UNITS | ANDREWS | DIESEL | WEST | 2013-06-15 | 9.38
POWER DEPOT - ANDREWS | ANDNR_15UNITS | ANDREWS | DIESEL | WEST | 2013-06-15 | 9.38
ROBERT MUELLER ENERGY CENTER | RMEC_CT1 | TRAVIS | GAS | SOUTH | 2011-09-23 | 5.8
RHODIA HOUSTON PLANT | DG_HG_2UNITS | HARRIS | GAS | HOUSTON | 1970-01-01 | 8.2

## Decommissioned Gen. Resources
Decommissioned Generation Resources
The following is a list of Decommissioned Generation Resources dating back to 2004. A Decommissioned Generation Resource is a Generation Resource for which a Resource Entity has submitted a Notification of Suspension of Operations (NSO) or a Notification of Change of Generation Resource Designation (NCGRD), for which ERCOT has declined to execute a Reliability Must-Run (RMR) Agreement, and which has been decommissioned and permanently retired. The information in the table below was provided in the NSO and/or NCGRD forms for each decommissioned resource. When a unit’s NSO/NCGRD form did not list a capacity, the capacity was taken from past CDR reports. Except for rare exceptions, the list does not include any planned unit retirements listed in the Capacities tabs or other sections of the report. Unit codes that are listed as retired in this tab but also appear in the operational sections of the CDR represent units that were repowered; for example, retired gas turbines may be repowered into new combined cycle plants. Treatment of Private Use Network (PUN) generators: PUN generators are included, but were not individually listed in past CDR reports when operational. PUN generators with zero MW capacity listed indicate that the unit was not available during the summer. Treatment of Settlement Only Generators (SOGs): The list does not include decommissioned or retired SOGs because there is currently no NSO/NCGRD process for this generator type.
Unit Name | Unit Code | Fuel | Summer Capacity (MW) | Retirement Effective Date
TIDAL ROAD COGEN | TJG401 | GAS-CC | 100 | 2004-02-01
HOLLY STREET 1 | HOLLY_HPG1 | GAS-ST | 102.5 | 2004-12-31
HOLLY STREET 2 | HOLLY_HPG2 | GAS-ST | 102.5 | 2004-12-31
C.E. NEWMAN 1 | NEWMAN_NEWMA_1 | GAS-ST | 8 | 2005-05-01
C.E. NEWMAN 2 | NEWMAN_NEWMA_2 | GAS-ST | 8 | 2005-05-01
C.E. NEWMAN 3 | NEWMAN_NEWMA_3 | GAS-ST | 18 | 2005-05-01
C.E. NEWMAN 4 | NEWMAN_NEWMA_4 | GAS-ST | 17 | 2005-05-01
SPENCER 3 | SPNCER_SPNCE_3 | GAS-ST | 27 | 2005-05-01
CHANEL 2 | CHLGT-2 | GAS-GT | 0 | 2005-07-20
VICTORIA 4 | VICTORIA_VICTORG4 | GAS-ST | 69 | 2005-10-09
VICTORIA 5 | VICTORIA_VICTORG5 | GAS-ST | 172 | 2005-10-09
VICTORIA 6 | VICTORIA_VICTORG6 | GAS-ST | 250 | 2005-10-09
CHANEL 1 | CHLGT-1 | GAS-GT | 0 | 2006-01-02
W B TUTTLE 2 | TUTTLE_WBT2G2 | GAS-ST | 100 | 2007-01-25
FT. PHANTOM 1 | FTPP_G1 | GAS-ST | 158 | 2008-02-14
FT. PHANTOM 2 | FTPP_G2 | GAS-ST | 202 | 2008-02-14
HANDLEY 1 | HLSES_UNIT1 | GAS-ST | 42 | 2009-03-01
HANDLEY 2 | HLSES_UNIT2 | GAS-ST | 80 | 2009-03-01
MOUNTAIN CREEK 2 | MCSES_UNIT2 | GAS-ST | 33 | 2009-03-01
MOUNTAIN CREEK 3 | MCSES_UNIT3 | GAS-ST | 70 | 2009-03-01
SAM BERTRON T1 | SRB_SRBGT_1 | GAS-GT | 20 | 2009-04-10
NORTH LAKE 1 | NLSES_UNIT1 | GAS-ST | 163 | 2009-05-05
NORTH LAKE 2 | NLSES_UNIT2 | GAS-ST | 175 | 2009-05-05
NORTH LAKE 3 | NLSES_UNIT3 | GAS-ST | 312 | 2009-05-05
MORGAN CREEK 5 | MGSES_UNIT5 | GAS-ST | 180 | 2009-05-06
MORGAN CREEK 6 | MGSES_UNIT6 | GAS-ST | 518 | 2009-05-06
PERMIAN BASIN 5 | PB5SES_UNIT5 | GAS-ST | 112 | 2009-05-06
SWEETWATER GENERATION PLANT 1 | SWCOG_CT1 | GAS-CC | 29 | 2009-05-06
SWEETWATER GENERATION PLANT 2 | SWCOG_CT2 | GAS-CC | 69 | 2009-05-06
SWEETWATER GENERATION PLANT 3 | SWCOG_CT3 | GAS-CC | 69 | 2009-05-06
SWEETWATER GENERATION PLANT 4 | SWCOG_UNIT1 | GAS-CC | 61 | 2009-05-06
TRADINGHOUSE 1 | THSES_UNIT1 | GAS-ST | 563 | 2009-05-06
P H ROBINSON 1 | PHR_PHR_G1 | GAS-ST | 444 | 2009-09-30
P H ROBINSON 2 | PHR_PHR_G2A | GAS-ST | 459 | 2009-09-30
P H ROBINSON 3 | PHR_PHR_G3 | GAS-ST | 551 | 2009-09-30
P H ROBINSON 4 | PHR_PHR_G4 | GAS-ST | 733 | 2009-09-30
NORTH CARBIDE G4 | NCARBIDE_NCARBIG4 | GAS-GT | 0 | 2010-01-10
COASTAL STATES (W) 1 | COASTAL_COASTAG1 | GAS-GT | 0 | 2010-06-30
COASTAL STATES (W) 2 | COASTAL_COASTAG2 | GAS-GT | 0 | 2010-06-30
COLLIN 1 | CNSES_UNIT1 | GAS-ST | 147 | 2010-12-31
EAGLE MOUNTAIN 1 | EMSES_UNIT1 | GAS-ST | 118 | 2010-12-31
EAGLE MOUNTAIN 2 | EMSES_UNIT2 | GAS-ST | 100 | 2010-12-31
EAGLE MOUNTAIN 3 | EMSES_UNIT3 | GAS-ST | 390 | 2010-12-31
TRADINGHOUSE 2 | THSES_UNIT2 | GAS-ST | 787 | 2010-12-31
DOW G62 | DOWGEN_DOW_G62 | GAS-GT | 0 | 2011-02-01
C E NEWMAN 5 | NEWMAN_NEWMA_5 | GAS-ST | 37.5 | 2011-02-14
W B TUTTLE 1 | TUTTLE_WBT1G1 | GAS-ST | 60 | 2011-03-01
W B TUTTLE 3 | TUTTLE_WBT3G3 | GAS-ST | 100 | 2011-03-01
W B TUTTLE 4 | TUTTLE_WBT4G4 | GAS-ST | 160 | 2011-03-01
RAYBURN 3 | RAYBURN_RAYBURG3 | GAS-ST | 24 | 2012-06-01
LEON CREEK 3 | LEON_CRK_LCP3G3 | GAS-ST | 70 | 2013-04-01
LEON CREEK 4 | LEON_CRK_LCP4G4 | GAS-ST | 95 | 2013-04-01
THOMAS C FERGUSON 1 | FERGUS_FERGUSG1 | GAS-ST | 354 | 2013-09-30
AES DEEPWATER | APD_APD_PS1 | STORAGE | 1 | 2013-12-27
ATKINS CTG 3 | ATKINS_ATKINSG3 | GAS-ST | 12 | 2014-06-01
ATKINS CTG 4 | ATKINS_ATKINSG4 | GAS-ST | 22 | 2014-06-01
ATKINS CTG 5 | ATKINS_ATKINSG5 | GAS-ST | 25 | 2014-06-01
ATKINS CTG 6 | ATKINS_ATKINSG6 | GAS-ST | 50 | 2014-06-01
APPLIED ENERGY | APD_APD_G1 | COAL | 138 | 2014-07-23
DELAWARE MOUNTAIN WIND FARM | KUNITZ_WIND_NWP | WIND-O | 28.5 | 2014-08-07
KUNITZ WIND | KUNITZ_WIND_LGE | WIND-O | 39.8 | 2014-08-07
NORTH TEXAS CTG 1 | NTX_NTX_1 | GAS-ST | 18 | 2015-06-03
NORTH TEXAS CTG 2 | NTX_NTX_2 | GAS-ST | 18 | 2015-06-03
NORTH TEXAS CTG 3 | NTX_NTX_3 | GAS-ST | 39.5 | 2015-06-03
PERMIAN BASIN SES U6 | PBSES_UNIT6 | GAS-ST | 515 | 2015-06-03
VALLEY SES U1 | VLSES_UNIT1 | GAS-ST | 174 | 2015-06-03
VALLEY SES U2 | VLSES_UNIT2 | GAS-ST | 520 | 2015-06-03
VALLEY SES U3 | VLSES_UNIT3 | GAS-ST | 375 | 2015-06-03
SILAS RAY CTG 5 | SILASRAY_SILAS_5 | GAS-ST | 10 | 2016-04-06
FRONTERA GENERATION CTG 1 | FRONTERA_FRONTEG1 | GAS-CC | 170 | 2016-09-30
FRONTERA GENERATION CTG 2 | FRONTERA_FRONTEG2 | GAS-CC | 170 | 2016-09-30
FRONTERA GENERATION STG | FRONTERA_FRONTEG3 | GAS-CC | 184 | 2016-09-30
CAPITAL COGEN GT 102 | CTL_GT_102 | GAS-CC | 75.35 | 2017-02-01
CAPITAL COGEN GT 103 | CTL_GT_103 | GAS-CC | 75.35 | 2017-02-01
CAPITAL COGEN GT 104 | CTL_GT_104 | GAS-CC | 75.35 | 2017-02-01
CAPITAL COGEN ST 101 | CTL_ST_101 | GAS-CC | 43.85 | 2017-02-01
CAPITAL COGEN ST 102 | CTL_ST_102 | GAS-CC | 10.1 | 2017-02-01
LUFKIN BIOMASS | LFBIO_UNIT1 | BIOMASS | 45 | 2017-02-06
PEARSALL STG U1 | PEARSALL_PEARS_1 | GAS-ST | 19 | 2017-08-01
PEARSALL STG U2 | PEARSALL_PEARS_2 | GAS-ST | 22 | 2017-08-01
PEARSALL STG U3 | PEARSALL_PEARS_3 | GAS-ST | 20 | 2017-08-01
UNION CARBIDE COGEN | UCC_COGN_UCC_C_1 | GAS-GT | 0 | 2017-09-29
GREENS BAYOU STG U5 | GBY_GBY_5 | GAS-ST | 371 | 2017-12-31
S R BERTRON CTG 2 | SRB_SRBGT_2 | GAS-GT | 13 | 2017-12-31
S R BERTRON U3 | SRB_SRB_G3 | GAS-ST | 211 | 2017-12-31
S R BERTRON U4 | SRB_SRB_G4 | GAS-ST | 211 | 2017-12-31
MONTICELLO U1 | MNSES_UNIT1 | COAL | 535 | 2018-01-04
MONTICELLO U2 | MNSES_UNIT2 | COAL | 535 | 2018-01-04
MONTICELLO U3 | MNSES_UNIT3 | COAL | 795 | 2018-01-04
SANDOW U4 | SDSES_UNIT4 | COAL | 600 | 2018-01-11
SANDOW U5 | SD5SES_UNIT5 | COAL | 600 | 2018-01-11
BIG BROWN U1 | BBSES_UNIT1 | COAL | 606 | 2018-02-12
BIG BROWN U2 | BBSES_UNIT2 | COAL | 602 | 2018-02-12
S R BERTRON U1 | SRB_SRB_G1 | GAS-ST | 112 | 2019-01-23
S R BERTRON U2 | SRB_SRB_G2 | GAS-ST | 168 | 2019-01-23
GIBBONS CREEK U1 | GIBCRK_GIB_CRG1 | COAL | 470 | 2019-10-23
WEST TEXAS WIND | SW_MESA_SW_MESA | WIND-O | 80.25 | 2019-11-15
OKLAUNION U1 | OKLA_OKLA_G1 | COAL | 650 | 2020-10-01
DECKER CREEK STG 1 | DECKER_DPG1 | GAS-ST | 315 | 2020-10-31
SHERBINO 1 WIND | KEO_KEO_SM1 | WIND-O | 150 | 2021-02-01
SAM RAYBURN POWER CTG 1 | RAYBURN_RAYBURG1 | GAS-GT | 11 | 2021-02-28
SAM RAYBURN POWER CTG 2 | RAYBURN_RAYBURG2 | GAS-GT | 11 | 2021-02-28
SNYDER WIND | ENAS_ENA1 | WIND-O | 63 | 2021-06-01
DECKER CREEK STG 2 | DECKER_DPG2 | GAS-ST | 420 | 2022-03-31
OCI ALAMO 1 (ASTRO) | OCI_ALM1_ASTRO1 | STORAGE | 1 | 2022-11-17