## Slide 1
NPRR1171 – Reliability Risk Scenarios
Jeff Billo
OWG
May 18, 2023

## Slide 2: Background
Ancillary Service Products
Non-Spin Reserve Service (NSRS)
  Capacity that can be started in 30 minutes to cover forecast errors, forced outages or ramps and replace deployed reserves until additional resources can be committed.
Responsive Reserve Service (RRS)
  Reserved capacity that is procured to respond to low frequency events typically triggered by generating unit trips.
Regulation Service (Reg)
  Reserved capacity that is deployed every 4 seconds to balance supply and demand and maintain frequency close to 60Hz between 5-minute SCED runs.
ERCOT Contingency Reserve Service (ECRS) – (deploys Summer 2023)
  Capacity that can be started in 10 minutes to cover forecast errors or ramps and replace deployed reserves.

## Slide 3: Risk Assessment
Resources on the distribution system that are connected to circuits subject to Load shed would be unable to provide energy or Ancillary Services to the system during those events.
  Note: DGRs/DESRs that are on circuits that are not subject to Load shed (e.g. if connected to a dedicated feeder) have no Ancillary Services restrictions.
These slides explore scenarios and their correlated risk to reliability when distribution circuits may be disconnected from the ERCOT system and the subsequent risk to reliability.

## Slide 4: Scenario 1: EEA3 Firm Load Shed
AS | Description of Risk of AS being provided by Resources on distribution Load shed circuits | Risk Level
Non-Spin | As system enters scarcity conditions (low PRC), ERCOT will deploy Non-Spin before entering EEA, if time allows. TOs should have visibility with regards to real-time net Load of Load shed circuits. Some risk that TOs do not take this into account and do not shed enough net Load, which would lead ERCOT to issue further Load shed instructions. Non-Spin may be used for restoring Load that was shed, hence, if Non-Spin Resources are disconnected it may delay full restoration. | Medium
RRS | RRS-PFR and RRS-UFR (EEA2) will be deployed prior to EEA3 Load shed, if time allows. However, ERCOT will maintain a minimum amount of PRC from PFR and FFR Resources during EEA3 Load shed to protect against a large unit trip. Hence, RRS-PFR and RRS-FFR Resources are critical to maintaining reliability during EEA3 Load shed. | High
Reg-Up | Frequency is expected to be below 60 Hz going into EEA3 conditions and Reg-Up Resources will be fully deployed to attempt to raise frequency back to 60 Hz. Hence, Reg-Up Resources are critical for frequency control. | High
Reg-Down | Frequency is expected to be below 60 Hz going into EEA3 conditions and Reg-Down will not be deployed. If frequency climbs above 60 Hz, all Resources online are required to provide down-PFR, which will prevent frequency from spiking too high. | Low
Risk Mitigation: Do not allow Resources on distribution Load shed circuits to provide RRS-PFR or Reg-Up; allow limited provision of Non-Spin.

## Slide 5: Scenario 2: UFLS – Sudden Event
AS | Description of Risk of AS being provided by Resources on distribution Load shed circuits | Risk Level
Non-Spin | Non-Spin may or may not be deployed based on system conditions just prior to the event, however, Non-Spin is not counted upon to restore frequency in UFLS-related studies. Some risk that Non-Spin is deployed and that distribution Resources providing Non-Spin were not accounted for in TO’s UFLS planning, leading to tripping of less net Load than expected. Non-Spin may be used for restoring Load that was shed, hence, if Non-Spin Resources are disconnected it may delay full restoration. | Medium
RRS | RRS-UFR is expected to trip (59.7 Hz) prior to UFLS relay action (59.3 Hz). RRS-PFR and RRS-FFR are critical to arresting the frequency decline and restoring frequency. | High
Reg-Up | Reg-Up Resources are critical for frequency control and attempting to restore frequency to 60 Hz during a UFLS event. | High
Reg-Down | By definition, UFLS events occur during low-frequency conditions. If frequency climbs above 60 Hz, all Resources online are required to provide down-PFR, which will prevent frequency from spiking too high. | Low
Risk Mitigation: Do not allow Resources on distribution Load shed circuits to provide RRS-PFR or Reg-Up; allow limited provision of Non-Spin.

## Slide 6: Scenario 3: UVLS
AS | Description of Risk of AS being provided by Resources on distribution Load shed circuits | Risk Level
Non-Spin | Non-Spin may or may not be deployed based on system conditions just prior to the event, however, Non-Spin is not counted upon to restore voltage in UVLS-related studies. | Low
RRS | If the UVLS event is part of a larger, system-wide event or cascades to a larger system-wide event, RRS Resources will be needed to restore frequency. | Medium
Reg-Up | If the UVLS event is part of a larger, system-wide event or cascades to a larger system-wide event, Reg-Up Resources may be needed to maintain frequency control. | Medium
Reg-Down | If the UVLS event is part of a larger, system-wide event or cascades to a larger system-wide event, Reg-Down Resources may be needed to maintain frequency control, though all Resources online are required to provide down-PFR, which will prevent frequency from spiking too high. | Low
Risk Mitigation: Do not allow Resources on distribution Load shed circuits to provide RRS-PFR or Reg-Up.

## Slide 7: Scenario 4: Local Load Shed for Transmission Security
AS | Description of Risk of AS being provided by Resources on distribution Load shed circuits | Risk Level
Non-Spin | Local Load shed to maintain transmission security is unlikely to impact a large amount of MWs from Resources providing Ancillary Services. | Low
RRS |  | Low
Reg-Up |  | Low
Reg-Down |  | Low
Risk Mitigation: N/A

## Slide 8: Summary
Reg-Up and RRS are critical to maintaining frequency stability during conditions when distribution circuits may be disconnected as part of a Load shed event. RRS is the primary mechanism for ensuring ERCOT has sufficient Physically Responsive Capacity (PRC) to respond to any event.
Non-Spin is primarily procured to address reserve margin risks associated with intra-day forecast errors and intra-day forced outages, but may be used to recover deployed RRS and Reg-Up.
Reg-Down is used to mitigate high frequency, but events where distribution circuits are disconnected are most likely to occur during low frequency conditions.
ERCOT will consider ECRS risks after ECRS implementation.
Do not allow RRS or Reg-Up from Resources that are on distribution circuits that may be disconnected
Limit Non-Spin from Resources that are on distribution circuits that may be disconnected
No limit for Reg-Down from Resources that are on distribution circuits that may be disconnected