## Slide 1
MTLF
Winter Storm Elliott Review
Calvin Opheim
Load Forecasting & Analysis
SAWG
5/19/2023

## Slide 2: Agenda
MTLF Model Review
Software Upgrade
Winter Storm Elliott
Corrective Action Plan

## Slide 3
MTLF Models

## Slide 4: MTLF Models
Two Independent Forecasting Systems
  Itron (creates the E, E1, E2, and E3 forecasts)
  GE (creates the A3, A6, and M forecasts)
  Residing on separate computer systems provides redundancy in case one system is unavailable

## Slide 5: MTLF Models
E, E1, E2, E3
  Based on neural network and linear regression models with a separate model for each hour
  49 weather stations (expanded set)
  Can easily switch between any available weather forecast provider

## Slide 6: MTLF Models
A3 Notes
  Uses recent history to update the model coefficients
  Limited to a single weather forecast provider
  Requires coding changes to switch to alternative weather forecast
  Provides a reasonable backup to the Itron models during the normal range of weather conditions

## Slide 7: MTLF Models
A6 Notes
  Uses recent history to update the model coefficients
  Only uses one weather station per weather zone
  Limited to a single weather forecast provider
  Requires coding changes to switch to alternative weather forecast
  Provides a reasonable backup to the Itron models during the normal range of weather conditions

## Slide 8: MTLF Models
M Notes
  The weighted average of the 6 other models
  Historically has shown to be the most accurate Day Ahead forecast
  Provides a good benchmark for other models
For more details
  https://www.ercot.com/calendar/04042022-SAWG-Meeting-by-Webex
  https://www.ercot.com/calendar/06242022-SAWG-Meeting-by-Webex

## Slide 9: MTLF Available Weather Forecasts
The following weather forecasts are available for the Itron models:
  European Model (Euro)
  Global Forecast System (GFS)
  Global Forecast System Ensemble (GENS)
  North American Model (NAM)
  3 vendor models
ERCOT was the first ISO that incorporated raw weather forecasts into their operational load forecasts
ERCOT is actively working on increasing the number of raw weather forecasts to those mentioned above
  Particularly of interest are the Canadian and HRRR models

## Slide 10
Software Upgrade

## Slide 11: Software Upgrade and Impacts
A software upgrade for Itron went live on 12/6/2022
Holiday configuration was not adequately tested
  Resulted in holidays being significantly under-forecasted
  Rendered E, E1, E2, and E3 unusable for most of the week
All enhancements/improvements previously implemented in the Itron created MTLFs were unavailable because these forecasts were unusable
  Ability to select from any available raw weather model (like Euro, GFS, NAM)
  Ability to apply error correction
  Extreme weather forecasting improvements

## Slide 12: Software Upgrade and Impacts
Chart: ERCOT Forecasts for 12/23 created 12/17
A3 | 57628.5195 | 56905.1172 | 56610.9375 | 57059.6172 | 57875.0859 | 59866.4844 | 62824.8438 | 65335.9102 | 67237.8984 | 68318.5547 | 67902.9688 | 66703.6562 | 64484.457 | 62797.6211 | 60537.9844 | 59329.3633 | 59073.0625 | 60677.8438 | 62419.7422 | 62679.8164 | 62338.0508 | 61831.0117 | 60136.9844 | 58353.7969
A6 | 56957.5586 | 56071.1211 | 55530.0117 | 55877.1641 | 56549.5078 | 58858.1797 | 62179.0742 | 64290.2266 | 65134.4141 | 66090.2812 | 66198.8281 | 65449.4883 | 63363.5312 | 61786.1641 | 60102.4062 | 59393.7695 | 59058.9453 | 60516.4883 | 61555.4141 | 61380.1172 | 60840.5117 | 59717.4688 | 58219.8867 | 56563.1445
E | 50198.1016 | 49148.5 | 48065.8008 | 48036.8008 | 48081.3008 | 48306.3008 | 48494.6992 | 48503.1016 | 48250.3008 | 48096.3984 | 47957.3984 | 47883.1992 | 47858.5 | 47525.6992 | 47267.6992 | 47477.1016 | 47111.1016 | 46932.8008 | 46839.5 | 47186.5 | 47468.3008 | 47749.3008 | 46989.3984 | 46400.8984
E1 | 51224.8008 | 49690.5 | 48125.8008 | 48025.3008 | 48130 | 48134.1016 | 48321.1016 | 48403 | 48302.8008 | 48191.5 | 48249.8984 | 48226.6016 | 48195.6992 | 48066.6016 | 48041.3008 | 48151.3984 | 47907.6016 | 47786.3008 | 47753.3984 | 48000.6016 | 48114.5 | 48297.1992 | 47575.1992 | 47009
E2 | 50820.3008 | 49289.1016 | 47727.6992 | 47627.8008 | 47732.1992 | 47735.5 | 47919.1992 | 48001.6016 | 47904.3984 | 47794.3984 | 47852.3008 | 47825.6016 | 47793.1992 | 47662.3008 | 47634.6992 | 47742.3008 | 47498.6992 | 47377.8984 | 47344.8008 | 47591 | 47704.8008 | 47887.6016 | 47172.1992 | 46612.8984
E3 | 48764.8984 | 47837.1016 | 46910.6992 | 46893.5 | 47138.8984 | 47300 | 47646.6016 | 47998.3984 | 48129.5 | 48123.8984 | 48155.3984 | 47994.8008 | 47684.3008 | 47240 | 46926 | 46833.5 | 46535 | 46555.6992 | 46790.6016 | 47153.3008 | 47338.1992 | 47603.6016 | 46708.3008 | 45968.3984
Actual | 70982.2422 | 70528.7812 | 70171.4062 | 70325.4219 | 70852.2344 | 71776.9688 | 72992.125 | 73962.6016 | 73910.4609 | 73687.8984 | 72242.3125 | 70034.1328 | 67487.0781 | 65539.2266 | 63850.8125 | 63395.7031 | 64255.1758 | 66505.4922 | 67948.1875 | 67977.6875 | 67856.9141 | 67342.5078 | 66338.4531 | 64822.7148

## Slide 13
Winter Storm Elliott

## Slide 14: Weather Forecasts
Chart: DFW Forecasts for 12/23 @0800
| 44909 | 44910 | 44911 | 44912 | 44913 | 44914 | 44915 | 44916 | 44917 | 44918
NAM | 25 | 21 | 19 | 18 | 19 | 11 | 11 | 9 | 10 | 9
GENS | 24 | 21 | 21 | 17 | 11 | 10 | 14 | 14 | 14 | 13
MDA | 21 | 21 | 19 | 18 | 18 | 12 | 14 | 14 | 13 | 12
Actual | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
NAM was the preferred forecast but was unavailable to the A3 and A6 forecasts

## Slide 15: Weather Forecasts
Chart: IAM Forecasts for 12/23 @0800
| 44909 | 44910 | 44911 | 44912 | 44913 | 44914 | 44915 | 44916 | 44917 | 44918
NAM | 30 | 28 | 24 | 23 | 24 | 15 | 18 | 20 | 15 | 18
GENS | 32 | 28 | 28 | 25 | 18 | 18 | 20 | 19 | 19 | 19
MDA | 30 | 28 | 24 | 23 | 24 | 18 | 19 | 19 | 18 | 16
Actual | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
NAM was the preferred forecast but was unavailable to the A3 and A6 forecasts

## Slide 16: Weather Forecasts
Chart: AUS Forecasts for 12/23 @0800
| 44909 | 44910 | 44911 | 44912 | 44913 | 44914 | 44915 | 44916 | 44917 | 44918
NAM | 24 | 23 | 22 | 20 | 18 | 16 | 17 | 14 | 16 | 17
GENS | 28 | 26 | 25 | 23 | 16 | 16 | 18 | 17 | 17 | 17
MDA | 22 | 24 | 22 | 20 | 18 | 15 | 17 | 17 | 17 | 14
Actual | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
NAM was the preferred forecast but was unavailable to the A3 and A6 forecasts

## Slide 17: Load Forecasts
Chart: Selected Forecast Peak Demand for 12/23 @0900
| 44918.334722222222 | 44917.334722222222 | 44916.334722222222 | 44915.334722222222 | 44914.334722222222 | 44913.334722222222 | 44912.334722222222
A3 | 70898.2109 | 67574.2656 | 67943.2109 | 69313.125 | 69324.3047 | 67237.8984
Actual | 73910.4609
Forecasts were created at 8:02 am each day

## Slide 18: Forecast Error Sources During Elliott
Using the A3 model resulted in an increase in forecast errors
  Ramifications of using A3
    Based on MDA’s weather forecast instead of the weather forecast (NAM) recommended by our meteorologists
    Seeing that the NAM forecast was better than MDA’s forecast in the days leading up to 12/23, the result was higher forecast errors than if the Itron models had been operational
    Limited features/flexibility as compared to the Itron models
Limited historical data on cold weather events
  Uri data after 2/14/21 was of no value due to system outages
Weather forecast error
Load forecasting model error

## Slide 19: ERCOT Load-Weighted Temperatures

## Slide 20
Corrective Action Plan

## Slide 21: Corrective Actions Currently Planned
Objective 1 – Reduce forecast errors from the alternative load forecasting source (currently the GE models A3, A6)
  Add an external load forecast that will complement ERCOT’s Itron models
  Must have the ability to seamlessly switch weather forecasts
Objective 2 – Develop an innovative process for developing extreme cold weather forecasts
  Develop a process for creating specialized extreme cold weather models
  Based on a robust set of historical cold weather data

## Slide 22: Corrective Actions Currently Planned
Objective 3 – Reduce weather forecast error
  Add more raw weather forecasting models
    If the Canadian forecast was available, the day(s) ahead forecast would have been better
    If the HRRR forecast was available, the intraday forecast would have been better
Objective 4 – Improve Itron software upgrade testing process
  Create a more robust testing environment
  Update testing procedures to include holidays and other outlier phenomena

## Slide 23: Questions?