| PGRR Number | 103 | PGRR Title | Establish Time Limit for Generator Commissioning Following Approval to Synchronize |
| --- | --- | --- | --- |

| Date | March 8, 2023 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Blair McGinnis |
| E-mail Address | bmcginnis@lpandl.com |
| Company | Lubbock Power & Light |
| Phone Number | 806-775-3559 |
| Cell Number | 806-775-3559 |
| Market Segment | Independent Generator |

Comments

Lubbock Power & Light (LP&L) believes resource owners understand the importance of progressing through the ERCOT resource commissioning process and make reasonable efforts to satisfy requirements.  LP&L proposes the following revisions:

- Increase the proposed 180 day commissioning window between initial synchronization and commercial operation to 365 days.

- PGRR 103 effective as of October1, 2023.  The funding mechanism for municipally owned LP&L is tied to a budget process starting Oct 1st of each year.

- Allows for good cause exceptions to the 365 days.

Revised Cover Page Language

| Revision Description | This Planning Guide Revision Request (PGRR) requires an Interconnecting Entity to complete all conditions for commercial operation of a Generation Resource or Energy Storage Resource (ESR) within 365 days of receiving approval for Initial Synchronization above 20 MVA from ERCOT. |
| --- | --- |
| Business Case | As of December 20, 2022, 53 projects representing more than 11,180 MW of capacity in Generator Interconnection or Modification (GIM) received approval for Initial Synchronization under Part 2 (or Part 2b, where applicable) of the ERCOT New Generator Commissioning Checklist more than 180 days ago, and still have not received their Part 3 approval required for full commercial operation. Of these, 36 projects representing 8,151 MW received approval for Initial Synchronization under Part 2 (or 2b) more than one year ago, and 18 projects representing 3,137 MW received approval for Initial Synchronization more than two years ago. Delays in completing the Resource commissioning process create a reliability risk because, in aggregate, there could be a significant amount of generation on the ERCOT System that is not providing system support services. Specifically, any Generation Resource or ESR whose Qualified Scheduling Entity (QSE) has not requested approval of Part 3 of the ERCOT New Generator Commissioning Checklist for the Resource may not have an operational Automatic Voltage Regulator (AVR), Power System Stabilizer (PSS), or turbine speed governor, and may not have demonstrated the Resource’s Reactive Power capability through testing. To alleviate this reliability risk, this PGRR limits the time between Initial Synchronization and commercial operation by requiring Generation Resources and ESRs to complete all conditions required for commissioning and to require submittal of Part 3 of the ERCOT New Generator Commissioning Checklist within 365 days of receiving ERCOT’s approval for Initial Synchronization. |

Revised Proposed Guide Language

5.5	Generator Commissioning and Continuing Operations

(1)	For each interconnecting Generation Resource or Energy Storage Resource (ESR), each Interconnecting Entity (IE) shall meet the conditions established by ERCOT before proceeding to Initial Energization, Initial Synchronization, and commercial operations.  These conditions may require proof of meeting applicable ERCOT requirements, which may include, but are not limited to, reactive capability, Voltage Ride-Through (VRT) standards, dynamic model template submission, Automatic Voltage Regulator (AVR), Primary Frequency Response (PFR), Power System Stabilizer (PSS), Subsynchronous Resonance (SSR) models, and telemetry.

(2)	Within 365 days of receiving ERCOT’s approval for Initial Synchronization above 20 MVA of a new or repowered Generation Resource or ESR, a Resource Entity shall ensure the Resource meets the conditions established by ERCOT for commercial operations and shall submit a request to ERCOT to commission the Resource.

In the event a Generation Resource or ESR will be unable to complete all necessary construction and required testing to commence commercial operations and connect reliably to the ERCOT System within the 365 days, the Generation Resource or ESR may request a good cause exception with sufficient detail, and shall notify ERCOT prior to the planned commercial operation date and provide ERCOT with an updated commercial operation date that the Generation Resource or ESR can reasonably expect to commence operations in a reliable manner.

(3)	No later than 30 days following the Resource Commissioning Date, the Resource Entity shall submit updates to the resource dynamic planning models based on “as-built” or “as-tested” data and provide a plant verification report as required by paragraph (5)(b) of Section 6.2, Dynamics Model Development.  Pursuant to paragraph (5)(c) of Section 6.2, any necessary model updates shall be accompanied with model quality tests.

(4)	During continuing operations:

(a)	Pursuant to paragraph (5)(c) of Section 6.2, any necessary model updates shall be accompanied by model quality tests.

(b)	The Resource Entity shall provide ERCOT with a plant verification report as required by paragraph (5)(b) of Section 6.2 at the following times:

(i)	No later than 30 days after implementing a settings change as required by paragraph (7) of Section 6.2;

(ii)	No earlier than 12 months and no later than 24 months following the later of the Resource Commissioning Date or March 1, 2021; and

(iii)	A minimum of every ten years.