## Slide 1
Dynamic Predicted Solar Ramp Rate in GTBD Calculation
ERCOT
Operations Planning
PDCWG | June 21st, 2023

## Slide 2: Overview – Static Threshold of Predicated Solar Ramp Rate (PSRR) in GTBD
ERCOT added PSRR in GTBD calculation with a threshold of 10MW/min on 6/1/2021 .
Over the last 2 years, ERCOT has increased this threshold to 40MW/min.
Chart: PSRR Threshold in GTBD
| 44348 | 44349 | 44441 | 44769
 | 10 | 20 | 30 | 40

## Slide 3: Actual Solar Ramp Rate (4/1/2023-6/1/2023)
Chart: HE
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Decoy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Q1 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 213.6841 | 238.6986 | 210.3141 | 196.8662 | 193.9517 | 186.5091 | 181.7987 | 176.5488 | 171.5901 | 164.4271 | 156.9651 | 125.8587 | 116.1827 | 188.5032 | 200 | 200 | 200
Med-Q1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1361 | 27.7653 | 15.5306 | 16.6517 | 14.6101 | 16.3038 | 19.6151 | 20.7976 | 19.9846 | 24.7557 | 22.7264 | 25.929 | 23.8258 | 10.0407 | 0 | 0 | 0
Q3-Med | 0 | 0 | 0 | 0 | 0 | 0 | 0.45633 | 32.3611 | 26.6995 | 18.0602 | 19.1319 | 19.1678 | 17.6624 | 17.0483 | 20.2856 | 21.5714 | 20.8295 | 23.8895 | 22.9039 | 20.9176 | 1.456 | 0 | 0 | 0
Mean | 0 | 0 | 0 | 0 | -0.00027951 | -0.003427 | 1.7295 | 44.1032 | 66.5881 | 27.5734 | 15.7188 | 9.9399 | 3.2724 | -0.13112 | -3.4757 | -8.9919 | -14.3136 | -20.8241 | -50.0504 | -62.5697 | -8.4159 | 0 | 0 | 0
Sunrise
Sunset

## Slide 4: Overview – Dynamic PSRR Threshold in GTBD
Chart: Dynamic PSRR Threshold
 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 100 | 100 | 100 | 0 | 0 | 0
ERCOT started to apply a dynamic PSRR threshold in GTBD calculation on 6/12/2023
PSRR thresholds change with 4 pre-defined day periods - Night, Sunrise, Sunset and Other
ERCOT started with a threshold of 80MW/min for Sunrise and Sunset periods on 6/12 and subsequently increased it to 100MW/min on 6/15
ERCOT plans to update the thresholds and the definition of day periods seasonally* (4 times a year)
Night
* Seasons will be defined by shift in solar ramping patterns

## Slide 5: % Intervals* Benefitted from Increased Threshold
Chart: 6/12/2023-6/19/2023
| Sunrise | Sunset
 | 0.38393 | 0.49206
*Intervals benefited :
Intervals with | PSRR | > 40 MW/min, when | actual solar ramp | >40MW/min

## Slide 6: Appendix

## Slide 7: Seasonal Update
Winter: Nov (Post DST) - Feb
Spring: Mar (Pre DST)
Summer: Mar (Post DST) - Aug
Fall: Sep - Nov(Pre DST)
Night | 0
Sunrise | 1
Other | 3
Sunset | 2
Summer
Fall
Winter
Winter
Spring
Mock-Up Table |  |  |  | 
 | Winter | Spring | Summer | Fall
Night | 0 | 0 | 0 | 0
Sunrise | 60 | 70 | 74 | 62
Other | 40 | 40 | 40 | 40
Sunset | 68 | 80 | 84 | 72
Each season has its own definition of 4 different periods of a day (Update if needed)
Four different caps per season
  Night : 0 MW/min
  Sunrise: Updated seasonally based on Installed Capacity Change
  Other: 40MW/min (current Cap)
  Sunset :Updated seasonally based on Installed Capacity

## Slide 8: Actual Solar Ramp Boxplot (March 2022-March 2023)