## Slide 1
Impact Analysis: NOGRR215
Freddy Garcia
Mgr. Ops Analysis and Improvement
ROS
July 2023

## Slide 2: NOGRR215 Impact Analysis
EMS enhancement to notify operator of a constraints greater than 125% Cascading Criteria with RAS action
  Currently in RTCA/TCM when a RAS resolves a constraint, the constraint is not displayed for Operator
  When a RAS does not fully resolve a constraint:
    Currently Operators will see a post contingency post RAS overload
    Constraint with RAS residual overload with highlighting is displayed for Operator Situation Awareness
  RAS resolves post contingency overload greater than or equal to 125% of emergency rating
    Possible failure to operate
    Operator is unaware of a constraint beyond cascading criteria
  Enhancement provides notification similar to above screenshot for operator situational awareness

## Slide 3: NOGRR215 Impact Analysis
Operator and Outage Coordinator notifications
  Forced outage of a RAS monitored or RAS associated element
    RAS monitored element is outaged, plus RAS action to reconfigure topology results in unintended consequences
    Operator will be given an alarm
    Investigate if RAS should be disabled or can remain in service
  Planned outage of a RAS monitored or RAS associated elements
    Outage Coordinator/Engineer will be given alarm if a submitted is Outage related to a RAS
    Similar to above, outage can be evaluated and determination made if RAS should be disabled to accommodate planned outage.
  RAS creates a new constraint
    New Constraint in RTCA is due to RAS trigger.
    Operator/Engineer will be notified

## Slide 4: NOGRR215 Impact Analysis
RAS Review Analysis
  Difficult to Assess all possible impact of RAS on the ERCOT system
  Operations planning studies cannot assess all possible prior outage and contingency pairs
    No way to determine what a Real-Time topology with outages might be seasons into future
  Incorporate N-2 analysis
    RAS review assessment can more accurately reflect a possible Real-Time outage plus contingency scenario.
    RAS reviews can more accurately determine possible negative RAS impact.
      Instability
      Cascading
      Steady State Voltage Collapse
    Be aware of outage plus RAS scenarios to avoid in Real-Time

## Slide 5: NOGRR215 Impact Analysis
DAM and CRR
  Planned outage of a RAS monitored or RAS associated elements
    DAM Operator will be given alarm if an outage is related to a RAS monitored or RAS associated element
    DAM Operator can determine if RAS should be disabled to avoid DAM run divergence
  DAM Operator will have the ability to disable RASs mid run
    Determine that a RAS has led to a DAM run divergence
    DAM Operator can disable RAS and resume DAM solution
    Currently DAM solution must be completely restarted after a solution has diverged
  Implementation of RASs in CRR
    Currently the limits for RAS impacted branches are manually changed to 9999
    Is intensive for multiple RAS
    Develop new tool to automate limit changes for RAS Impacted branches