## Introduction
Notes # | Description | Worsheet Name | Description | Field Name | Visible | Description
1 | This workbook contains illustrative examples to demonstrate how the State of Charge (SOC) requirements proposed with NPRR1186 will be applied in practice. | RegUp | ESR is providing RegUp only | MNOS | Y | (telemetered) Minimum Operating SOC (MWh)
2 | These examples are not exhaustive. These examples are not reflective of how ERCOT systems will be actually designed for NPRR1186. | RRS-PFR | ESR is providing RRS-PFR only | MXOS | Y | (telemetered) Maximum Operating SOC (MWh)
3 | Each worksheet has been setup with an example. Each example assumes a 100 MW/100 MWh Energy Storage Resource (ESR) that is qualified to provide Reg Up, RRS-PFR, ECRS and Non-Spin. Each example demonstrates how SOC available for dispatch and SOC compliance requirements will be calculated over a 3 hour period (in steps of 5-minute granularity, 5-minute is used for simplicity). | ECRS | ESR is providing ECRS only | SOC_t0 | Y | (telemetered) SOC at t0. t0 = start of the example's time horizon, 12:00pm (MWh)
4 | Yellow highlighted rows in the worksheets represent rows that do not have embedded formulas | NonSpin | ESR is providing Non-Spin only | Interval Beginning | Y | Interval beginning time
5 | If Stakeholders have questions with the data in this workbook or desire to see other scenarios, please contact ERCOT. | Reg + RRS | ESR is providing Reg Up and RRS-PFR simultaneously | HSL | Y | (telemetered) High Sustained Limit from ESR-GR (MW)
|  | RRS + ECRS | ESR is providing RRS-PFR and ECRS simultaneously | MPC | Y | (telemetered) Maximum Power Consumption from ESR-CLR (MW), represented as negative value for graphical purposes
|  | ECRS + NonSpin | ESR is providing ECRS and NonSpin simultaneously | RegUp Resp./RRS Resp./ECRS Resp./NonSpin Resp. | Y | (telemetered) RegUp, RRS, ECRS, Non-Spin Responsibility (MW), enterable field no formula
|  |  |  | RegUp Deployed/RRS Sched/ECRS Sched./NonSpin Schedule | Y | (telemetered) RRS, ECRS, Non-Spin Schedule (MW); ESR's portion of RegUp Deployed (MW), enterable field no formula
|  |  |  | HASL-GR Curr. | Y | ESR GR High Ancillary Service Limit, calculated using ESR GR's AS Responsibilities (MW)
|  |  |  | SOCReq1 | N | Step 1 in calculating SOC available for ESR-GR HASL (MWh)
|  |  |  | SOCReq2 | N | Step 2 in calculating SOC available for ESR-GR HASL (MWh)
|  |  |  | SOCReq | N | Final calculated SOC available for ESR-GR HASL (MWh)
Worksheet | Corrections Made on 7172023 |  |  | HASL-GR Post 1186 | Y | Post 1186 ESR GR High Ancillary Service Limit (MW)
ECRS | Updated values in Cell R20 so that BP would be less than or equal to HASL |  |  | HASL-CLR Curr. | Y | ESR CLR High Ancillary Service Limit, calculated using ESR CLR's AS Responsibilities (MW), represented as negative value for graphical purposes
NonSpin | Included “SoCReq-Compliance minus charging credit” trace on graph |  |  | HASL-CLR Post 1186 | Y | Post 1186 ESR CLR High Ancillary Service Limit (MW). Current formula does not account RegDown SOC obligation. Represented as negative value for graphical purposes
ECRS+NonSpin | Updated values in Cells S22 to V22 & AF22 to AG22 so that BP would be less than or equal to HASL |  |  | BP-GR | Y | Base Point for ESR-GR (MW), enterable field no formula
|  |  |  | BP-CLR | Y | Base Point for ESR-CLR (MW), enterable field no formula, represented as negative value for graphical purposes
|  |  |  | Net BP | Y | Net Base Point for ESR derived from BP-GR and BP-CLR.
|  |  |  | Governor Response | Y | Enterable field that may be used to simualte Primary Frequency Response from ESR (MW)
|  |  |  | Net MW | Y | Computed as RegUp Deployed + Net BP + PFR
|  |  |  | SOC | Y | Computed as Previous Interval SOC - Energy depleted/gained in current interval based on Net MW (MWh)
|  |  |  | SOCReq-Compliance | Y | SOC requirement for Compliance (MWh)
|  |  |  | SoCReq-Compliance minus charging credit | N | Computed as SOC requirement for Compliance - energy credit when ESR-CLR BP > 0 (MWh)
chang

## RegUp
MNOS | 0 | [7 empty] | SOC Req Ramp Start |  | 0 |  |  |  | MPC, HASL-CLR, and BP-CLR are represented as negative values for graphical purposes
MXOS | 100 | [13 empty] | Governor Response = 0 indicates that frequency is relatively stable in the interval, resulting in minimal autonomous governor response
SOC_t0 | 100
Hour 1 | Significant deployment during first half hour depletes SOC | [12 empty] | Hour 2 | Significant deployment during first half hour depletes SOC | [11 empty] | Hour 3 | The ESR receives BPs to charge at the top of the hour
| The ESR-CLR starts receiving basepoints halfway through the hour | [13 empty] | The ESR waits until last 15 minutes before the top of the hour to charge | [12 empty] | Although Reg Up deployments prevent the ESR from gaining SOC, the requirement drops due to the charging BP
| The ESR achieves sufficient SOC to cover next hour's responsibility | [13 empty] | The SOC does not fully recover before the top of the hour, but the requirement is reduced due to charging BP | [12 empty] | The CLR continues to obtain charging BPs and eventually restores its SOC for the next hour's obligation
Interval Beginning | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 | 13:00 | 13:00 | 13:05 | 13:10 | 13:15 | 13:20 | 13:25 | 13:30 | 13:35 | 13:40 | 13:45 | 13:50 | 13:55 | 14:00 | 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:00
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MPC | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
RegUp Resp. | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
RegUp Deployed | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HASL-GR Curr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOCReq1 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 0 | 0 | 0 | 0 | 0 | 3.3333 | 0 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 0 | 100
SOCReq2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOCReq | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 0 | 0 | 0 | 0 | 0 | 3.3333 | 100 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 100 | 100
HASL-GR Post 1186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HASL-CLR Curr. | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
HASL-CLR Post 1186 | 0 | -80 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -60 | -5.1159e-13 | -5.1159e-13 | -80 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -60 | -8.5265e-13 | -8.5265e-13 | -8.5265e-13 | -8.5265e-13 | -8.5265e-13 | -8.5265e-13
BP-GR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0
Net BP | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0
Governor Response | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net MW | 80 | 80 | 80 | 80 | 80 | 80 | -20 | -100 | -100 | -100 | -100 | -60 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 | 0 | 0 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0
SOC | 100 | 93.3333 | 86.6667 | 80 | 73.3333 | 66.6667 | 60 | 61.6667 | 70 | 78.3333 | 86.6667 | 95 | 100 | 100 | 93.3333 | 86.6667 | 80 | 73.3333 | 66.6667 | 60 | 53.3333 | 53.3333 | 53.3333 | 53.3333 | 61.6667 | 70 | 70 | 70 | 70 | 70 | 70 | 78.3333 | 86.6667 | 95 | 100 | 100 | 100 | 100 | 100 | 100
SOCReq-Compliance | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 0 | 0 | 0 | 0 | 0 | 3.3333 | 0 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 0 | 100
SoCReq-Compliance minus charging credit | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 0 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 0 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 0 | 100

## RRS-PFR
MNOS | 0 | [7 empty] | SOC Req Ramp Start |  | 0 |  |  |  | MPC, HASL-CLR, and BP-CLR are represented as negative values for graphical purposes
MXOS | 100 | [13 empty] | Governor Response = 0 indicates that frequency is relatively stable in the interval, resulting in minimal autonomous governor response
SOC_t0 | 90
Hour 1 | RRS is not deployed and frequency is stable, resulting in minimal governor response output | [12 empty] | Hour 2 | RRS is not released to SCED | [11 empty] | Hour 3 | RRS is released to SCED and governor response is required due to low frequency
| The ESR-GR may receive BPs as its SOC Req decreases throughout the hour, and these BPs decrease the ESR's SOC | [13 empty] | There is a large unit trip, resulting in governor response for 10 minutes which depletes SOC | [12 empty] | The released RRS allows HASL to rise to the HSL, and the ESR-GR receives large BPs which deplete the SOC
| The ESR-CLR receives a BP to charge and restores the SOC before the top of the next hour | [13 empty] | The ESR-CLR receives a BP to charge and restores the SOC before the top of the next hour | [12 empty] | The ESR-CLR does not receive any BPs before the top of the next hour due to high prices, so 50 MW of RRS Responsibility is traded to another unit
Interval Beginning | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 | 13:00 | 13:00 | 13:05 | 13:10 | 13:15 | 13:20 | 13:25 | 13:30 | 13:35 | 13:40 | 13:45 | 13:50 | 13:55 | 14:00 | 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:00
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MPC | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
RRS Resp. | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 50
RRS Sched. | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 90 | 90 | 90 | 90 | 50 | 50
HASL-GR Curr. | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 10 | 10 | 50 | 50
SOCReq1 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 10 | 15 | 7.5 | 90 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 2.5 | 90 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 7.5 | 50 | 50
SOCReq2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOCReq | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 10 | 15 | 7.5 | 90 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 2.5 | 90 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 7.5 | 50 | 50
HASL-GR Post 1186 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 3.4106e-13 | 3.4106e-13 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 10 | 10 | 50 | 50
HASL-CLR Curr. | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
HASL-CLR Post 1186 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
BP-GR | 0 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 90 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net BP | 0 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -60 | 0 | 0 | 0 | 10 | 90 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Governor Response | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net MW | 0 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | -50 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -60 | 0 | 0 | 5 | 20 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOC | 90 | 90 | 89.1667 | 88.3333 | 87.5 | 86.6667 | 85.8333 | 85.8333 | 85.8333 | 85.8333 | 90 | 90 | 90 | 90 | 90 | 90 | 88.3333 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 91.6667 | 91.6667 | 91.6667 | 91.25 | 89.5833 | 81.25 | 72.9167 | 64.5833 | 64.5833 | 64.5833 | 64.5833 | 64.5833 | 64.5833 | 64.5833 | 64.5833
SOCReq-Compliance | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 10 | 15 | 7.5 | 0 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 2.5 | 0 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 7.5 | 0 | 50
SoCReq-Compliance minus charging credit | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 7.5 | 0 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 7.5 | 0 | 90 | 82.5 | 75 | 67.5 | 60 | 52.5 | 45 | 37.5 | 30 | 22.5 | 15 | 7.5 | 0 | 50
SCED Interval | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 |  | 13:00 | 13:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100
ECRS Resp. | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
ECRS Sched. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-curr | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-new | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 50 | 1.7053e-13 | 50 |  | 50 | 0
BP-GR | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 50 | 0 | 50 |  | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 0 | -50 | 0 |  | 0 | 0
Net MW | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | -50 | 50 | -50 | 50 |  | 0 | 0
SOC | 100 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 58.3333 | 58.3333 | 62.5 | 58.3333 | 62.5 |  | 58.3333 | 58.3333
SOCReq1-Compliance | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 0 | 62.5 | 0:00 | 54.1667 |  | 100 | 95.8333
SOCReq2-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq1-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq2-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
SOCReq-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq1-Base | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 66.6667 | 62.5 | 58.3333 | 54.1667 |  | 100 | 95.8333
SOCReq2-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SoCReq-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!

## ECRS
MNOS | 0 | [7 empty] | SOC Req Ramp Start |  | 0 |  |  |  | MPC, HASL-CLR, and BP-CLR are represented as negative values for graphical purposes
MXOS | 100 | [13 empty] | Governor Response = 0 indicates that frequency is relatively stable in the interval, resulting in minimal autonomous governor response
SOC_t0 | 100
Hour 1 | ECRS is not deployed but the ESR-GR may receive BPs as its SOC Req decreases throughout the hour | [12 empty] | Hour 2 | ECRS is released to SCED and the ESR-GR receives large BPs up to its new HASL | [11 empty] | Hour 3 | The ESR-CLR continues to receive charging BPs at the top of the hour, which drop the requirement and keep the unit in compliance
| The ESR-GR may receive BPs as its SOC Req decreases throughout the hour, and these BPs decrease the ESR's SOC | [13 empty] | The HASL-GR decreases so that the SOC cannot dip below the SOC Req due to a SCED BP | [12 empty] | The ESR-CLR recovers SOC to cover the SOC Req during the current hour and at the top of the next hour
| The ESR-CLR starts receiving BPs to charge, and recovers its SOC before the top of the next hour | [13 empty] | The ESR-CLR receives a BP during the last interval, but does not fully recover its SOC before the top of the next hour
Interval Beginning | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 | 13:00 | 13:00 | 13:05 | 13:10 | 13:15 | 13:20 | 13:25 | 13:30 | 13:35 | 13:40 | 13:45 | 13:50 | 13:55 | 14:00 | 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:00 | 15:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MPC | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
ECRS Resp. | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
ECRS Sched. | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
HASL-GR Curr. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 100 | 100 | 100 | 100 | 100 | 100 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SOCReq1 | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 0 | 0 | 0 | 17.5 | 48.75 | 90 | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 0 | 0 | 0 | 0 | 0 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 48.75 | 90 | 90
SOCReq2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOCReq | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 0 | 0 | 0 | 17.5 | 48.75 | 90 | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 0 | 0 | 0 | 0 | 0 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 48.75 | 90 | 90
HASL-GR Post 1186 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 100 | 100 | 55 | 45 | 45 | 45 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HASL-CLR Curr. | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
HASL-CLR Post 1186 | 0 | 0 | -55 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -30 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -50 | -50 | -50 | -50 | -50 | -50 | -50 | -50 | -50 | -50
BP-GR | 0 | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 45 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -60 | -60 | -60 | -60 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net BP | 0 | 55 | 55 | 55 | 55 | 55 | 55 | -100 | -100 | -100 | -30 | 0 | 0 | 0 | 100 | 100 | 55 | 45 | 45 | 45 | 0 | 0 | 0 | 0 | -60 | -60 | -60 | -60 | -60 | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Governor Response | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net MW | 0 | 55 | 55 | 55 | 55 | 55 | 55 | -100 | -100 | -100 | -30 | 0 | 0 | 0 | 100 | 100 | 55 | 45 | 45 | 45 | 0 | 0 | 0 | 0 | -60 | -60 | -60 | -60 | -60 | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOC | 100 | 100 | 95.4167 | 90.8333 | 86.25 | 81.6667 | 77.0833 | 72.5 | 80.8333 | 89.1667 | 97.5 | 100 | 100 | 100 | 100 | 91.6667 | 83.3333 | 78.75 | 75 | 71.25 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | 72.5 | 72.5 | 77.5 | 82.5 | 87.5 | 95.8333 | 95.8333 | 95.8333 | 95.8333 | 95.8333 | 95.8333 | 95.8333 | 95.8333 | 95.8333 | 95.8333
SOCReq-Compliance | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 0 | 0 | 0 | 17.5 | 48.75 | 45 | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 0 | 0 | 0 | 0 | 0 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 48.75 | 45 | 90
SoCReq-Compliance minus charging credit | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 48.75 | 45 | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 48.75 | 45 | 90 | 86.25 | 82.5 | 78.75 | 75 | 71.25 | 67.5 | 63.75 | 60 | 56.25 | 52.5 | 48.75 | 45 | 90
SCED Interval | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 |  | 13:00 | 13:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100
ECRS Resp. | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
ECRS Sched. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-curr | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-new | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 50 | 1.7053e-13 | 50 |  | 50 | 0
BP-GR | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 50 | 0 | 50 |  | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 0 | -50 | 0 |  | 0 | 0
Net MW | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | -50 | 50 | -50 | 50 |  | 0 | 0
SOC | 100 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 58.3333 | 58.3333 | 62.5 | 58.3333 | 62.5 |  | 58.3333 | 58.3333
SOCReq1-Compliance | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 0 | 62.5 | 0:00 | 54.1667 |  | 100 | 95.8333
SOCReq2-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq1-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq2-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
SOCReq-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq1-Base | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 66.6667 | 62.5 | 58.3333 | 54.1667 |  | 100 | 95.8333
SOCReq2-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SoCReq-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!

## NonSpin
MNOS | 0 | [7 empty] | SOC Req Ramp Start |  | 0 |  |  |  | MPC, HASL-CLR, and BP-CLR are represented as negative values for graphical purposes
MXOS | 100 | [13 empty] | Governor Response = 0 indicates that frequency is relatively stable in the interval, resulting in minimal autonomous governor response
SOC_t0 | 100
Hour 1 | NonSpin is not deployed but the ESR-GR may receive BPs as its SOC Req decreases throughout the hour | [12 empty] | Hour 2 | NonSpin is released to SCED and the ESR-GR receives large BPs up to its new HASL | [11 empty] | Hour 3 | The ESR-CLR continues to receive charging BPs at the top of the hour, which drop the requirement and keep the unit in compliance
| The ESR-GR does receive BPs which decrease its SOC | [13 empty] | The HASL-GR decreases so that the SOC cannot dip below the SOC Req due to a SCED BP | [12 empty] | The ESR-CLR recovers SOC to cover the SOC Req during the current hour and at the top of the next hour
| The ESR-CLR starts receiving BPs to charge, and recovers its SOC before the top of the next hour | [13 empty] | The ESR-CLR receives a BP during the last interval, but that alone does not fully recover its SOC before the top of the next hour. ESR continues to receive BP in the next hour
Interval Beginning | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 | 13:00 | 13:00 | 13:05 | 13:10 | 13:15 | 13:20 | 13:25 | 13:30 | 13:35 | 13:40 | 13:45 | 13:50 | 13:55 | 14:00 | 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:00 | 15:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MPC | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
NonSpin Resp. | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
NonSpin Sched. | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
HASL-GR Curr. | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
SOCReq1 | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 0 | 0 | 80 | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 0 | 0 | 0 | 0 | 0 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 61.6667 | 80 | 80
SOCReq2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOCReq | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 0 | 0 | 80 | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 0 | 0 | 0 | 0 | 0 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 61.6667 | 80 | 80
HASL-GR Post 1186 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 60 | 60
HASL-CLR Curr. | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
HASL-CLR Post 1186 | 0 | 0 | -20 | -40 | -60 | -80 | -100 | -100 | -100 | -100 | -100 | -50 | -1.7053e-13 | -1.7053e-13 | -1.7053e-13 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
BP-GR | 0 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -60 | -60 | -60 | -60 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net BP | 0 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | -50 | -50 | 0 | 0 | 100 | 100 | 100 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | -60 | -60 | -60 | -60 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Governor Response | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net MW | 0 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | -50 | -50 | 0 | 0 | 100 | 100 | 100 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | -60 | -60 | -60 | -60 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOC | 100 | 100 | 98.3333 | 96.6667 | 95 | 93.3333 | 91.6667 | 91.6667 | 91.6667 | 91.6667 | 91.6667 | 95.8333 | 100 | 100 | 100 | 91.6667 | 83.3333 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 65 | 70 | 70 | 75 | 80 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
SOCReq-Compliance | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 0 | 0 | 0 | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 0 | 0 | 0 | 0 | 0 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 61.6667 | 60 | 80
SoCReq-Compliance minus charging credit | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 61.6667 | 60 | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 61.6667 | 60 | 80 | 78.3333 | 76.6667 | 75 | 73.3333 | 71.6667 | 70 | 68.3333 | 66.6667 | 65 | 63.3333 | 61.6667 | 60 | 80
SCED Interval | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 |  | 13:00 | 13:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100
ECRS Resp. | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
ECRS Sched. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-curr | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-new | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 50 | 1.7053e-13 | 50 |  | 50 | 0
BP-GR | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 50 | 0 | 50 |  | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 0 | -50 | 0 |  | 0 | 0
Net MW | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | -50 | 50 | -50 | 50 |  | 0 | 0
SOC | 100 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 58.3333 | 58.3333 | 62.5 | 58.3333 | 62.5 |  | 58.3333 | 58.3333
SOCReq1-Compliance | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 0 | 62.5 | 0:00 | 54.1667 |  | 100 | 95.8333
SOCReq2-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq1-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq2-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
SOCReq-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq1-Base | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 66.6667 | 62.5 | 58.3333 | 54.1667 |  | 100 | 95.8333
SOCReq2-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SoCReq-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!

## Reg+RRS
MNOS | 0 | [7 empty] | SOC Req Ramp Start |  | 0 |  |  |  | MPC, HASL-CLR, and BP-CLR are represented as negative values for graphical purposes
MXOS | 100 | [13 empty] | Governor Response = 0 indicates that frequency is relatively stable in the interval, resulting in minimal autonomous governor response
SOC_t0 | 100
[27 empty] | Hour 3 | Due to high prices, the ESR-CLR does not receive BPs from SCED at the top of the hour
Hour 1 | Significant Reg Up deployment during first half hour depletes SOC | [12 empty] | Hour 2 | Regulation Up is deployed towards the end of the hour, and low frequency requires governor response | [12 empty] | 30 MW of RRS is traded to another unit, which drops the SOC Req and keeps the ESR in compliance
| The ESR-CLR starts receiving basepoints halfway through the hour | [13 empty] | The combination of these elements depletes SOC | [12 empty] | Reg Up is deployed and RRS is released to SCED. The ESR-GR receives BPs and the combination depletes SOC
| The ESR achieves sufficient SOC to cover next hour's responsibility | [13 empty] | Regulation Up continues to be deployed into the top of the next hour | [12 empty] | The rest of the RRS is traded away at the top of the following hour due to the current SOC
Interval Beginning | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 | 13:00 | 13:00 | 13:05 | 13:10 | 13:15 | 13:20 | 13:25 | 13:30 | 13:35 | 13:40 | 13:45 | 13:50 | 13:55 | 14:00 | 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:00 | 15:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MPC | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
RegUp Resp. | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
RegUp Deployed | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 40 | 30 | 20 | 40 | 40 | 40 | 40 | 30 | 10 | 20 | 20 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0
RRS Resp. | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0
RRS Sched. | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 0
HASL-GR Curr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 35 | 30 | 60 | 60
SOCReq1 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 0 | 0 | 0 | 6.6667 | 8.3333 | 100 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 70 | 70 | 64.1667 | 58.3333 | 52.5 | 46.6667 | 40.8333 | 35 | 29.1667 | 23.3333 | 17.5 | 11.6667 | 5.8333 | 40 | 40
SOCReq2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOCReq | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 0 | 0 | 0 | 6.6667 | 8.3333 | 100 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 70 | 70 | 64.1667 | 58.3333 | 52.5 | 46.6667 | 40.8333 | 35 | 29.1667 | 23.3333 | 17.5 | 11.6667 | 5.8333 | 40 | 40
HASL-GR Post 1186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 35 | 30 | 25 | 25
HASL-CLR Curr. | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
HASL-CLR Post 1186 | 0 | -40 | -80 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -20 | -70 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
BP-GR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 35 | 0 | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net BP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 35 | 0 | 0 | 0
Governor Response | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 5 | 5 | 0 | 0 | 0 | 2 | 3 | 10 | 7 | 5 | 8 | 5 | 5 | 2 | 3 | 0 | 0 | 0
Net MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | -60 | -60 | -100 | -60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 50 | 50 | 40 | 25 | 45 | 40 | 40 | 40 | 32 | 13 | 30 | 27 | 15 | 63 | 60 | 55 | 52 | 38 | 0 | 0 | 0
SOC | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 81.6667 | 86.6667 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98.3333 | 94.1667 | 90 | 86.6667 | 84.5833 | 80.8333 | 77.5 | 77.5 | 74.1667 | 71.5 | 70.4167 | 67.9167 | 65.6667 | 64.4167 | 59.1667 | 54.1667 | 49.5833 | 45.25 | 42.0833 | 42.0833 | 42.0833
SOCReq-Compliance | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 0 | 0 | 0 | 0 | 8.3333 | 0 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 0 | 70 | 64.1667 | 58.3333 | 52.5 | 46.6667 | 40.8333 | 35 | 29.1667 | 23.3333 | 17.5 | 11.6667 | 5.8333 | 0 | 40
SoCReq-Compliance minus charging credit | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 0 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 50 | 41.6667 | 33.3333 | 25 | 16.6667 | 8.3333 | 0 | 70 | 64.1667 | 58.3333 | 52.5 | 46.6667 | 40.8333 | 35 | 29.1667 | 23.3333 | 17.5 | 11.6667 | 5.8333 | 0 | 40

## RRS+ECRS
MNOS | 0 | [7 empty] | SOC Req Ramp Start |  | 0 |  |  |  | MPC, HASL-CLR, and BP-CLR are represented as negative values for graphical purposes
MXOS | 100 | [13 empty] | Governor Response = 0 indicates that frequency is relatively stable in the interval, resulting in minimal autonomous governor response
SOC_t0 | 100
[14 empty] | Hour 2 | ECRS is released to SCED which raises HASL-GR, and low frequency requires a governor response | [11 empty] | Hour 3 | Both ECRS and RRS are released to SCED, which raises HASL-GR
Hour 1 | Neither RRS nor ECRS is deployed | [13 empty] | The ESR-GR receives BPs up to its new HASL | [12 empty] | The ESR-GR receives BPs up to its new HASL, which decreases so that the SOC cannot dip below the SOC Req due to a SCED BP
| The ESR-GR may receive BPs as its SOC Req decreases throughout the hour, and these BPs decrease the ESR's SOC | [13 empty] | HASL-GR decreases so that the SOC cannot dip below the SOC Req due to a SCED BP | [12 empty] | The ESR-CLR does not receive any BPs until the last interval of the hour.
| The ESR-CLR receives a BP to charge and restores the SOC before the top of the next hour | [13 empty] | The ESR-CLR receives BPs to charge and restores the SOC before the top of the next hour | [12 empty] | The SOC is not fully recovered, but the ESR-CLR continues to receive BPs at the top of the next hour which reduces the SOC Req
Interval Beginning | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 | 13:00 | 13:00 | 13:05 | 13:10 | 13:15 | 13:20 | 13:25 | 13:30 | 13:35 | 13:40 | 13:45 | 13:50 | 13:55 | 14:00 | 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:00
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MPC | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
RRS Resp. | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RRS Sched. | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
ECRS Resp. | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
ECRS Sched. | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20
HASL-GR Curr. | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 50 | 50 | 50 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 100 | 100 | 100 | 100 | 50 | 50 | 30 | 30 | 30 | 30 | 30 | 30
SOCReq1 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 33.3333 | 30 | 31.6667 | 25.8333 | 90 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 0 | 0 | 25 | 90 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 37.5 | 31.6667 | 0 | 0 | 0
SOCReq2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOCReq | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 33.3333 | 30 | 31.6667 | 25.8333 | 90 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 0 | 0 | 25 | 90 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 37.5 | 31.6667 | 0 | 0 | 0
HASL-GR Post 1186 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 50 | 50 | 50 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 30 | 100 | 100 | 80 | 70 | 50 | 50 | 30 | 30 | 30 | 30 | 30 | 30
HASL-CLR Curr. | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
HASL-CLR Post 1186 | 0 | 0 | 0 | -30 | -60 | -90 | -100 | -100 | -100 | -90 | -60 | -60 | -60 | -60 | -62 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
BP-GR | 0 | 0 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 80 | 70 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -30 | -30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100
Net BP | 0 | 0 | 30 | 30 | 30 | 30 | 0 | 0 | -30 | -30 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 20 | 20 | 0 | 0 | -100 | -100 | -10 | 0 | 0 | 0 | 100 | 100 | 80 | 70 | 50 | 50 | 0 | 0 | 0 | -100 | -100 | -100
Governor Response | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 5 | 10 | 10 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net MW | 0 | 0 | 30 | 30 | 30 | 30 | 0 | 0 | -30 | -30 | 0 | 0 | 2 | 2 | 55 | 60 | 60 | 53 | 20 | 20 | 0 | 0 | -100 | -100 | -10 | 0 | 0 | 0 | 100 | 100 | 80 | 70 | 50 | 50 | 0 | 0 | 0 | -100 | -100 | -100
SOC | 100 | 100 | 100 | 97.5 | 95 | 92.5 | 90 | 90 | 90 | 92.5 | 95 | 95 | 95 | 95 | 94.8333 | 90.25 | 85.25 | 80.25 | 75.8333 | 74.1667 | 72.5 | 72.5 | 72.5 | 80.8333 | 89.1667 | 90 | 90 | 90 | 90 | 81.6667 | 73.3333 | 66.6667 | 60.8333 | 56.6667 | 52.5 | 52.5 | 52.5 | 52.5 | 60.8333 | 60.8333
SOCReq-Compliance | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 33.3333 | 30 | 31.6667 | 25.8333 | 20 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 0 | 0 | 25 | 20 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 37.5 | 31.6667 | 0 | 0 | 0
SoCReq-Compliance minus charging credit | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 37.5 | 31.6667 | 25.8333 | 20 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 37.5 | 31.6667 | 25.8333 | 20 | 90 | 84.1667 | 78.3333 | 72.5 | 66.6667 | 60.8333 | 55 | 49.1667 | 43.3333 | 37.5 | 31.6667 | 25.8333 | 20 | 90
SCED Interval | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 |  | 13:00 | 13:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100
ECRS Resp. | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
ECRS Sched. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-curr | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-new | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 50 | 1.7053e-13 | 50 |  | 50 | 0
BP-GR | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 50 | 0 | 50 |  | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 0 | -50 | 0 |  | 0 | 0
Net MW | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | -50 | 50 | -50 | 50 |  | 0 | 0
SOC | 100 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 58.3333 | 58.3333 | 62.5 | 58.3333 | 62.5 |  | 58.3333 | 58.3333
SOCReq1-Compliance | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 0 | 62.5 | 0:00 | 54.1667 |  | 100 | 95.8333
SOCReq2-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq1-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq2-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
SOCReq-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq1-Base | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 66.6667 | 62.5 | 58.3333 | 54.1667 |  | 100 | 95.8333
SOCReq2-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SoCReq-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!

## ECRS+NonSpin
MNOS | 0 | [7 empty] | SOC Req Ramp Start |  | 0 |  |  |  | MPC, HASL-CLR, and BP-CLR are represented as negative values for graphical purposes
MXOS | 100 | [13 empty] | Governor Response = 0 indicates that frequency is relatively stable in the interval, resulting in minimal autonomous governor response
SOC_t0 | 100
[14 empty] | Hour 2 | ECRS is released to SCED which raises HASL-GR | [11 empty] | Hour 3 | Both ECRS and NonSpin are released to SCED, which raises HASL-GR
Hour 1 | Neither ECRS nor NonSpin is deployed | [13 empty] | The ESR-GR receives BPs up to its new HASL | [12 empty] | The ESR-GR receives BPs up to its new HASL, which decreases so that the SOC cannot dip below the SOC Req due to a SCED BP
| The ESR-GR may receive BPs as its SOC Req decreases throughout the hour, and these BPs decrease the ESR's SOC | [13 empty] | HASL-GR decreases so that the SOC cannot dip below the SOC Req due to a SCED BP | [12 empty] | The ESR-CLR does not receive any BPs until the last interval of the hour.
| The ESR-CLR receives a BP to charge and restores the SOC before the top of the next hour | [13 empty] | The ESR-CLR receives BPs to charge and restores the SOC before the top of the next hour | [12 empty] | The SOC is not fully recovered, but the ESR-CLR continues to receive BPs at the top of the next hour which reduces the SOC Req
Interval Beginning | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 | 13:00 | 13:00 | 13:05 | 13:10 | 13:15 | 13:20 | 13:25 | 13:30 | 13:35 | 13:40 | 13:45 | 13:50 | 13:55 | 14:00 | 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:00 | 15:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MPC | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
ECRS Resp. | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
ECRS Sched. | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NonSpin Resp. | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
NonSpin Sched. | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HASL-GR Curr. | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 90 | 90 | 90 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SOCReq1 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 33.3333 | 32.5 | 0 | 63.3333 | 100 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 0 | 0 | 0 | 100 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 70 | 66.6667 | 0 | 0 | 0
SOCReq2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOCReq | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 33.3333 | 32.5 | 0 | 63.3333 | 100 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 0 | 0 | 0 | 100 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 70 | 66.6667 | 0 | 0 | 0
HASL-GR Post 1186 | 0 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 40 | 60 | 60 | 35 | 35 | 35 | 35 | 40 | 60 | 60 | 60 | 0 | 0 | 40 | 80 | 70 | 60 | 40 | 40 | 40 | 40 | 80 | 100 | 100 | 100 | 100
HASL-CLR Curr. | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
HASL-CLR Post 1186 | 0 | 0 | 0 | -60 | -90 | -100 | -100 | -100 | -100 | -100 | -90 | 0 | 0 | 0 | 0 | 0 | -60 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -80 | 0 | 0 | 0 | 0 | -50 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100 | -100
BP-GR | 0 | 0 | 60 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 35 | 35 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 60 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -30 | -30 | -90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -100 | -100 | -100
Net BP | 0 | 0 | 60 | 30 | 30 | 30 | 0 | 0 | -30 | -30 | -90 | 0 | 0 | 0 | 0 | 60 | 60 | 35 | 35 | 35 | 35 | 0 | -100 | -100 | -80 | 0 | 0 | 0 | 50 | 50 | 60 | 40 | 40 | 40 | 0 | 0 | 0 | -100 | -100 | -100
Governor Response | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net MW | 0 | 0 | 60 | 30 | 30 | 30 | 0 | 0 | -30 | -30 | -90 | 0 | 0 | 0 | 0 | 60 | 65 | 40 | 40 | 40 | 35 | 0 | -100 | -100 | -80 | 0 | 0 | 0 | 50 | 50 | 60 | 40 | 40 | 40 | 0 | 0 | 0 | -100 | -100 | -100
SOC | 100 | 100 | 100 | 95 | 92.5 | 90 | 87.5 | 87.5 | 87.5 | 90 | 92.5 | 100 | 100 | 100 | 100 | 100 | 95 | 89.5833 | 86.25 | 82.9167 | 79.5833 | 76.6667 | 76.6667 | 85 | 93.3333 | 100 | 100 | 100 | 100 | 95.8333 | 91.6667 | 86.6667 | 83.3333 | 80 | 76.6667 | 76.6667 | 76.6667 | 76.6667 | 85 | 85
SOCReq-Compliance | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 33.3333 | 32.5 | 0 | 63.3333 | 60 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 0 | 0 | 0 | 0 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 70 | 66.6667 | 0 | 0 | 0
SoCReq-Compliance minus charging credit | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 70 | 66.6667 | 63.3333 | 60 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 70 | 66.6667 | 63.3333 | 60 | 100 | 96.6667 | 93.3333 | 90 | 86.6667 | 83.3333 | 80 | 76.6667 | 73.3333 | 70 | 66.6667 | 63.3333 | 60 | 100
SCED Interval | 12:00 | 12:05 | 12:10 | 12:15 | 12:20 | 12:25 | 12:30 | 12:35 | 12:40 | 12:45 | 12:50 | 12:55 |  | 13:00 | 13:05
HSL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100
ECRS Resp. | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
ECRS Sched. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-curr | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 |  | 50 | 50
HASL-new | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 50 | 1.7053e-13 | 50 |  | 50 | 0
BP-GR | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 50 | 0 | 50 |  | 0 | 0
BP-CLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 0 | -50 | 0 |  | 0 | 0
Net MW | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | -50 | 50 | -50 | 50 |  | 0 | 0
SOC | 100 | 100 | 91.6667 | 83.3333 | 75 | 66.6667 | 58.3333 | 58.3333 | 58.3333 | 62.5 | 58.3333 | 62.5 |  | 58.3333 | 58.3333
SOCReq1-Compliance | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 0 | 62.5 | 0:00 | 54.1667 |  | 100 | 95.8333
SOCReq2-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq-Compliance | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SOCReq1-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq2-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
SOCReq-Sched | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8333 | 0 | 62.5 | 0 | 54.1667 |  | 100 | 95.8333
SOCReq1-Base | 100 | 95.8333 | 91.6667 | 87.5 | 83.3333 | 79.1667 | 75 | 70.8333 | 66.6667 | 62.5 | 58.3333 | 54.1667 |  | 100 | 95.8333
SOCReq2-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
SoCReq-Base | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!