## Slide 1
San Antonio South Reliability Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
July 25, 2023

## Slide 2: Overview
CPS Energy submitted the San Antonio South Reliability Project for Regional Planning Group (RPG) review in December 2022
  This is a Tier 1 project that was estimated to cost $281.0 million
  Addresses the reliability need in the San Antonio area

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review indicated reliability planning criteria violations
System improvement is needed to meet reliability planning criteria
 | Thermal Overloads
Total | 26.9 miles of 138-kV transmission lines

## Slide 5: Comparison of Project Options
ERCOT analyzed five options and short-listed three options
Among the short-listed three options, Option 5 improves long-term load serving capability, operational flexibility, provides an additional transfer path from Southern Texas into the San Antonio area, and is significantly less expensive than Option 3
Option 5 is the preferred option
 | Option 3 | Option 4 | Option 5
Meets ERCOT and NERC Reliability Criteria | Yes | Yes | Yes
Improves Long-Term Load Serving Capability | Yes (Better) | Marginally | Yes
Improves Performance in Summer Peak Operations Case Sensitivity | Yes | No | Yes
Improves Operational Flexibility | No | No | Yes
Provides an additional transfer path from South | No | No | Yes
Requires CCN (Miles) | No | Yes (1.7) | Yes (51.7)
Construction Feasible (Based on TSP assessment) | Yes | No | Yes
Cost Estimate ($M) | 505.6* | N/A | 329.1
* Updated cost estimate from the original estimate in the RPG submittal

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 5 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 5 did cause one new congestion
    Upgrade of new congested line did not yield any economic benefit and therefore will not be recommended for upgrade as part of this project
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse Option 5 to address the reliability need in the San Antonio area
TSP expects to implement the upgrades by June 2027
Estimated Capital Cost: $329.1 Million
ERCOT will recommend that the ERCOT Board designate Option 5 as critical to the reliability of the ERCOT System pursuant to PUCT Substantive Rule 25.101(b)(3)(D)

## Slide 9: ERCOT Recommendation: Option 5
Construct a new 50-mile Howard Road to San Miguel 345-kV double circuit transmission line with a normal and emergency rating of at least 1982 MVA per circuit, will require 50 miles of new ROW
Rebuild the existing 14.9-mile Cagnon to Howard Road 345-kV double circuit transmission line with a normal and emergency rating of at least 1746 MVA per circuit
Rebuild the existing 4.9-mile Howard Road to Leon Creek 138-kV transmission line with a normal and emergency rating of at least 698 MVA, will require 1.7 miles of new ROW
Add a third 600-MVA 345/138-kV autotransformer at Howard Road substation
Rebuild the existing 2.9-mile Leon Creek to Southsan 138-kV transmission line with a normal and emergency rating of at least 478 MVA

## Slide 10: Option 5