ERCOT Nodal Operating Guide

- Table of Contents

- August 1, 2023

1	Overview	1

1.1	Document Purpose	1

1.2	Document Relationship	1

1.3	Process for Nodal Operating Guide Revision	1

1.3.1 Introduction	1

1.3.2 Submission of a Nodal Operating Guide Revision Request	3

1.3.3 Nodal Operating Guide Revision Procedure	3

1.3.3.1 Review and Posting of Nodal Operating Guide Revision Requests	 3

1.3.3.2 Withdrawal of a Nodal Operating Guide Revision Request	 4

1.3.3.3 ROS Review and Action	 5

1.3.3.4 Comments to teh ROS Report	 6

1.3.3.5 Nodal Operating Guide Revision Request Impact Analysis	 6

1.3.3.6 ROS Review of Impact Analysis	 7

1.3.3.7 ERCOT Impact Analysis Based on ROS Report	 7

1.3.3.8 PRS Review of Project Prioritization	 7

1.3.3.9 Technical Advisory Committee Vote	 7

1.3.3.10 ERCOT Board Vote	 9

1.3.3.11 PUCT Approval of Revision Requests…………………..   		            9

1.3.3.12 Appeal of Action	 10

1.3.4 Urgent Requests	11

1.3.5 Nodal Operating Guide Revision Implementation	11

1.4	Definitions	12

1.5	Operational Training	18

1.5.1 System Operator Training Objectives	18

1.5.2 System Operator Training Requirements	18

1.5.3 ERCOT Operations Training Seminar	19

1.5.4 ERCOT Severe Weather Drill	19

1.5.5 Training Practices	20

1.5.6 ERCOT Operator Certification Program	20

2	System Operations and Control Requirements	1

2.1	Operational Duties	1

2.2	System Monitoring and Control	3

2.2.1 Overview	3

2.2.2 Security Criteria	5

2.2.3 Response to Transient Voltage Disturbance	5

2.2.4 Load Frequency Control	5

2.2.4.1 Maintenance and Verification	 6

2.2.4.2 Regulation Provider Loss of AGC	6

2.2.4.3 ERCOT Loss of AGC	7

2.2.5 Automatic Voltage Regulators	7

2.2.6 Power System Stabilizers	10

2.2.7 Turbine Speed Governors	12

2.2.8 Performance/Disturbance/Compliance Analysis	13

2.2.9 Time Error and Time Synchronization	14

2.2.9.1 Time Error	 14

2.2.9.2 Time Synchronization	14

2.2.10 Generation Resource and Energy Storage Resource Response Time Requirements	15

2.3	Ancillary Services	18

2.3.1 Responsive Reserve	24

2.3.1.1 Obligation	24

2.3.1.2 Additional Operational Details for Responsive Reserve Provders	25

2.3.1.2.1 Limit on Generation Resources and Controllable Load Resources Providing RRS	31

2.3.2 Non-Spinning Reserve Service	32

2.3.2.1 Additional Operational Details for Non-Spinning Reserve Service Providers	32

2.4	Outage Coordination	35

2.5	Reliability Unit Commitment	35

2.5.1 Criteria for Removing Contingencies from the RUC Analyses	35

2.6	Requirements for Under-Frequency and Over- Frequency Relaying	35

2.6.1 Automatic Firm Load Shedding	35

2.6.2 Generators	37

2.6.2.1 Frequency Ride-Through Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs)	38

2.6.3 Frequency Ride-Through Requirements for Direct Current Ties (DC Ties)	39

2.7	System Voltage Profile and Operational Voltage Control	39

2.7.1 Introduction	39

2.7.2 Maintaining Voltage Profile	40

2.7.3 Real-Time Operational Voltage Control	43

2.7.3.1 Operational Guidelines	43

2.7.3.2 ERCOT Responsibilities	44

2.7.3.3 TO/TSP Responsibilities	46

2.7.3.4 QSE Responsibilities	48

2.7.3.5 Resource Entity Responsibilities and Generation Resource Requirements	50

2.7.4 Special Consideration for Nuclear Power Plants	53

2.7.5 Parameters for Standard Reactor and Capacitor Switching Plan	53

2.7.6 Unit Dispatch Beyond the Corrected Unit Reactive Limit or Unit Reactive Limit	54

2.8	Operation of Direct Current Ties	54

2.8.1 Inadvertent Energy Management	55

2.9	Voltage Ride-Through Requirements For Generation Resources	55

2.9.1 Voltage Ride-Through Requirements for Intermittent Renewable Resources Connected to the ERCOT Transmission Grid	59

2.9.2 Voltage Ride-Through Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs)	64

2.10	Voltage Ride-Through Requirements For DC Ties	64

3 	ERCOT AND MARKET PARTICIPANT RESPONSIBILITIES	1

3.1	System Control Interfaces with ERCOT	1

3.1.1 Introduction	1

3.1.2 Compliance with Dispatch Instructions	1

3.1.3 Dispatch Instructions	1

3.2	Qualified Scheduling Entities	3

3.2.1 Operating Obligations	3

3.2.2 Changes in Resource Status	4

3.2.3 Regulatory Required Incident and Disturbance Reports	4

3.2.4 Ancillary Service Qualification and Testing Program	5

3.3	Resource Entities	6

3.3.1 Unit Capability Requirements	10

3.3.2 Unit Reactive Capability Requirements	10

3.3.3 Resource Entity Responsibilities for Equipment Ratings	17

3.4	Load Resource Testing Requirement	18

3.5	ERCOT Implementation	18

3.6	Transmission Service Providers	19

3.7  	Transmission Operators	19

3.7.1 Transmission Owner Responsibility for a Vegetation Management Program	22

3.7.2 Trasmission Service Provider Responsibilities for Equipment Ratings	22

3.8  	Requirements for Reporting Sabotage Information	23

4	Emergency Operations	2

4.1	Introduction	2

4.2	Communication Under Emergency Conditions	2

4.2.1 Operating Condition Notice	2

4.2.2 Advisory	3

4.2.3 Watch	5

4.2.4 Emergency Notice	6

4.3	Operation to Maintain Transmission System Security	7

4.3.1 Real-Time and Short Term Planning	7

4.4	Block Load Transfers between ERCOT and Non-ERCOT System	7

4.5	Energy Emergency Alert (EEA)	8

4.5.1 General	8

4.5.2 Operating Procedures	8

4.5.3 Implementation	10

4.5.3.1 General Procedures Prior to EEA Operations	 12

4.5.3.2 General Procedures During EEA Operations	12

4.5.3.3 EEA Levels	13

4.5.3.4 Load Shed Obligation………………………………………………………………..20

4.5.3.5 EEA Termination…………………………………………...……………………….20

4.6	Black Start Service	21

4.6.1 Principles	21

4.6.2 Strategies	21

4.6.3 Priorities	22

4.6.4 Responsibilities	23

4.6.5 Black Start Emergency Back Up Communication Facilities Criteria	26

4.7	Geomagnetic Disturbance Operating Plan	27

4.7.1 Monitoring and Dissemination of Space Weather Information	27

4.7.2 Development and Submission of TO GMD Operating Procedures or Processes	27

4.7.3 ERCOT’s GMD Operating Plan and ERCOT Review of TO GMD Operating Procedures or Processes	28

4.8	Responsive Reserve Service During Scarcity Conditions…………………………………………28

4.8.1 Responsive Reserve Service Manual Deployment…………………………………………..29

4.8.2 Responsive Reserve Service Manual Recall…….……….………….………………………30

5	Network Operations Modeling Requirements	1

5.1	System Modeling Information	1

6	Disturbance Monitoring and System Protection	1

6.1	Disturbance Monitoring Requirements	1

6.1.1 Introduction	1

6.1.2 Fault Recording and Sequence of Events Recording Equipment	1

6.1.2.1 Fault Recording Requirements	 2

6.1.2.2 Fault Recording and Sequence of Events Recording Equipment Location Requirements	 2

6.1.2.3 Fault Recording and Sequence of Events Recording Data Requirements	 3

6.1.2.4 Fault Recording and Sequence of Events Recording Data Retention and Reporting Requirements	4

6.1.3 Phasor Measurement Recording Equipment Including Dynamic Disturbance Recording Equipment	4

6.1.3.1 Recording and Triggering Requirements	 4

6.1.3.2 Location Requirements	 5

6.1.3.3 Data Recording and Redundancy Requirements	 6

6.1.3.4 Data Retention and Data Reporting Requirements	 7

6.1.4 Maintenance and Testing Requirements	8

6.1.5 Equipment Reporting Requirements	8

6.1.5.1 Geomagnetic Disturbance (GMD) Measurement Data Processes	 8

6.1.6 Review Process	8

6.2	System Protective Relaying	9

6.2.1 Introduction	9

6.2.1.1 Applicability	 9

6.2.2 Design and Operating Requirements for ERCOT System Facilities	10

6.2.3 Performance Analysis Requirements for ERCOT System Facilities	11

6.2.4 Protective Relay System Failure Response	13

6.2.5 Maintenance and Testing Requirements for ERCOT System Facilities	14

6.2.6 Requirements and Recommendations for ERCOT System Facilities	15

6.2.6.1 General Protection Criteria	 15

6.2.6.1.1 Dependability	 15

6.2.6.1.2 Security	 15

6.2.6.1.3 Dependability and Security	 15

6.2.6.1.4 Operating Time	 16

6.2.6.1.5 Testing and Maintenance	 16

6.2.6.1.6 Analysis of System Performance and Associated Protection Systems	 17

6.2.6.2 Equipment and Design Considerations	 18

6.2.6.2.1 Current Transformers	 18

6.2.6.2.2 Voltage Transformers and Potential Devices	 19

6.2.6.2.3 Batteries and Direct Current Supply	 20

6.2.6.2.4 AC Auxiliary Power	 21

6.2.6.2.5 Circuit Breakers	 21

6.2.6.2.6 Communication Channels	 21

6.2.6.2.7 Control Cables and Wiring	 22

6.2.6.2.8 Environment	 23

6.2.6.3 Specific Application Considerations	 23

6.2.6.3.1 Transmission Line Protection	 23

6.2.6.3.2 Transmission Station Protection	 24

6.2.6.3.3 Breaker Failure Protection	 25

6.2.6.3.4 Generator Protection and Relay Requirements	 26

6.2.6.3.5 Automatic Under-Frequency Load Shedding Protection Systems	 28

6.2.6.3.6 Automatic Under-Voltage Load Shedding Protection Systems	 28

7	Telemetry and Communication	1

7.1  	ERCOT Wide Area Network	1

7.1.1 ERCOT Responsibilities	2

7.1.2 WAN Participation Responsibilities	2

7.1.3 Joint Responsibilities (Maintenance and Restoration)	10

7.2	ERCOT ICCP Interface	11

7.2.1 Quality Codes	11

7.2.2 Metric of Availability	11

7.3	Telemetry	12

7.3.1 Data from ERCOT to QSEs	13

7.3.2 Data from ERCOT to TSP	13

7.3.3 Data from WAN Participants to ERCOT	14

7.3.4 Resolving Real-Time Data Issues that affect ERCOT Network Security Analysis	15

7.3.5 TSP and QSE Telemetry Restoration	16

7.3.6 General Telemetry Performance Criterion..............................................................................16

7.4	Calibration and Testing of Telemetry Responsibilities	16

7.5	Competitive Renewable Energy Zone Circuits and Stations	16

8	Attachments

8A Black Start Info

8B Protection System Misoperation Report

8C Turbine Governor Speed Tests

8D Seasonal Unit Net Real Power Capability Verification

8E Black Start Plan Template

8F Seasonal Hydro Responsive Reserve Net Capability Verification

8G Load Resource Tests

8H Unit Alternative Fuel Capability

8I Black Start Resource Availabiity Test Form

8J Initial and Sustained Measurements for Primary Frequency Response

8K Remedial Action Scheme (RAS) Template

8L Emergency Operations Plan

8M Selecting Buses for Capturing Sequence of Events Recording and Fault Recording Data

9	Monitoring Programs	1

9.1	QSE and Resource Monitoring Program	1

9.1.1 Real-Time Data	1

9.1.2 Compliance with Valid Dispatch Instructions	1

9.1.3 Resource Outage Reporting	2

9.1.4 Current Operating Plan Metrics for QSEs	2

9.2	TSP Monitoring Program	2

9.2.1 Intentionally Left Blank	3

9.2.2 Real-Time Data Monitor	3

9.2.3 Transmission Outage Reporting	3

9.3	ERCOT Monitoring Program	4

9.3.1 Transmission Control	4

9.3.2 System and Resource Control	5

9.3.3 Computer and Communication Systems Real-Time Availability and Systems Security	5

9.4	Ancillary Services Monitoring Program	5

9.4.1 Hydro Responsive Testing	5

9.4.2 Resource-Specific Responsive Reserve Performance	6

9.4.3 Resource-specific Non-Spinning Reserve	6

10	Market Data Transparency	1

10.1	Direct Current Tie Outage Information	1

11	Constraint Management Plans and Remedial Action Schemes	1

11.1	Introduction	1

11.2	Remedial Action Schemes	1

11.2.1 Reporting of RAS Operations	7

11.3	Automatic Mitigation Plans	8

11.4	Remedial Action Plan	9

11.4.1 Remedial Action Plan Process	10

11.5	Mitigation Plan	11

11.6	Pre-Contingency Action Plans	11

11.6.1 Pre-Contingency Action Plan Process	12

11.7	Temporary Outage Action Plan	13