| NOGRR Number | 215 | NOGRR Title | Limit Use of Remedial Action Schemes |
| --- | --- | --- | --- |
| Date of Decision |  | August 3, 2023 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation |  |
| Priority and Rank Assigned |  | Priority – 2026; Rank – 4700 |  |
| Nodal Operating Guide Sections Requiring Revision |  | 8, Attachment K, Remedial Action Scheme (RAS) Template 11.1, Introduction 11.2, Remedial Action Schemes 11.2.1, Reporting of RAS Operations |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) will allow new Remedial Action Schemes (RASs) to be used only to address an actual or anticipated violation of transmission security criteria when market tools are insufficient to address those violations. This NOGRR also clarifies the procedures for retiring RASs. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | ERCOT has noted an increase in the number of RASs that are being proposed for new Generation Resources that are being planned in areas where the Resources would need to be curtailed on a near constant basis to maintain the reliability of the transmission grid in the immediate area. It is expected that the number of such RAS proposals will continue to significantly increase, based on the locations and unit sizes being considered in the interconnection process. ERCOT is concerned that such a large increase in the number of RASs could significantly and negatively impact the reliability of the ERCOT System. ERCOT notes the following ways in which RASs increase reliability risks: 1. It is difficult or impossible to assess all possible impacts of RASs on the ERCOT System during the RAS approval process. As a result, an increased burden and risk is imposed in Real-Time or near Real-Time operations to catch issues and evaluate the impacts of those issues. 2. Because all combinations of Outage and system dispatch conditions cannot feasibly be studied during the RAS approval process, the approval studies may not recognize that a particular RAS may need to be disabled during certain Outage conditions. As issues of this type are identified due to subsequent Outage coordination or operational studies, ERCOT keeps a list of these issues and manually checks for them during subsequent Outage evaluations. As the number of RASs increases, this manual process to identify when RASs need to be disabled will become infeasible, and the risk that ERCOT may overlook the need to disable one or more RASs also increases. 3. In addition, the need to recognize issues with and disable RASs introduces even more risk during Forced Outages because the need to disable the RAS may not immediately be recognized. This risk goes up as the number of RASs increases. 4. RASs are modeled in the Energy Management System (EMS) in such a way that they are expected to fully alleviate the conditions for which they have been implemented all the time, but ERCOT’s experience has shown this not to be the case. For example, certain dispatch patterns or other operating conditions not considered during the RAS approval process could be sufficiently severe to cause cascading Outages before the RAS has time to operate. 5. Similarly, RASs are modeled in the Market Management System (MMS) in such a way that they are expected to fully alleviate all overloads for a given condition that triggers the RAS all the time. There could be a reliability concern unrelated to, or unprotected by, a RAS for a given contingency where generation may need to be committed to manage that reliability concern, and the MMS tools will never reflect that need. 6. The risk of RAS misoperation can be a significant reliability issue. In some areas of the network, the implementation of one or more RAS in a particular area could result in a situation where the post-contingency, pre-RAS condition would exceed a local or regional stability limit. If the RAS(s) were to fail or misoperate, the region could experience instability that could lead to cascading Outages or voltage collapse. 7. If the number of RASs increase, especially if there are multiple RASs in a particular area, there is a heightened possibility of RAS-RAS interaction or cascading RAS operation resulting in unforeseen reliability consequences. 8. As the number of RASs in the ERCOT System increase, so does the amount of maintenance needed in ERCOT systems and situational awareness tools related to RASs. 9. The design of a RAS can lead to a condition where a constraint that is easily resolved by ERCOT market tools (e.g., Security-Constrained Economic Dispatch (SCED)) is replaced with post-RAS congestion that does not have a market solution. 10. North American Electric Reliability Corporation (NERC) Reliability Standards associated with the implementation and maintenance of RAS facilities place compliance burdens upon both the RAS owners as well as ERCOT. Given these significant reliability risks, ERCOT believes that a RAS should only be used when it is necessary to address an actual or anticipated violation of transmission security criteria that cannot be resolved by ERCOT market tools. |  |
| ROS Decision |  | On 7/9/20, ROS voted unanimously to table NOGRR215. All Market Segments participated in the vote. On 3/2/23, ROS voted to recommend approval of NOGRR215 as amended by the 3/1/23 LCRA comments as revised by ROS. There were two opposing votes from the Consumer (OPUC) and Cooperative (STEC) Market Segments, and seven abstentions from the Consumer (2) (Air Liquide, Sierra Club), Independent Generator (Calpine), Independent Power Marketer (IPM) (SENA), and Investor Owned Utility (IOU) (3) (Oncor, CNP, TNMP) Market Segments. All Market Segments participated in the vote. On 4/6/23, ROS voted to table NOGRR215. There was one abstention from the IPM (SENA) Market Segment. All Market Segments participated in the vote. On 7/6/23, ROS voted unanimously to table NOGRR215. All Market Segments participated in the vote. On 8/3/23, ROS voted unanimously to endorse and forward to TAC the 7/6/23 ROS Report as amended by the 7/31/23 ERCOT comments and 7/10/23 Revised Impact Analysis for NOGRR215 with a recommended priority of 2026 and rank of 4700. All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 7/9/20, ERCOT Staff provided an overview of NOGRR215 and noted the intent to schedule a workshop for further discussion on related topics. Market Participants briefly discussed the history and potential future impacts of RASs in ERCOT. On 3/2/23, participants discussed the 1/3/23 LCRA, 1/31/23 LCRA, 1/31/23 AEP, 3/1/23 LCRA, 3/1/23 AEP, and 3/1/23 STEC comments. ERCOT Staff emphasized the RAS’s diminished usefulness and purpose in correlation with the ERCOT System’s evolution, and cited SCED as a more capable, comparable tool. ERCOT Staff also expressed support for the 3/1/23 AEP comments, arguing that the 3/1/23 LCRA comments’ preservation of the RAS undermines reliability. LCRA Staff remarked upon the similarities found between AEP’s and their 3/1/23 comments. At LCRA’s suggestion and with Market Participants’ support, Market Rules transferred redlines from the 3/1/23 AEP comments regarding exit strategy and review time period in Section 8, Attachment K, and Section 11.2 as edits on top of LCRA’s 3/1/23 comments. ERCOT Staff reaffirmed support for the 3/1/23 AEP comments but not the 3/1/23 LCRA comments. On 4/6/23, participants reviewed the 3/27/23 ERCOT comments. On 7/6/23, ERCOT Staff provided an overview of the 6/27/23 Revised Impact Analysis and confirmed that, if a contingency triggers a RAS, then all overloaded elements will be ignored in the Day-Ahead Market (DAM). ERCOT Staff also proposed prioritization after completion of the Real-Time Co-Optimization (RTC) project and an associated Priority/Rank of 2027/4800. ERCOT Staff assured Market Participants that ERCOT would remain mindful of NOGRR215 requirements during RTC project execution. Participants agreed to table NOGRR215 to provide ERCOT time to determine which edits require greyboxing and which edits can be made effective upon PUCT approval in order to grant ERCOT the availability to approve RAS for dispatchable generation prior to 2027. On 8/3/23, ERCOT Staff reviewed the 7/31/23 ERCOT comments and 7/10/23 Revised Impact Analysis. Participants also discussed additional priority and rank options. |  |

| Opinions |  |
| --- | --- |
| Credit Review | Not applicable |
| Independent Market Monitor Opinion | To be determined |
| ERCOT Opinion | To be determined |
| ERCOT Market Impact Statement | To be determined |

| Submitter’s Information |  |
| --- | --- |
| Name | Freddy Garcia |
| E-mail Address | Freddy.Garcia@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4245 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jordan Troublefield |
| E-Mail Address | Jordan.Troublefield@ercot.com |
| Phone Number | 512-248-6521 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| WMS 071420 | Requested ROS table NOGRR215 until after a workshop, and requested an opportunity to consider NOGRR215 after the workshop |
| Joint Commenters 010821 | Argued that NOGRR215’s changes to ERCOT’s binding documents (e.g., Protocols, Planning Guides, Operating Guides, etc.) are currently unwarranted, so that historic levels of reliability and open access are preserved |
| DME 011121 | Supported the 1/8/21 Joint Commenters comments and recommended that NOGRR215 be rejected and expressed a willingness to support a small increase to the ERCOT Admin Fee if increasing the Interconnect Fee is not workable |
| ERCOT 051822 | Urged stakeholders to recommend approval of NOGRR215 as originally submitted, acknowledged that other recent policy changes might allow for congestion relief without the use of RASs, and expressed openness in considering other policy changes in order to limit the impact of congestion without negatively impacting reliability |
| LCRA 053122 | Requested that ERCOT Staff file substantive comments responding to the 1/8/21 Joint Commenters’ comments and provide the data that ERCOT Staff indicated they intended to bring to stakeholders over the course of 2021, so that interested parties may fully evaluate NOGRR215 and develop potential alternative approaches |
| Lancium 060122 | Requested that ROS continue to table NOGRR215 while the Large Flexible Load Task Force (LFLTF) discusses interconnections of large loads that may impact RAS/Constraint Management Plan (CMP) policy in unforeseen ways |
| LCRA and Luminant 083122 | Requested that stakeholders continue to allow NOGRR215 to be tabled while parties continue to develop a workable compromise in procedural modifications |
| LCRA 010323 | Recommends that ERCOT be required to consider a new RAS proposal if it supports dispatchable generation and a viable transmission project that meets an existing ERCOT planning criterion that can be identified as a long-term solution to replace the RAS |
| LCRA 013123 | Submitted revisions to further elaborate on the proposal outlined in its 1/3/23 comments |
| AEP 013123 | Proposed changes to ERCOT’s revisions that allows for use of RAS when there is an identified and approved exit strategy to mitigate a reliability problem; reinforces that RAS is only used for reliability purposes; and reduces the review period for existing RAS from five to three years |
| LCRA 030123 | Updated Sections 8, Attachment K, 11.2, and 11.2.1’s baseline of their 1/31/23 LCRA comments in order to reflect the October 1, 2020 incorporation of NOGRR183, Remedial Action Scheme (RAS) Submittal and Review Requirements, into the Nodal Operating Guide and requested that stakeholders consider the 3/1/23 LCRA comments in place of their 1/31/23 comments |
| AEP 030123 | Updated Sections 8, Attachment K, 11.2, and 11.2.1’s baseline of their 1/31/23 AEP comments in order to reflect the October 1, 2020 incorporation of NOGRR183 into the Nodal Operating Guide and requested that stakeholders consider the 3/1/23 AEP comments in place of their 1/31/23 comments |
| STEC 030123 | Argued that it is premature to remove the RAS until the costs and expected decreases in reliability risks are defined |
| ERCOT 032723 | Proposed an alternative schedule to complete a Revised Impact Analysis for NOGRR215 prior to the May 4, 2023 ROS meeting |
| ERCOT 042523 | Proposed an alternative schedule to complete a Revised Impact Analysis for NOGRR215 prior to the June 8, 2023 ROS meeting |
| ERCOT 060723 | Proposed an alternative schedule to complete a Revised Impact Analysis for NOGRR215 prior to the July 6, 2023 ROS meeting |
| ERCOT 073123 | Addressed the anticipation of years-long resource constraints as multiple high-priority improvement projects that impact ERCOT systems are developed and implemented; and proposed edits that distinguish between which revisions do not require a project and therefore may take effect upon PUCT approval and which project-causing revisions must remain greyboxed until ERCOT’s completion of the project |

Market Rules Notes

Administrative changes to the language were made and authored as “ERCOT Market Rules.”

Please note the baseline language in the following Section has been updated to reflect the incorporation of the following NOGRR(s) into the Nodal Operating Guides:

- NOGRR183, Remedial Action Scheme (RAS) Submittal and Review Requirements (unboxed 10/1/20)

  - Section 8, Attachment K

  - Section 11.2

  - Section 11.2.1

Proposed Guide Language Revision

ERCOT Nodal Operating Guides

Section 8

Attachment K

Remedial Action Scheme (RAS) Template

TBD

- This attachment provides a template to be used by an entity for the proposal, modification, and/or retirement of a Remedial Action Scheme (RAS).  If an item in this template does not apply to a specific RAS, a response of “Not Applicable” for that item is appropriate.  All submittals related to RAS must be emailed to ras_cmp@ercot.com.

- I.	General

- 1.	Information such as maps, one-line drawings, substation and schematic drawings that identify the physical and electrical location of the RAS and related facilities.

- 2.		Functionality of new RAS or proposed functional modifications to existing RAS and documentation of the pre- and post-modified functionality of the RAS.

- 3.	The corrective action plan if RAS modifications are proposed in a corrective action plan.

- 4. 	Data to populate the RAS database:

- a.	RAS name;

- b.	RAS Entity and contact information;

- c.	Expected or actual in-service date, most recent ERCOT approval date, most recent ERCOT evaluation date, and date of retirement;

- d.	System performance issue or reason for installing the RAS (e.g., thermal overload, angular instability, poor oscillation damping, voltage instability, under- or over-voltage, or slow voltage recover;

- e.	Description of the contingencies or system conditions for which the RAS was designed;

- f.	Action(s) to be taken by the RAS;

- g.	Identification of Limited Impact RAS; and

- h.	Any additional explanation relevant to high-level understanding of RAS.

- II.	Functional Description and Transmission Planning Information

- 1.	Contingencies and system conditions that the RAS is intended to remedy.

- 2.	The action(s) to be taken by the RAS in response to disturbance conditions.

- 3.	A summary of technical studies, if applicable, demonstrating that the proposed RAS actions satisfy system performance objectives for the scope of system events and conditions that the RAS is intended to remedy.  The technical studies summary shall also include information such as the study year(s), system conditions, and contingencies analyzed on which the RAS design is based, and the date those technical studies were performed.

- 4.	Information regarding any future system plans that will impact the RAS.

- 5.	Exit Strategy that has been identified including the approved transmission project or ERCOT’s recommendation to mitigate the need for the RAS.  For example, reconductor Point A to Point B.

- 6.	RAS Entity proposal and justification for Limited Impact RAS designation.

- 7.	Documentation describing the system performance resulting from the possible inadvertent operation of the RAS, except for Limited Impact RAS, caused by any single RAS component malfunction.  Single component malfunctions in a RAS not determined to be a Limited Impact RAS must satisfy the requirements in paragraph (3)(f) of Section 11.2, Remedial Action Schemes.

- 8.	An evaluation indicating that the RAS settings and operation avoid adverse interactions with other RASs, and protection and control systems.

- 9.	Identification of other affected non-ERCOT Control Areas.

- III.	Implementation

- 1.	Documentation describing the applicable equipment used for detection, dc supply, communications, transfer trip, logic processing, control applications, and monitoring.

- 2.	Information on detection logic and settings/parameters that control the operation of the RAS.

- 3.	Documentation showing that any multifunction device used to perform RAS function(s), in addition to other functions such as protective relaying or Supervisory Control and Data Acquisition (SCADA), does not compromise the reliability of the RAS when the device is not in service or is being maintained.

- 4.	For a RAS not designated as a Limited Impact RAS, documentation describing the system performance resulting from a single component failure in the RAS, except for a Limited Impact RAS, when the RAS was intended to operate.  A single component failure in a RAS not designated as a Limited Impact RAS must not prevent the bulk electric system from meeting the same performance requirements as those required for the events and conditions for which the RAS is designed.  The documentation should describe or illustrate how the design achieves this objective.

- 5.	Documentation describing the functional testing process.

- IV.	RAS Retirement

- 1.	Information necessary to ensure that ERCOT is able to understand the physical and electrical location of the RAS and related facilities;

- 2.	A summary of applicable technical studies and technical justifications upon which the decision to retire the RAS is based; and

- 3.	The anticipated date of RAS retirement.

- 11.1 	Introduction

(1)	Constraint Management Plans (CMPs) are developed in accordance to the guidelines set forth in the sections below, and are defined in Protocol Section 2.1, Definitions.  CMPs include, but are not limited to the following:

(a)	Remedial Action Plans (RAPs) which are modeled in Network Security Analysis (NSA) where practicable;

(b)	Automatic Mitigation Plans (AMPs) which are modeled in NSA where practicable;

(c)	Pre-Contingency Action Plans (PCAPs);

(d)	Temporary Outage Action Plans (TOAPs); and

(e)	Mitigation Plans.

(2)	When developing CMPs, ERCOT shall first attempt to utilize the 15-Minute Rating of the impacted Transmission Facilities, where available, to develop RAPs such that the ERCOT Transmission Grid is utilized to the fullest extent.

[NOGRR215: Insert paragraph (3) below upon system implementation and renumber accordingly:] (3) Remedial Action Schemes (RASs) and/or AMPs may also be implemented in order to allow Generation Resources described in paragraph (3) of Planning Guide Section 4.1.1.7, Minimum Delivery Criteria, to meet the minimum deliverability criteria in Planning Guide Section 4.1.1.7, or Transmission Facilities that would otherwise be subject to restrictions to operate without such restrictions.

(3)	ERCOT shall provide notification to the market of any approved, amended, or removed CMP or Remedial Action Scheme (RAS).  ERCOT shall provide notification to the market of any RAP, AMP, or RAS that cannot be modeled in the Network Operations Model.  ERCOT shall post to the Market Information System (MIS) Secure Area all CMPs and RASs and any unmodeled CMPs or RASs.

(4)	ERCOT shall provide notification to the market of any proposed RASs or PCAPs on the MIS Secure Area.

(5)	ERCOT is not required to provide notification to the market of any proposed TOAPs.

(6)	All submittals related to CMPs or RASs must be emailed to ras_cmp@ercot.com.

- 11.2 	Remedial Action Schemes

(1)	Remedial Action Schemes (RASs) are designed to detect abnormal predetermined ERCOT System conditions and automatically take corrective actions to maintain a secure system.  Any RAS proposed on or after June 24, 2020 may not be approved or implemented unless ERCOT has first determined that the RAS is necessary to avoid an actual or anticipated violation of transmission security criteria, as defined in Operating Guide Section 2.2.2, Security Criteria, that cannot be resolved through ERCOT market tools.

[NOGRR215: Replace paragraph (1) above with the following upon system implementation:] (1) Remedial Action Schemes (RASs) are designed to detect abnormal predetermined ERCOT System conditions and automatically take corrective actions to maintain a secure system. Any RAS proposed on or after June 24, 2020 may not be approved or implemented unless ERCOT has first determined that the RAS is necessary to avoid an actual or anticipated violation of transmission security criteria, as defined in Operating Guide Section 2.2.2, Security Criteria, that cannot be resolved through ERCOT market tools, or unless the RAS would allow a Generation Resource of the type described in paragraph (3) of Planning Guide Section 4.1.1.7, Minimum Delivery Criteria, to operate at a level that comports with the minimum deliverability criteria in Planning Guide Section 4.1.1.7.

(2)	The following do not individually constitute a RAS:

(a)	Protection systems installed for the purpose of detecting faults on Transmission Elements and isolating the faulted Transmission Elements;

(b)	Schemes for automatic Under-Frequency Load Shedding (UFLS) and automatic Under-Voltage Load Shedding (UVLS) comprised of only distributed relays;

(c)	Out-of-step tripping and power swing blocking;

(d)	Automatic reclosing schemes;

(e)	Schemes applied on a Transmission Element for non-fault condition, such as, but not limited to, generator loss-of-field, transformer top-oil temperature, overvoltage or overload to protect the Transmission Element against damage by removing it from service;

(f)	Controllers that switch or regulate one or more of the following: series or shunt reactive devices, flexible alternating current transmission system (FACTS) devices, phase-shifting transformers, variable-frequency transformers, or tap-changing transformers; and that are located at and monitor quantities solely at the same station as the Transmission Element being switched or regulated;

(g)	FACTS controllers that remotely switch static shunt reactive devices located at other stations to regulate the output of a single FACTS device;

(h)	Schemes or controllers that remotely switch shunt reactors and shunt capacitors for voltage regulation that would otherwise be manually switched;

(i)	Schemes that automatically de-energize a line for a non-faults operation when one end of the line is open;

(j)	Schemes that provide anti-islanding protection (e.g. protect Load from effects of being isolated with generation that may not be capable of maintaining acceptable frequency and voltage);

(k)	Automatic sequences that proceed when manually initiated solely by a System Operator;

(l)	Modulation of high voltage, direct current (HVDC) or FACTS via supplementary controls, such as angle damping or frequency damping applied to damp local or inter-area oscillation;

(m)	Sub-synchronous resonance protection schemes that directly detect sub-synchronous quantities (e.g. currents or torsional oscillations); or

(n)	Generation controls such as, but not limited to, Automatic Generation Control (AGC), generation excitation (e.g. Automatic Voltage Regulation (AVR) and Power System Stabilizers (PSSs)), fast valving, and speed governing.

(3)	In addition to the requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards, RASs shall also meet the following requirements:

(a)	A RAS may be proposed by a Transmission Service Provider (TSP) or Resource Entity, and be approved by ERCOT and the TSP(s) and/or Resource Entity(ies) included in the RAS prior to implementation;

(b)	The design, implementation, and testing of the RAS shall be coordinated within the RAS Entity;

(c)	The RAS shall be automatically armed when appropriate;

(d)	The RAS shall not operate unnecessarily;

(e)	A RAS designated as a Limited Impact RAS shall be reviewed according to the process described in paragraph (4)(e) below and subject to ERCOT approval;

(f)        For a RAS not designated by ERCOT as a Limited Impact RAS, the possible inadvertent operation of the RAS, resulting from any single RAS component malfunction satisfies all of the following as determined by the review process in paragraph (4)(e) below and subject to ERCOT approval:

(i)	The ERCOT System shall remain stable;

(ii)	Cascading shall not occur;

(iii)	Applicable Facility Ratings shall not be exceeded;

(iv)	ERCOT System voltages shall be within post-contingency voltage limits and post-contingency voltage deviation limits;

(v)	Transient voltage responses shall be within acceptable limits.

(g)	To avoid unnecessary RAS operation, the RAS Entity may provide a Real-Time status indication to the owner of any Generation Resource controlled by the RAS to show when the flow on one or more of the RAS monitored Facilities exceeds 90% of the flow necessary to arm the RAS.  The cost necessary to provide such status indication shall be the responsibility of the RAS Entity;

(h)	The status indication of any automatic or manual arming/activation or operation of the RAS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owner(s) of any Facility controlled by the RAS;

(i)	When a RAS is removed from service, the RAS Entity or a Designated Agent shall immediately notify ERCOT;

(j)	When a RAS is returned to service, the RAS Entity or its Designated Agent shall immediately notify ERCOT.  ERCOT shall modify its reliability constraints to recognize the availability of the RAS;

(k)	The RAS Entity shall telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems:

(i)	Any automatic or manual arming/activation or operation of the RAS;

(ii)	The in-service/out-of-service status of the RAS; and

(iii)	Any additional related telemetry that already exists pertinent to the monitoring of the RAS (e.g. status indication of communications links between associated RAS equipment and the owner’s control center, arming limits of associated RAS equipment); and

(l)	The TSP may receive telemetry for a Resource Entity owned RAS through ERCOT or through the RAS Entity, at the option of the TSP.  The RAS Entity, at its own cost, must provide telemetry for Resource Entity owned RASs to the TSP upon request.

(4)	The RAS Entity shall submit to ERCOT documentation of an existing, modified, proposed, or retiring RAS for review and compilation into an ERCOT RAS database using the form in Section 8, Attachment K, Remedial Action Scheme (RAS) Template.  The documentation shall detail the design, operation, modeling, functional testing, and coordination of the RAS with other RASs, Automatic Mitigation Plans (AMPs), protection and control systems.  The exit strategy described in the RAS submission shall identify the ERCOT endorsed transmission project or near term mitigation that will address the constraint.

(a)	ERCOT shall conduct a review of each proposed new or modified RAS and each proposed  etirement of a RASinof Adthin five Business Days of receipt, ERCOT shall post the proposal to the MIS Secure Area and shall issue a Market Notice describing the proposal and inviting submission of Market Participant comments.  Within 30 Business Days of receiving the proposal, ERCOT shall inmplete an evaluatein of eae proposal in accordance with paragraph (4)(e) below and shall issue a Market Notice approving or rejecting the proposal.  ERCOT shall coordinate any additional time needed for the evaluation with the RAS Entity.  Addditionally, ERCOT shall conduct a review of each existing RAS at least once every three years or as required by changes in system conditions.

(b)	The review of a proposed RAS shall be completed before the RAS is placed in service.  The timing of placing the RAS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Network Operations Model Change Request (NOMCR) to ERCOT.

(c)	Existing RASs that have already undergone at least one review shall remain in service during any subsequent review.  Modifications to existing RASs may be implemented upon approval by ERCOT.

(d)	The schedule for placing a RAS into service must be coordinated among ERCOT and the RAS Entity, and shall provide sufficient time to perform any necessary functional testing prior to its being placed in service.

(e)	For any proposed, modified, or existing RAS, ERCOT’s review of the RAS shall:

(i)	Validate that RAS is needed to mitigate the system condition(s) or contingency(ies) for which it was designed, and that the RAS actions, designed timing, and arming conditions mitigate those system condition(s) or contingency(ies);

(ii)	Identify any conflicts with the Protocols, NERC Reliability Standards, and this Operating Guide;

(iii)	Validate that transient voltage responses are within acceptable limits as established by ERCOT;

(iv)	Evaluate and document the consequences of misoperation, incorrect operation, unintended operation, or failure of a RAS.  Additionally, validate that the RAS is designed to meet the requirements in paragraphs (3)(e) and (3)(f) above;

(v)	Validate that the proposed RAS facilitates periodic testing and maintenance;

(vi)	Determine whether or not the RAS is a Limited Impact RAS;

(vii)	Validate that the proposed RAS avoids adverse interactions with other RASs, AMPs, protection and control systems, and applicable emergency procedures;

(viii)	Evaluate the effects of future bulk electric system modifications on the design and operation of the RAS where applicable;

(ix)	Validate the implementation of RAS logic appropriately correlates desired actions (outputs) with events and conditions (inputs);

(x)	Validate the mechanism of procedure by which the RAS is armed is clearly described, and is appropriate for reliable arming and operation of the RAS for the conditions and events for which it is designated to operate;

(xi)	Evaluate future transmission project(s) that will eliminate the need for the RAS; and

(f)	Upon completion of ERCOT’s RAS review, ERCOT shall provide all results and underlying studies to the RAS Entity and each impacted TSP.

(g)	If deficiencies are identified for a new, functionally modified, or retiring RAS by ERCOT or other parties’ comments, the RAS Entity shall either submit an amended RAS proposal or withdraw the RAS proposal.  The amended RAS proposal shall undergo the review process specified in paragraph (4)(e) above using the 30 Business Day RAS review timeline in paragraph (4)(a) above until the identified deficiencies have been resolved to the satisfaction of ERCOT.

(h)       For any proposed retirement of a RAS, ERCOT shall evaluate whether the proposed retirement will cause any reliability concern, including whether the proposed retirement will adversely impact the dispatch of a Generation Resource subject to the minimum deliverability criteria set forth in Planning Guide Section 4.1.1.7, Minimum Delivery Criteria.  After considering any comments submitted, if ERCOT does not identify any reliability concern, ERCOT shall issue a Market Notice indicating its approval of the proposed retirement of the RAS.  If ERCOT does identify a reliability concern or an adverse impact to the dispatch of a Generation Resource subject to the minimum deliverability criteria set forth in Planning Guide Section 4.1.1.7, ERCOT shall issue a Market Notice denying the retirement.

(i)	As part of the ERCOT review, ERCOT may notify the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and the System Protection Working Group (SPWG) of the RAS proposal, and each working group or any member of each working group may provide any comments, questions, or issues to ERCOT.  ERCOT may work with the owner(s) of Facilities affected by the RAS as necessary to address all issues.

(j)	ERCOT shall develop a method to include the RAS where practicable in Security-Constrained Economic Dispatch (SCED), Outage coordination, and Reliability Unit Commitment (RUC).

(k)	ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the RAS.

(l)	ERCOT shall update the RAS database at least once every 12 calendar months.

(5)	ERCOT shall provide the results of the RAS evaluation including any identified deficiencies to the RAS Entity and impacted TSPs.  If ERCOT’s RAS evaluation identifies a deficiency, then within six calendar months, the RAS Entity shall develop and submit a corrective action plan, subject to ERCOT approval, to correct the deficiencies.  For each plan developed, the RAS Entity shall implement the approved plan, update the plan if actions or timetables change, and notify ERCOT via email at ras_cmp@ercot.com if plan actions or timetables change and when the plan is completed.

(6)	If ERCOT determines that a RAS is no longer needed, either as part of an ERCOT-initiated review or as a consequence of ERCOT’s determination that a transmission project has addressed the condition(s) or contingency(ies) the RAS was designed to address, ERCOT shall issue a Market Notice proposing to retire the RAS and inviting comments from Market Participants on the proposed retirement.  After considering all comments, if ERCOT confirms that the RAS is not needed, then ERCOT shall retire the RAS on a date specified in a separate Market Notice.

(7)	The RAS Entity shall perform a functional test of each of its RAS to verify the overall RAS performance and the proper operation of non-protection system components at least once every six calendar years for a RAS not designated as a Limited Impact RAS, and once every 12 calendar years for a RAS designated as a Limited Impact RAS.  For any identified deficiencies, the RAS Entity shall develop and submit a corrective action plan within six calendar months, and subject to ERCOT approval, to correct the deficiencies. For each plan developed, the RAS Entity shall implement the approved plan, update the plan if actions or timetables change, and notify ERCOT via email at ras_cmp@ercot.com if plan actions or timetables change and when the plan is completed.

- 11.2.1 	Reporting of RAS Operations

(1)	RAS Entity shall notify ERCOT of all RAS operations.  Documentation of RAS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report form as an email to ras_cmp@ercot.com.  Within 120 calendar days, the RAS Entity shall conduct an analysis of all RAS operations, misoperations, and failures.  If deficiencies are identified, the RAS Entity shall develop and submit a corrective action plan within six calendar months, and subject to ERCOT approval, correct the deficiencies.  For each plan developed, the RAS Entity shall implement the approved plan, update the plan if actions or timetables change, and notify ERCOT via email at ras_cmp@ercot.com if plan actions or timetables change and when the plan is completed.  Analysis of RAS operational performance shall include, but is not limited to:

(a)	Determination of whether system events or conditions appropriately armed or triggered the RAS;

(b)	Determination of whether the RAS responded as designed;

(c)	Determination of whether the RAS was effective in mitigating the performance issues it was designed to address; and

(d)	Determination of whether the RAS operation resulted in any unintended or adverse system response.

(2)	ERCOT shall report all RAS operations and misoperations to the Reliability Monitor for review.  RAS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to the Reliability Monitor and the NERC Regional Entity.  A misoperation of a RAS with respect to reporting requirements to the Reliability Monitor and the NERC Regional Entity occurs when one of the items specified in paragraph (4) of Section 6.2.3, Performance Analysis Requirements for ERCOT System Facilities, occur.  RAS Entities will provide a monthly report to ERCOT by the 15th of each month describing each instance a RAS armed/activated and reset during the previous month.  The report will include the date and time of arming/activation and reset.  ERCOT shall consolidate the monthly reports and forward to the Reliability Monitor and NERC Regional Entity on a quarterly basis.

(3)	If a RAS which removes generation from service operates more than two times within a six month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource Entity(ies) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource Entity(ies) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.