## Slide 1: ERCOT IBRTF: NERC and Other Industry Updates
Julia Matevosyan
08/11/2023
Chief Engineer
ESIG

## Slide 2: Agenda
FinGrid: Specific Study Requirements for Grid Energy Storage Systems
NERC Dynamic Modeling Guidance: Recommended Modeling Practices and List of Unacceptable Models
FERC Order Interconnection: Improvements to Generator Interconnection Procedures and Agreement

## Slide 3: Fingrid: Specific Study Requirements for Grid Energy Storage System
A large number of BESSs are planned to connect to the transmission grid in Finland.
Studies show that GFL IBR are unable to operate stably with higher shares of GFL IBR in the future.
Solution is to use GFM control to compensate for the reduction of synchronous generation and external system strength required by present GFL inverters to function properly.
The need is becoming obvious already now in weak grid regions, where connection of more GFL IBRs is not possible without further grid strengthening.
The use of GFM technology is also seen as beneficial because it improves connectivity of new IBRs
Fingrid decided to skip the initially-planned pilot projects stage and allow all customers to build GFM batteries in parts of grid where we are otherwise limiting connections until grid reinforcements.
To enable this, Fingrid defined Specific Study Requirements for BESS ( ≥30 MW, ≥110 kV) connected to specific locations, where use of grid forming controls (GFM) is seen as necessary.
Notes: According to the Grid Code, the Connectee shall request from Fingrid the assessment of a need for specific study during the preliminary planning stage of the BESS, so that the requirements are considered in the design and procurement of equipment.

## Slide 4: Fingrid: Specific Study Requirements for Grid Energy Storage System
A GFM IBR shall be able to self-synchronize, operate in stand-alone mode and provide synchronization services: synchronizing power, system strength, fault current and virtual inertial response (within current inverter rating)
The document describes functional requirements, simulation studies and field tests
The requirements are in addition to existing grid code specifications for energy storage systems, in case of conflict, GFM requirements prevail.
The requirements for GFM BESS are divided in
  functional requirements
  active power control and frequency control requirements
  voltage control and reactive power control requirements
  modelling requirements and
  test requirements
Notes: Field tests and simulation tests are necessary to ensure that the GFM control is implemented in a way that it supports the stable operation of the inverter dominated grid and that the unique characteristics of GFM are utilized in an appropriate way.

## Slide 5: Fingrid: Specific Study Requirements for Grid Energy Storage System
When the GFM BESS is reaching the current limit, stability and grid support must still be maintained, switching to GFL mode at the limit is not permitted.
GFM BESS shall continue providing GFM operational characteristics even at its highest and lowest allowable state of charge.
GFM shall provide autonomous, near-instantaneous frequency and voltage support by maintaining a nearly constant internal voltage phasor in the sub-transient time frame, including:
Phase jump performance: resist near-instantaneous voltage phase angle sub-transient time frame
System strength: resisting the change in voltage in the sub-transient time frame
Seamless transition between islanded and grid-connected operation
Positive damping: GFM shall present a positive resistance to the grid within frequency ranges 0–47 Hz and 53-250 Hz to prevent adverse interactions.
Notes: Phase jump performance: GFM shall resist near-instantaneous voltage phase angle changes by providing appropriate levels of active and reactive power output in the sub-transient time frame.
System strength: GFM shall improve the strength of the local network by resisting the change in voltage in the sub-transient time frame
Seamless transition between islanded and grid-connected operation is required: GFM shall be able to seamlessly respond based only on its local measurements to changes from a grid connected situation to an islanded situation and reconnect back again.
Positive damping: GFM shall present a positive resistance to the grid within frequency ranges 0–47 Hz and 53-250 Hz to prevent adverse interactions.
(especially important that the GFM shall not reduce damping of 0.2-0.5 Hz interarea oscillation modes)
Indicative response times i. Initial response within few milliseconds ii. Full response < 10 ms

## Slide 6: Fingrid: Specific Study Requirements for Grid Energy Storage System
Voltage balancing: GFM shall provide a closed loop path for unbalanced current to flow
Additions to active power control and frequency control requirements
Additions to voltage control and reactive power control requirements
Required simulation studies : a table with the list of disturbances to be tested & acceptance criteria, simulation software and BESS operating scenarios (prescribed values of SOC, P and Q). The list also includes loss of last synchronous generator in test network model – very similar to HECO and NERC’s white paper Grid Forming Functional Specifications for BPS-Connected BESSs
Additionally, hardware type test reports are required
Additional site tests and high level acceptance criteria: for phase jump, island operation (upstream 110 kV breaker is opened), measurement of power quality
Monitoring period after grid code tests, 30 days
Notes: GFM shall present negative sequence current to ensure that its internally generated voltage remains balanced during normal operation and disturbances

## Slide 7: Fingrid: Specific Study Requirements for Grid Energy Storage System – Current Status
Fingrid finalized and sent the requirements to their customers in June 2023.
They requirements will be published on Fingrid’s website after summer holidays in beginning of August. https://www.fingrid.fi/en/grid/grid-connection-agreement-phases/grid-code-specifications/grid-energy-storage-systems/
Currently the plan is to require GFM capabilities from BESS connected to parts of the grid with high penetration of inverters.
Fingrid plans to gather more experience from the current GFM projects and aims to make it a general requirement for all BESS systems next year.

## Slide 8: FERC Order: Improvements to Generator Interconnection Procedures and Agreement
Key Takeaways*
Developers will be expected to do more due diligence up-front - With increased penalties on withdrawing from the queue, developers will need to fully understand interconnection feasibility before applying for interconnection.
Some standardization across the US – with regard to cluster studies, material modification studies, affected system studies
Alternative transmission technologies for cost and time savings in the cluster study process
RMS Modeling Requirements: validated RMS models, both generic and user defined, are required in the early stages of interconnection
EMT modeling efforts are at the discretion of each transmission operator
Fault Ride-Through requirement
*Adapted from https://www.telos.energy/post/6-takeaways-from-ferc-order-2023-ferc-s-latest-ruling-on-interconnections
FERC Order https://www.ferc.gov/media/e-1-order-2023-rm22-14-000
Notes: The inclusion of alternative transmission technologies (GETs)-static synchronous compensators, static VAR compensators, advanced power flow control devices, transmission switching, synchronous condensers, voltage source converters, advanced conductors, and tower lifting- allows for the transmission provider to understand during the cluster study how alternatives to traditional network upgrades could benefit the cluster study through cost and time savings.

## Slide 9: NERC Dynamic Modeling Guidance
Dynamic Modeling Guidance
Recommended Modeling Practices and List of Unacceptable Models
Click here for: Dynamic Modeling Recommendations
NERC has released new dynamic modeling recommendations replacing the NERC Acceptable Model List and emphasizing recommended modeling practices and including a list of dynamic models considered unacceptable.
The guidance focuses on positive sequence dynamic models used for interconnection-wide grid stability analyses; but also includes recommendations for EMT models as well as GMD models covering a range of modeling scenarios relevant to the industry.
NERC will be periodically updating this guidance to ensure that relevant stakeholders are informed about the latest developments in dynamic modeling standards and practices.
Notes: The purpose of these recommendations is to provide clear and comprehensive guidance on the use of dynamic models for various types of reliability studies and to support consistent interconnection-wide base case development across the different Regional Entities.

## Slide 10: Electromagnetic Transient Simulation Workshop
Industry Workshop Announcement
Electromagnetic Transient Simulation (EMT) Workshop
Workshop Dates: August 24-25, 2023
Click here for: Registration Link
Deadline for Registration: July 27, 2023 (non-US citizens), August 14, 2023 (US citizens)
Organized at Oak Ridge National Laboratory, in collaboration with Department of Energy and North American Electric Reliability Corporation

## Slide 11
Julia Matevosyan
julia@esig.energy