## Slide 1
Large Loads – Impact on Grid Reliability and Overview of Revision Request Package
NPRR1191 and Related Revision Requests Workshop
August 16, 2023

## Slide 2: Workshop Agenda
Welcome and Antitrust Admonition
Large Loads – Impact on Reliability
Overview of the Large Load Revision Request Package
Next Steps

## Slide 3
Antitrust Admonition
To avoid raising concerns about antitrust liability, participants in ERCOT activities should refrain from proposing any action or measure that would exceed ERCOT’s authority under federal or state law. For additional information, stakeholders should consult the Statement of Position on Antitrust Issues for Members of ERCOT Committees, Subcommittees, and Working Groups, which is posted on the ERCOT website.1
Disclaimer
All presentations and materials submitted by Market Participants or any other Entity to ERCOT staff for this meeting are received and posted with the acknowledgement that the information will be considered public in accordance with the ERCOT Websites Content Management Operating Procedure.
1The document is available at http://www.ercot.com/about/governance/index.html.

## Slide 4
Large Loads – Impact on Grid Reliability

## Slide 5: Improvements for the Reliable Integration of Large Loads
ERCOT, like many grids around the world, is seeing an unprecedented amount of larger Loads interconnecting. To serve these Loads reliably requires changes to traditional processes. ERCOT has proposed a set of changes to integrate these new Loads and enhance the overall reliability of the grid.
These changes include:
A faster, more efficient interconnection process to meet the needs of these new Loads.
Load forecasting improvements to capture the unique demand characteristics of larger Loads.
Voltage ride-through standards to maintain grid resiliency during events.
Ramp rate limits to mitigate negative impacts on Ancillary Service availability.
A new Load category to reduce the need for Emergency Operations.

## Slide 6: Faster Load Interconnection Process
  Since January 2022, more than 2,700 MW (~5x city of Lubbock) of Load approved in the interim process representing 22 projects have been approved to energize in 2 years or less bypassing the established reliability process. Another 16,199 MW of proposed Load (55 projects) have requested energization dates on or before Dec 31, 2024.
New types of Large Loads want to interconnect in less than 2 years.
Traditional planning processes do not review this timeframe and cannot prepare the grid to serve this new Load reliably.
Implement a Large Load Interconnection study process to make it possible to interconnect new load reliably in less than 2 years.
Reliability Risk
Impact
Proposed Solution

## Slide 7: Load Forecasting Enhancement
ERCOT cannot readily identify larger load facilities and has limited visibility into their sensitivity to price and other factors.
ERCOT is seeing greater load forecast error on extreme or unusual operating days when an accurate forecast is most critical.
Implement 4CP and price responsive demand forecasts and require Loads 25 MW or greater to provide additional information to ERCOT.
Reliability Risk
Impact
Proposed Solution
  ERCOT has limited visibility into the location and consumption of all larger Loads. This has been evident during summer operations when high prices and 4CP response make industrial load usage difficult to forecast for upcoming days. Increased visibility into industrial load consumption would have also been useful during both Winter Storm Uri and Elliot, when larger Load usage was a critical forecasting input.

## Slide 8: Voltage Ride-Through Standards
ERCOT has experienced multiple events in the last year where a significant amount of Large Load unexpectedly disconnected from the grid.
Large Load behavior can magnify the severity of grid events, increasing the negative impact to reliability.
Establish a voltage ride-through standard that applies to all Loads 75 MW or greater.
Reliability Risk
Impact
Proposed Solution
See slide 12 for more events
  Multiple events have demonstrated new Large Loads are not always capable of remaining stable during voltage fluctuations. The most severe event occurred near Odessa at 3:50 AM on 12/7/22 when more than 1,600 MW of Load (including data centers, oil/gas load, and other industrial loads) unexpectedly disconnected from the grid due to a low-voltage fluctuation. System frequency increased to 60.235 Hz and did not return to normal for over 10 minutes. Large Loads can make a low-voltage event become a frequency control event.

## Slide 9: Frequency Control Improvements
Large Loads can change their MW consumption rapidly enough to exhaust available Regulation service.
ERCOT eventually will need to buy what may become an infeasible quantity of Regulation service to maintain frequency stability. This could add significant costs to ratepayers.
Create a path so as many Large Loads as possible can participate as Controllable Load Resources (CLRs). Establish ramp-rate standards for Large Loads that are not CLRs.
Reliability Risk
Impact
Proposed Solution
  Since January 2023, 49 SCED intervals have exceeded available Regulation due to rapid changes in Large Load consumption. The loss of available Regulation temporarily limits ERCOT’s ability to control frequency. This was not an issue prior to the connection of the 2700 MW of Large Loads. Ramp rate limits on Large Loads not controlled by SCED will help mitigate depletion of Regulation by Large Loads.

## Slide 10: Reducing Emergency Operations
Large Loads have exhibited inconsistent behavior during Resource scarcity events.
If ERCOT plans for expected Large Load response and the Load does not respond, it could drive the system into emergency conditions. If ERCOT plans for no response, it will increase consumer costs unnecessarily when the Load does respond.
Create a new Registered Curtailable Load category that ERCOT may curtail before shedding firm load.
Reliability Risk
Impact
Proposed Solution
  In the last two years, ERCOT has acquired some information regarding Large Load behavior during periods of Resource scarcity. Experience shows inconsistent response from Large Load sites that should be expected to reduce consumption. ERCOT needs the capability to coordinate Large Load response before curtailment of firm Load is required. For example, if Large Loads had not voluntarily curtailed on June 20, 2023 ERCOT would have been forced into Emergency Operations.

## Slide 11: Path Forward
Large Loads with demand flexibility have the potential to be an important tool for maintaining grid reliability.
For this flexibility to enhance rather than detract from grid reliability, it must be coordinated with generator dispatch. Participation of Large Load as CLRs, where applicable, is a necessary step in meeting this need.
Additional information collected from all larger Loads will enable ERCOT to improve its load forecasts and operational processes.
ERCOT is committed to working with all stakeholders in a transparent manner to utilize the flexibility offered by some Large Loads to ensure the reliability of the grid for all customers.

## Slide 12: List of recent Voltage Ride-Through events
Click to return to Slide 8

## Slide 13
Overview of Large Load Revision Request Package

## Slide 14: Scope of Proposed Changes in Large Load Revision Requests
Formalize the interim interconnection process and establish operational requirements for Large Loads (≥ 75 MW)
Require certain basic information about all Loads ≥ 25 MW (size, contact info, registration type, etc.)
Creation of a new ERCOT team to manage the interconnection process, analyze Large Load behavior and compliance, and support other affected ERCOT teams
  FTE impact is accounted for in ERCOT’s 2024 budget
ERCOT systems affected: RIOO, EMS, MMS, NMMS, PI, Grid-Geo, reporting and data replication
Preliminary IA: ~$1M

## Slide 15: Revision Request Package – Structure
NPRR1188 – CLR Nodal Settlement
Future CLR-related NPRR
NPRR1191
Definitions
Provision of Information
Ramp rate limits
Changes to SSO/SSR terminology
Interconnection fee and other changes
PGRR111
Handling of Large Loads in Planning studies
New interconnection process for Large Loads
  Studies
  Quarterly Stability Assessment
  Modeling
  Approval to Energize
Ongoing obligations for Large Loads
NOGRR256
Large Load voltage ride-through requirements
Curtailing of RCLs prior to EEA
Exemption of RCLs from TSP firm load shed obligations
Requires CLRs to be in SCED when consuming energy
Changes non-battery CLRs to Nodal settlement
CLR AS bids co-optimized in DAM
Could remove requirement that CLRs provide PFR if they are not providing AS
Could address impacts to outage coordination and Ops studies/systems
RRGRR036
New sections added to RIOO
New RIOO fields to support the interconnection process
Large Load RR Package
These RRs directly address Large Load issues
and will be covered at today’s workshop
Related NPRRs
These NPRRs may impact some Large Loads but are not
included in this package and will not be covered in detail today

## Slide 16: Revision Request Package – Interactive Directory
NPRR1188 – CLR Nodal Settlement
Future CLR-related NPRR
NPRR1191
Definitions
Provision of Information
Ramp rate limits
Changes to SSO/SSR terminology
Interconnection fee and other changes
PGRR111
Handling of Large Loads in Planning studies
New interconnection process for Large Loads
  Studies
  Quarterly Stability Assessment
  Modeling
  Approval to Energize
Ongoing obligations for Large Loads
NOGRR256
Large Load voltage ride-through requirements
Curtailing of RCLs prior to EEA
Exemption of RCLs from TSP firm Load shed obligations
Requires CLRs to be in SCED when consuming energy
Changes non-battery CLRs to Nodal settlement
CLR AS bids co-optimized in DAM
Could remove requirement that CLRs provide PFR if they are not providing AS
Could address impacts to outage coordination and Ops studies/systems
RRGRR036
New sections added to RIOO
New RIOO fields to support the interconnection process
Click on underlined text to see more detail

## Slide 17: New Defined Terms
Large Load – One or more Facilities at a single site with an aggregate peak Demand greater than or equal to 75 MW behind one or more common Points of Interconnection (POIs) or Service Delivery Points
Interconnecting Large Load Entity (ILLE) – Any Entity that has submitted a request to interconnect a Large Load to the ERCOT system. Equivalent to an Interconnecting Entity in the generation interconnection process
Large Load Interconnection Study (LLIS) – The set of interconnection studies done by the TSP for a Large Load connecting in 2 years or less
Registered Curtailable Load (RCL) – A Load registered with ERCOT that has agreed to curtail its consumption on instruction from ERCOT prior to EEA
Load Commissioning Plan – A schedule furnished by the ILLE detailing dates and peak Demand amounts from the Initial Energization date to the date peak consumption is reached
Other New or Modified Terms – Subsynchronous Ferroresonance (SSFR), Torque Amplification, Controllable Load Resource
Back to Directory
References – NPRR1191 2.1, PGRR111 2.1
Next Slide

## Slide 18: New Defined Load Type – Registered Curtailable Load (RCL)
New category of Loads developed in response to feedback from Large Load Customers that wish to help ERCOT avoid EEA events.
RCLs may be directed to curtail by ERCOT prior to entering emergency operations and must have a QSE to receive ERCOT instructions.
RCLs are not counted toward Transmission Operator EEA 3 firm Load shed obligations.
RCLs are eligible to participate in ERS.
RCLs are not a Resource and are not eligible to carry Ancillary Services.
References – NPRR1191 6.5.9.4.1, 16.20.1, NOGRR256 4.5.3.1
Firm
RCL
(new category)
NCLR
CLR
Types of “flexible” Load
Least Flexible
More
Flexible
Next Slide
Back to Directory

## Slide 19: Comparison of Load Types
 | Firm | RCL | NCLR | CLR
Must provide registration data to ERCOT |  |  |  | 
Is a Resource as defined in the Protocols |  |  |  | 
May be reduced to min Load in Planning studies for system capacity issues |  |  |  | 
May be dispatched like a Generation Resource in Planning studies |  |  |  | 
Required to have a QSE |  |  |  | 
May be curtailed by ERCOT at 3,100 MW PRC |  |  |  | 
May participate in Emergency Response Service (ERS) |  |  |  | 
May qualify to provide Ancillary Services |  |  |  | 
Can change Demand level outside of SCED |  |  |  | 
Rate at which Demand may change (ramp rate) will be restricted |  |  |  | 
Is dispatched by SCED at all times when consuming energy |  |  |  | *
Settled at Zonal prices |  |  |  | 
Settled at Nodal prices |  |  |  | *
* Pending approval of NPRR1188
Back to Directory

## Slide 20: Provision of Information from ≥ 25 MW Loads
Requires any existing or proposed Load 25 MW or greater at a single site to provide additional information to ERCOT via RIOO.
  Proposed Loads going through the new Large Load Interconnection Study (LLIS) process must submit their information prior to the start of the study.
  Proposed Loads not going through the LLIS have 30 days to submit information after signing a binding interconnection agreement with the interconnecting TSP.
  Existing Loads have 60 days to submit information once their consumption reaches 25 MW.
Prohibits affected proposed Loads from being added to the Network Operations Model and receiving Approval to Energize until information has been submitted.
References – NPRR1191 16.20, PGRR111 9.2.1, 9.2.2
More Details
Back to Directory

## Slide 21: Ramp Rate Limits
Similar to intermittent Resources, Large Loads registered as CLRs will be limited to a telemetered ramp rate of 20% per min. The actual ramping of these Loads will be managed by SCED.
All Large Loads that are not registered as CLRs will be subject to ramp rate restrictions, measured at the POI or Service Delivery Point:
  Lesser of 5% peak Demand or 20 MW per min when reducing consumption
  Lesser of 2% peak Demand or 8 MW per min when increasing consumption
These limits do not apply to NCLRs while appropriately responding to an ERCOT deployment.
Large Loads connected before the March 25, 2022 Market Notice will be grandfathered unless a material change to the Facility is made.
References – NPRR1191 6.5.7.12
Back to Directory

## Slide 22: SSO/SSR Changes
Numerous references to Subsynchronous Resonance (SSR) are updated to Subsynchronous Oscillation (SSO).
Defines how Large Loads are assessed for SSO vulnerability and how Large Loads are incorporated into SSO assessments for Generation Resources and transmission projects.
The SSO study is separate from the Large Load Interconnection Study (LLIS), but it will be scoped at the same time as the LLIS.
The Interconnecting Large Load Entity will be required to mitigate any SSO vulnerability identified during the initial SSO study prior to Initial Energization.
References – NPRR1191 3.22
Back to Directory

## Slide 23: Interconnection Fee and Other Changes
A $14,000 fee is added to the ERCOT Fee Schedule for LLIS studies.
Any non-netted Large Load not registered as a CLR or NCLR is added to the Peak Load Estimate used in the SARA.
  Other categories in the calculation already capture CLRs, NCLRs, and netted Loads.
The interconnection of a Large Load is added to the list in Section 3.3.2(1), Types of Work Requiring ERCOT Approval.
Adds a requirement that a Generation Resource adding 20 MW or more Load submit a new Reactive Power Study.
References – NPRR1191 3.2.6.2.1, 3.3.2, 3.15, Fee Schedule
Back to Directory

## Slide 24: Handling of Large Loads in Planning Studies
Adds a requirement to study the contingency loss of a Large Load in all planning studies in the ERCOT region.
Updates language in other paragraphs to add the opening of a line section without a fault as a valid transmission contingency. This is to align with current practice.
References – PGRR111 4.1.1.2
Back to Directory

## Slide 25: Large Load Interconnection Study (LLIS) – Concepts
A replacement for the current interim process in place since March 2022
Applies to new Loads of 75 MW or greater (or increases of 75 MW or greater) connecting within 2 years
Defines
  Studies to be performed
  Process and timeline for studies, modeling, and approval to energize
  Ongoing obligations for Large Loads
RIOO will be used to manage this interconnection process.
Wherever possible, the structure of the new Large Load process mirrors the existing interconnection process for generators.
References – PGRR111 6.6, Section 9
Next Slide
Back to Directory

## Slide 26: Large Load Interconnection Study (LLIS) Process
Similarities to the Interim Process
Process still applicable to Loads 75 MW or greater seeking interconnection within 24 months
Same suite of studies as the interim process
TSPs perform the studies, ERCOT reviews and determines operating limit until transmission upgrades in place
Allows for approvals of more Load conditioned on transmission upgrades
The new LLIS process is designed to formalize current practices with some modifications to cover gaps identified in the interim process that has been in effect since March 25, 2022.
Changes from the Interim Process
Scoping meeting to start the LLIS
Allows Loads intending to qualify as a CLRs to be studied as flexible and potentially interconnect more MWs*
Some Large Loads must be included in the quarterly stability assessment (QSA)
More formal Approval to Energize process
Co-located Loads 20-75 MW only require a new Reactive Study – LLIS studies are no longer needed
Next Slide
Back to Directory
* Pending approval of NPRR1188

## Slide 27: LLIS Process Flow – High-Level Overview
ILLE Requests LLIS
Kick-off Meeting Held
TSP Performs Studies
ERCOT Determines Reliability Limit
Large Load Added to Models
Approved to Energize
ILLE Requests Approval to Energize
Large Load Studied in QSA
(if required)
(IF REQUIRED)
Back to Directory

## Slide 28: Large Load Interconnection Studies
Requires that Large Loads be evaluated through a steady-state analysis, a system protection analysis, and a dynamic stability analysis, unless waived by ERCOT.
The steady-state analysis
  Studies the full proposed amount of Load for the purpose of identifying needed transmission improvements; and
  Studies the Load according to its registration type (CLR, NCLR, RCL, firm) for the purpose of identifying how much Load can be reliably interconnected by the customer’s desired Initial Energization date.
  This study may result in a lesser amount of Load being approved for interconnection until transmission upgrades are in service.
References – PGRR111 9.3.4
Next Slide
Back to Directory

## Slide 29: Steady-State Study – Examples
Notes
Since the steady-state study did not identify reliability violations under any Planning contingency, the study concludes that 300 MW could be reliably interconnected regardless of the Load’s planned participation type.
Scenario 1
A customer requests to interconnect a 300 MW Load via the LLIS process. The steady-state study shows no reliability violations under any Planning contingency.
Chart: Desired Load Participation Type
| Firm | CLR
Reliable Interconnection Amount (MW) | 300 | 300
Next Slide
Back to Directory

## Slide 30: Steady-State Study – Examples
Scenario 2
A customer requests to interconnect a 300 MW Load via the LLIS process. The steady-state study identifies a N-1 contingency that overloads a nearby transmission line to 108% when the Load is at 300 MW. Reducing the Load to 210 MW resolves the issue.
Chart: Desired Load Participation Type
| Firm | CLR
Reliable Interconnection Amount (MW) | 210 | 300
Notes
The proposed Firm load would be limited to 210 MW until the needed transmission upgrades are in service.
The proposed CLR would be allowed to connect the full 300 MW. In operation, SCED would be able to dispatch the CLR according to its bid-to-buy curve to resolve the N-1 constraint if needed.
Back to Directory
Next Slide

## Slide 31: Steady-State Study – Examples
Scenario 3
A customer requests to interconnect a 300 MW Load via the LLIS process. The steady-state study identifies a N-1 contingency that overloads a nearby transmission line to 130% when the Load is at 300 MW. The overload is reduced to 125% at 270 MW of Load and to 100% at 150 MW.
Chart: Desired Load Participation Type
| Firm | CLR
Reliable Interconnection Amount (MW) | 150 | 270
Notes
The proposed Firm load would be limited to 150 MW until the needed transmission upgrades are in service.
The CLR would be limited 270 MW until the needed transmission upgrades are in service.
  An overload of greater than 125% is considered a cascading condition and is not resolvable by SCED.
  The load will be limited to the point where any overload can be resolved via SCED dispatch.
Back to Directory
Next Slide

## Slide 32: Steady-State Study – Examples
Scenario 4
A customer requests to interconnect a 300 MW Load via the LLIS process. The steady-state study does not identify any thermal violations but does identify a N-1 contingency that creates a low voltage condition when the load is greater than 190 MW.
Chart: Desired Load Participation Type
| Firm | CLR
Reliable Interconnection Amount (MW) | 190 | 190
Notes
SCED does not resolve voltage violations.
The proposed Firm load would be limited to 190 MW until the needed transmission upgrades are in service.
The CLR would also be limited 190 MW until the needed transmission upgrades are in service.
Back to Directory
Next Slide

## Slide 33: Large Load Interconnection Studies
The system protection (short circuit) analysis
  Identifies the maximum fault currents at the interconnection substation for sizing switching devices and determining relay settings.
  This study is required for reliable interconnection but will not limit the size of the Load.
The dynamic stability analysis
  Studies stability of the ERCOT system in terms of angular stability, voltage stability, and excessive frequency excursions. Other studies may be performed.
  If the TSP identifies instability:
    The proposed Load will need to be included in the next quarterly stability assessment (QSA)
    The TSP should identify mitigation, including transmission improvements
  This study may result in a lesser amount of Load being approved for interconnection until transmission upgrades are in service.
References – PGRR111 9.3.4
Back to Directory

## Slide 34: Large Loads in the Quarterly Stability Assessment (QSA)
Large Loads subject to the LLIS will be included in the QSA if:
  ERCOT determines during the LLIS scoping process that the Load may have an impact on an existing GTC, or
  The LLIS stability study identifies one or more stability issues
Large Loads subject to the QSA will need to meet the same deadlines as Generation Resources and will not be permitted to energize prior to being included in a QSA.
Large Loads not subject to the LLIS will not be included in the QSA but will be reviewed as part of the annual stability assessment.
References – PGRR111 5.3.5, 9.3.4.3, 9.4
Back to Directory

## Slide 35: Modeling of Large Loads
Establishes a set of criteria that must be met before a Large Load may be included in SSWG base cases and the Network Operations Model.
No Large Load may be modeled prior to signing a binding interconnection agreement with the TSP.
The interconnecting TSP will be responsible for modeling Large Loads not co-located with a Generation Resource, subject to the new restrictions.
Large Loads co-locating with a Generation Resource will be treated as a modification of the registration data for that Resource, and it will be the responsibility of the RE for the Generation Resource to submit updated registration data to ERCOT. ERCOT will then model the Load on the RE’s behalf using that data.
References – PGRR111 6.6
Back to Directory

## Slide 36: Approval to Energize Process for Large Loads
Requires all Large Loads (even those not going through the LLIS) to provide to ERCOT a Load Commissioning Plan before receiving Approval to Energize.
Several validation checks are also performed by ERCOT:
  The Large Load has been properly modeled as described in PG 6.6
  The Load has been studied in the QSA, if applicable
  The Load has completed any SSO mitigation and monitoring, if required
  The telemetry for the Load is in place and accurate
  The Load has provided a current Load Commissioning Plan
References – PGRR111 9.5, 9.6
Next Slide
Back to Directory

## Slide 37: Approval to Energize Process for Large Loads
After receiving approval to energize, Large Loads that indicated during the planning phase an intent to register as a Controllable Load Resource (CLR) or Load Resource (NCLR) will be limited to 10 MW of consumption until the Load has completed all required qualification tests.
As with the Generation Interconnection process, the full Approval to Energize process for Large Loads will be described in a Handbook.
References – PGRR111 9.6
Back to Directory

## Slide 38: Continuing Obligations for Large Loads
Requires the Interconnecting Large Load Entity (ILLE) to maintain current project information in RIOO.
Requires the ILLE to maintain the Load Commissioning Plan for 2 years after Initial Energization and update the document within 5 business days of a material change.
Prohibits the Large Load from exceeding any limit placed on it by ERCOT.
Once a transmission upgrade identified in the LLIS becomes operational, the Large Load may increase its Demand level after receiving written approval from ERCOT.
References – PGRR111 9.6
Back to Directory

## Slide 39: Voltage Ride-Through (VRT) Requirements
Historically, engineers have considered some load reduction or tripping during a fault or low-voltage event as permissible and sometimes preferable, particularly for Loads that increase real or reactive power consumption at lower voltages.
However, as the amount of voltage-sensitive Load increases and system strength decreases, the likelihood of large amounts of load loss, perhaps gigawatts, during a voltage excursion increases, which can lead to frequency instability and potentially other reliability issues.
To address this reliability risk, ERCOT proposes a ride-through standard for Large Loads.
In developing these requirements, consideration was given to IBR ride-through requirements, CBEMA (1970s), ITIC (1990s), and IEEE 1668 (2017).1
1 https://standards.ieee.org/ieee/1668/6798/
Next Slide
References – NOGRR256 2.11
Back to Directory

## Slide 40: Voltage Ride-Through (VRT) Requirements (1 of 2)
REQUIREMENT 1: Large Loads that interconnect to the ERCOT Transmission Grid must be designed and relays must be set to ride through and continue to consume power for the following operating conditions in Tables A and B, as measured at the Large Load’s Point of Interconnection:
From ITIC Curve
Based on IEEE 1668 Single-Phase and Phase-Phase Curve
Based on ITIC Curve, but extended to ride-through fault duration
Based on proposed IBR requirements in NOGRR245
Next Slide
References – NOGRR256 2.11
Back to Directory

## Slide 41: Voltage Ride-Through (VRT) Requirements (2 of 2)
REQUIREMENT 2: Large Loads that interconnect to the ERCOT Transmission Grid and that consist of primarily power electronic equipment and/or variable speed drives must be designed to use constant current control and may not be designed to use constant power level control.
The purpose of this requirement is to prevent Loads that are riding-through the voltage excursion from exacerbating the low-voltage conditions.
A similar recommendation was made in the NERC-WECC paper on electric vehicle charging performance: https://www.nerc.com/comm/RSTC/Documents/Grid_Friendly_EV_Charging_Recommendations.pdf
References – NOGRR256 2.11
Back to Directory

## Slide 42: Load Shed by RCL Prior to EEA
ERCOT may curtail any Registered Curtailable Loads (RCLs) that are still consuming energy when PRC drops below 3,100 MW and is not expected to recover within 30 minutes
  Occurs before ERS may be deployed
QSEs with RCLs will shed their share of 100 MW blocks at the instruction of ERCOT. RCLs must comply with the instruction from their QSE to curtail.
Deploying RCLs will trigger the Reliability Deployment Price Adder (RDPA)
RCLs are not counted toward Transmission Operator EEA 3 firm Load shed obligations
References – NPRR1191 6.5.7.3.1, 6.5.9.4.1, NOGRR256 4.5.3.4, 4.5.3.5
PRC
1000 MW
1500 MW
2000 MW
2500 MW
3000 MW
3500 MW
PRC <1000 MW
Firm Load shed
in 100 MW blocks
PRC <1430 MW
EEA Level 3
PRC <1750 MW
EEA Level 2
PRC <2300 MW
EEA Level 1
PRC <3100 MW – May deploy Registered Curtailable Loads
PRC <3000 MW
May deploy ERS
Back to Directory
PRC <1500 MW
EEA Level 3 and firm Load shed in 100 MW blocks
PRC <2000 MW
EEA Level 2
PRC <2500 MW
EEA Level 1
PRC <3000 MW
May deploy ERS
PRC <3100 MW – May deploy Registered Curtailable Loads
Current
Post-NPRR1176
(Expected October 1, 2023)

## Slide 43: Additions and Changes to RIOO
Two new sections will be added to RIOO:
  Large Load Interconnection Study (LLIS) – this section will also handle the provision of information by Loads 25 MW and greater
  Registration as a Registered Curtailable Load (RCL)
During the LLIS, RIOO will be used in a similar manner to the Generation Interconnection process, allowing coordination between ERCOT, the TSP(s), and the ILLE
Existing fields from the Generation Resource and Load Resource registration processes that are applicable to Large Loads will be reused where possible.
  Some new fields related to Large Loads and the Load Commissioning Plan are added.
References – NPRR1191 16.20, PGRR256 Section 9, RRGRR036
Next Slide
Back to Directory

## Slide 44: RIOO – New Fields
Required of all Loads 25 MW and greater
  Customer contact information
  Information needed to identify the Load in the Network Operations Model
  Load Registration Type - CLR, Load Resource (“NCLR”), RCL, firm
  Load Classification (Data Center, Crypto, Hydrogen, Manufacturing, Other…)
Additional information required for Loads going through the LLIS process
  Load Commissioning Plan (required of all Large Loads)
  LLIS Application Fee
Information required of RCLs only
  Portion of the Load that is curtailable
References – NPRR 16.20, PGRR Section 9, RRGRR
Back to Directory

## Slide 45: Benefits of More Loads Participating in SCED
Benefits for Loads
Takes the guesswork out of being responsive to system prices
Still free to set strike price(s) via bid-to-buy curve
Eligibility to provide AS
Potential pricing and settlement benefits*
The optimal solution for grid reliability is for more Loads to participate in economic dispatch (SCED) as a Controllable Load Resource (CLR).
* Pending approval of NPRR1188
Benefits for ERCOT
Load ramping is coordinated with other grid reliability needs
More data available to aid in forecasting and reliability studies
More Loads eligible to provide AS
Next Slide
Back to Directory

## Slide 46: NPRR1188 – CLR Nodal Settlement
There are several provisions of NPRR1188 that will impact Large Loads participating as a CLR if adopted.
  A CLR must participate in SCED when consuming energy.
  A CLR will be dispatched according to Nodal Shift Factors (same as Generation Resources).
  CLR Ancillary Service bids will be co-optimized in the Day Ahead Market.
  CLRs will receive Nodal settlement instead of Zonal settlement.
Additionally, NPRR1058 (already approved, pending ERCOT market system upgrades) will allow the QSE for a CLR to submit a new Energy Bid curve at any time.
Back to Directory

## Slide 47
Large Load Revision Request Package
Next Steps

## Slide 48: Future CLR-related NPRR
ERCOT expects to introduce an additional CLR-related NPRR in the near future to address some other topics discussed at the LFLTF. This NPRR will likely include the following concepts:
Lower the barrier to qualifying as a CLR by modifying the Primary Frequency Response (PFR) requirement
  CLRs that are not qualified to provide AS (and thus are only participating in SCED) would not have to provide PFR.
  CLRs qualified to provide one or more AS products would also have to provide PFR.
Allow for CLRs to be treated as dispatchable in Outage Coordination studies and other Operations studies.
Back to Directory

## Slide 49: Future topics
In addition to future discussion on the proposed Revision Requests, some items from the LFLTF Issues List remain unresolved and require additional discussion:
LFL-15: Determine if or how Large Loads, specifically those modeled as CLRs, should be considered in constraint competitiveness test and Resource mitigation processes.
LFL-26: Evaluate rules and process changes that may be necessary for considering Large Loads, particularly those modeled as CLRs, in near-term reliability studies, including the Reliability Unit Commitment (RUC) process.
LFL-31: Consider impacts to Transmission Operator UFLS obligations.
LFL-35: Consider what changes to outage coordination processes are needed to incorporate Large Loads, including Load assumptions for outage coordination studies.

## Slide 50: Joint LFLTF Meetings
The August LFLTF Meeting will be a joint WMS and LFLTF meeting to discuss this package of Revision Requests.
The September meeting LFLTF meeting will likely be a joint meeting with OWG and PLWG to discuss the NOGRR, PGRR, and RRGRR.

## Slide 51: Questions