## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE. High-side voltage for transformers
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## MTE(2023)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items | From Acronym | To Acronym | ERCOT Equip Name | ERCOT Contingency ID
CNPE | Addicks - TH Wharton | LN | 345 | 22/4 | Roans Prairie - Singleton 345 kV & Singleton - Tomball 345 kV | TH Wharton - Zenith 345 kV | RT | Planned | [6 empty] | THW | ADK | ADKTHW71A | SADKTHW5
CNPE | Addicks - White Oak | LN | 345 | 23/1 | DCKT Obrien-WAP (OB-WAP98 & OB-WAP99) 345 kV | Jeanetta - Westwood 138 kV | RT | Planned | [6 empty] | WO | ADK | ADKWO_71 | SWOADK5
ETRTX | Agave - Whitepoint | LN | 138 | 22/12, 23/3 | DCKT White Point - Nueces Bay & Portland & Gibbs 138kV, Whitepoint Auto 345_1 345/138 kV, Lon Hill - Whitepoint 345 kV, Weil Tract - Lon Hill 138 kV | Lon_Hill - Calallan Waterworks Tap 69 kV, Lon_ Hill - Koch_ Hearns Ferry 138 kV | RT | Planned | [6 empty] | PELICAN | WHITE_PT | PELICA_WHITE_1 | SPELWHI8
AEP | Air Liquide Ingleside - … - Dupont Switch - Ingleside & Oxychem Ingleside | LN | 138 | 18/1, 17/8, 16/4 | Dupont Pp1 Ingleside to Ingleside Cogen Sw 138 kV (3A), Lon Hill to Coleto Creek 345 kV, Dupont Sw - Ingleside to Ingleside Cogen Sw 138 Kv | Duppont Pp1 Ingleside - Duppont Sw Ingleside 138 kV, Lon Hill - Pawnee Switching Station 345 kV, Dupont Pp1 - Ingleside to Dupont Sw - Ingleside 138 kV | ST, RT | Planned, Forced | [6 empty] | ALIQUING | ALIQUSW | ALIQUI_ALIQUS1 | SALII_D8
AEP | Airline AEP - … - Westside AEP | LN | 138 | 21/2, 20/3 | Gila-…-Whitpoint 138 kV, Holly to Westside AEP 138 kV | Nueces Bay-Whitepoint 138 kV , Arcadia - Southside 138 kV | RT | Planned | [6 empty] | AIRLINE, CABANISS | CABANISS, WESTSIDE | AIRLIN_CABANI11, CABANI_WESTSI1 | SCABWES8
CNPE | Airpro - Boggy | LN | 138 | 23/1 | Jefferson - College 138 kV | Conial - Philip 138 kV | RT | Planned | [6 empty] | AZ | BOG | AZ_BOG85A | SAZBOG8
AEP | Ajo - … - Rio Hondo | LN | 345 | 17/2, 16/2 | DCKT Lon Hill - North Edinburg 345 kV & Orange Grove Sw 138 kV | Celanese Bishop - Nelson Sharpe 138 kV, Lon Hill - Bessel 138 kV | ST | Planned | [6 empty] | AJO | MAGICVAL | AJO_MAGICV1 | SAJORI25
AEP | Ajo - Cebolla | LN | 345 | 22/3, 22/5 | Fowlerton - Lobo 345 kV, LON HILL - NELSON SHARPE 345 kV | North Laredo Switch - Piloncillo Ranch 138 kV, Celanebi Bishop - Kleberg Aep 138 kV | RT | Planned | [6 empty] | CEBOLLA | AJO | AJO_CEBOLL1 | SAJ2CEB5
TNMP | Alvin TNP - Mainland TNP | LN | 138 | 21/11 | Meadow - Ph Robinson 345 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned | [6 empty] | MAINLAND | ALVIN | 138_ALV_MNL | SALVMAI8
ONCOR | Anna Switch - Cedar Elm Switch | LN | 345 | 22/3 | Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned | [6 empty] | CDESW | ANASW | 38025_A | SCDEANA5
ONCOR | Anna Switch - Krum West Switch | LN | 345 | 22/3, 21/12 | Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned | [6 empty] | KRWSW | ANASW | 38010_A | SANAKR15
AEP | Aransas Pass - Gregory | LN | 69 | 21/6 | Rincon Auto 69A1 138/69 kV | Whitepoint 138_69A1 138/69 kV | RT | Planned | [6 empty] | ARANSASP | GREGORY | ARANSA_GREGOR1 | SGREAR29
AEP | Armstrong Aep - … - Raymondville 2 | LN | 138 | 21/1, 16/3 | Lon Hill-Nelson Sharpe 138 kV, Valley Import | Celanese Bishop - Kleberg AEP , N/A | RT | Planned, Forced | [6 empty] | RAYMND2, ARMSTRON | MV_YUTT, MV_YUTT | MV_YUT_RAYMND1, ARMSTR_MV_YUT1 | SARMRA38
LCRA, ONCOR | Austrop - Sandow Switch (440) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV (1661_A), Gilleland Creek - Mcneil 138 kV | RT | Planned | [6 empty] | SNDSW | AUSTRO | 440 | SSNDAU15
LCRA, ONCOR | Austrop - Sandow Switch (450) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV (1661_A), Gilleland Creek - Mcneil 138 kV | RT | Planned | [6 empty] | SNDSW | AUSTRO | 450 | SSNDAUS5
LCRA, STEC | Bakersfield - Cedar Canyon | LN | 345 | 22/4 | Midessa South Sw - Odessa EHV Switch 345 kV & Morgan Creek Ses -…- Quail Switch 345 kV, DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 kV | Midessa South SW AXFMR1 345/138 kV, Dewey Lake Tap - Polecat Creek Switch 138 kV, Falcon Seaboard - Morgan Creek Ses 345 kV, Odessa - Odessa North 138 kV | RT | Planned | [6 empty] | CEDACA | BAKESW | BAKRFLD_CEDCAN | SBAKSCH5
GAR, LCRA | Bakersfield - Nevill Road Switch | LN | 345 | 22/4 | Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 kV | Odessa - Odessa North 138 kV | RT | Planned | [6 empty] | NEVILLSW | BAKESW | NEVILL_BAKESW1 | SBAKNOR5
CNPE | Baytown - Miller | LN | 138 | 21/2 | DCKT Chambers-King & Chambers Jordan-North Belt 345 kV | Exxon - Lynch 138 kV | RT | Forced | [6 empty] | BT | MLR | BT_MLR88A | SBTMLR8
CNPE | Bellaire - Kirby | LN | 138 | 21/10 | Eastside - Polk 138 kV | Downtown - Polk 138 kV | RT | Planned | [6 empty] | BI | KB | BI_KB_37A | SKBBI8
ONCOR | Benbrook Switch - Parker Switch | LN | 345 | 21/10 | Comanche Peak Ses - Mitchell Bend Switch 345 kV & Comanche Peak Ses - Wolf Hollow 345 Switch 345 kV, DBCKT Comanche Peak Ses - Parker Switch 345 kV | Benbrook Switch - Parker Switch 345 kV (6042_A) | RT | Planned | [6 empty] | BNBSW | PKRSW | 6005_A | SBNBPKR5
ONCOR | Benbrook Swith - … - Timberview Switch | LN | 345 | 20/10, 19/11, 17/3, 17/2 | DCKT Wedgewood Sw - Benbrook Switch 138 kV, DCKT Timberview Switch - Comanche Peak SES & Carmichael Bend Switch 345 KV | Hemphill - Mistletoe Heights 138 kV | RT | Planned, Forced | N | [5 empty] | BNBSW | SYCRK | 6000_A | SSYCEV25
LCRA | Benedum - Midkiff Switch | LN | 138 | 22/9 | SKYWEST to SPRABERRY SWITCH LIN 1 | Smidla Midland - Ctfld Sub 138 kV | RT | Planned | [6 empty] | BENEDU | MDKSW | 631T631 | SBENUPT8
LCRA | Bergheim - Hays Energy | LN | 345 | 21/10, 22/7,22/8, 23/2, 23/3, | Cagnon - Kendall 345 kV & Cico - Menger Creek 138 kV, Cagnon - Kendall 345 kV & Cico - Comfort 138 kV, DCKT Cagnon-Kendall 345 kV&Txresch-Tally_Rd 138 kV | Medina Lake - Pipe Creek 138 kV, Bergeim - Kendall 345 kV, Bergheim AT1 345/138kV, Helotes - Ranchtwn 138 kV, Medila Lake - Pipec Creek 138 kV | RT | Forced | [6 empty] | BERGHE | HAYSEN | 398T3891 | SHAYBER5
LCRA | Bergheim - Kendall | LN | 345 | 20/12 | DCKT Cagnon-Kendall 345 kV & Cico-Comfort 138 kV, Zorn - Haysen 345KV | Mason Creek - Bandera 138 kV, Bergheim Auto | RT | Planned | N | [5 empty] | BERGHE | KENDAL | 656T6561 | SKENBER5
AEP | Bessel - Lon Hill | LN | 138 | 22/3 | Fowlerton - Lobo 345 kV | Falfurrias - Premont 69 kV | RT | Planned | [6 empty] | BESSEL | LON_HILL | BESSEL_LON_HI1 | SBESLON8
STEC | Bevo Auto BEVO 138/69 kV | XF | 138 | 15/6 | Bevo Sub to Asherton 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned | [6 empty] | BEVO |  | BEVO | XBEV89
ONCOR | Big Spring Switch -…- Natural Dam | LN | 138 | 21/11, 21/10 | Grady - Brown 138 kV, DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses | Big Spring West - Stanton East 138 kV | RT | Planned | [6 empty] | BSPSW | BEALS | 6315_A | SSTABS18
AEP | Big Three - … - Bp Chem Vistron4 | LN | 138 | 17/6 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Formosa - Lolita 138 kV | RT | Planned, Forced | [6 empty] | BIGTRE | BLCBAYU4 | BIGTRE_BLCBAY1 | SBIGVIS8
AEP, STEC | Blessing - Danevang Switching Station | LN | 138 | 17/5 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Formosa - Lolita 138 kV | RT | Planned | [6 empty] | DANEVA | BLESSING | DANEVANG | SDANBLE8
AEP | Blessing - Stp Switch | LN | 138 | 18/1 | Lane City to Blessing 138 kV | El_Campo - Lane City Pump 138 kV | RT | Forced | [6 empty] | BLESSING | STP | BLESSI_STPSW1 | SBAYBLE8
CNPE | Boggy - Pair | LN | 138 | 22/10 | DCKT Exxon - Baytown & SR Bertron - Texas 138 kV, DCKT SR Bertron - Quanab & Dowlap 138 kV | Jefferson - Sc Channel 138 kV | RT | Forced, Planned | [6 empty] | BCV | PSA | BCVPSA | SBCVPSA8
AEP, ONCOR | Bowman Switch - Riley (34570) | LN | 345 | 21/3 | DCKT Clear Crossing-Coulomb & Clear Crossing-Pendulo 345 kV | Fisher Road Switch - Riley 345 kV | RT | Planned | N | [5 empty] | RILEY | BOMSW | 34570_A | SBOMRI25
ONCOR, ETT | Bowman Switch -…- Riley (34560) | LN | 345 | 21/3 | DCKT Clear Crossing-Coulomb & Clear Crossing-Pendulo 345 kV | Fisher Road Switch - Riley 345 kV | RT | Planned | N,Y | [5 empty] | RILEY | BOMSW | 34560_A | SBOMRI15
AEP | Brackettville - … - Hamilton Road | LN | 138 | 18/4 | DCKT Big Hill to Kendall 345 kV | Hamilton Road - Maverick 138 kV | RT | Planned | [6 empty] | HAMILTON | PINTCR | 464T464 | SBRAHAM8
CPS | Braunig - Calaveras | LN | 345 | 21/1 | DCKT Skyline-Calaveras 345 kV | Cagnon - Calaveras 345 kV | RT | Planned | N | [5 empty] | CALAVERS | BRAUNIG | N5_U31 | SBRACAL5
CPS | Brooks - Southton | LN | 138 | 22/12 | DCKT Calavers - Kirby & Beck Rd 138kV | Harlanda - Southsan 138 kV, Stockdale - Sutherland Springs 138 kV | RT | Planned | [6 empty] | V2 | Z5 | V2_Z5 | SV2Z58
ONCOR | Brown - Buzzard Draw Switch Lin _A | LN | 138 | 22/5 | Wett_grelton to ODESSA EHV SWITCH LIN 1 | Luther - Vealmoor 138 kV | RT | Planned | [6 empty] | BUZSW | BROWN | 15055 | SBROBUZ8
ONCOR | Brown Switch -…- Killeen Switch | LN | 345 | 21/6, 20/12, 22/9, 22/12 | Comanche Sw (Oncor)-Comanche Peak 345 kV, DCKT Bighil-Kendall 345kV | Comanche Tap - Comanche Switch (oncor) 138 kV, Yellow Jacket - Treadwell 138 kV | RT | Planned, Forced | N | [5 empty] | BWNSW | KLNSW | 35090_A | SKLNBWN5
ONCOR | Brownwood - … - Brownwood Switch | LN | 138 | 17/5, 17/4, 17/3, 17/2 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Holder Auto FMR1 138/69 kV | RT, ST | Planned | [6 empty] | BRNSO | BRNWD | 670_A | SBRNCMP8
AEP | Bruni - Crestonio | LN | 138 | 15/6, 15/5 | Laquinta to Lobo 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y, N | [5 empty] | BRUNI4 | CRESTONI | BRUNI4_CRESTO1 | SCREBRU8
TMPA | Btu_Jack_Creek - Gibbons Creek | LN | 345 | 17/4, 16/1 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Twin Oak Sw 345 kV, BTU_Jack_Creek Auto XF1 345/138 kV | RT, ST | Planned | Y | [5 empty] | GIBCRK | JK_CK | GC_JK | SJK_GIB5
ONCOR | Buckhorn Switch - Killeen Switch (35092) | LN | 345 | 22/12 | Comanche Sw (Oncor)-Comanche Peak 345 kV | Comanche Tap - Comanche Switch (oncor) 138 kV | RT | Planned | [6 empty] | KLNSW | BUCSW | 35092 | SBUCKLN5
CNPE | Bunker - H O Clarke | LN | 138 | 21/9 | Meadow - Oasis 345 kV | Blodgett - Garrott 138 kV | RT | Planned | [6 empty] | BUN | HOC | BUNHOC08 | SBUNHO28
ONCOR | Burwick Switching Station - Graham SES | LN | 345 | 21/10 | DBCKT Graham Ses - Parker Switch 345 kV | Barton Chapel Wind Farm - Graham Switch 138 kV, Barton Chapel Wind Farm - Oran Sub 138 kV | RT | Planned | [6 empty] | BURSW | GRSES | 36030_A | SGRSJC25
ONCOR | Buzzard Draw Switch -…- Koch Tap | LN | 138 | 22/5 | Wett_grelton to ODESSA EHV SWITCH | Luther - Vealmoor 138 kV | RT | Planned | [6 empty] | BUZSW | KOCHTAP | 15060_A | SKOCBUZ8
CPS | Cagnon - Calaveras | LN | 345 | 17/8 | DCKT Calaveras to Skyline 345 kV | Braunig - Cagnon 345 kV | RT | Forced | [6 empty] | CALAVERS | CAGNON | N5_R5 | SCAGCA25
CPS | Cagnon - Howard | LN | 138 | 23/3 | DCKT Calavers-Kirby&Beck_Rd 138kV | Merida - Wstside 138 kV | RT | Planned | [6 empty] | CAGNON | S1 | R4_S1 | SS1CAG8
CPS | Calaveras - Skyline (N5_P4_1) | LN | 345 | 22/4, 22/3, 17/12, 17/5, 22/5 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV, HILL COUNTRY to CAGNON 345 kV | Skyline - Calaveras 345 kV, Pawnee Switching Station - Calaveras 345 kV, Skyline - Elmcreek 345 kV, Coleto Creek - Rosata Tap 138 kV, Cagnon - Calaveras 345 kV, Pawnee Swithing Station Auto XF1 345/138 kV, Cagnon Auto XFMR4L-H 345/138 kV | RT | Planned, Forced | [6 empty] | CALAVERS | SKYLINE | N5_P4_1 | SSKYCA25
CPS | Calaveras - Skyline (N5_P4_2) | LN | 345 | 22/4, 22/3, 17/12, 22/5 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV, HILL COUNTRY to CAGNON 345 kV, CAGNON to BRAUNIG 345 kV | Pawnee Switching Station - Calaveras 345 kV, Pawnee Switching Station Auto XF1 345/138 kV, Skyline - Elmcreek 345 kV, Coleto Creek - Rosata Tap 138 kV, Cagnon - Calaveras 345 kV, Cagnon Auto XFMR4L-H 345/138 kV | RT | Planned | [6 empty] | CALAVERS | SKYLINE | N5_P4_2 | SSKYCAL5
AEP | Campwood - … - Rock Springs | LN | 69 | 21/9 | DBCKT Big Hill - Kendall 345 kV | Friess Ranch - Rocksprings 69 kV | RT | Planned | [6 empty] | NEWBARKS | CAMPWOOD | CAMPWO_NEWBAR1 | SCAMROC9
ONCOR | Carmichael Bend Switch - Mitchell Bend Switch | LN | 345 | 23/3 | Benbrook Switch - Parker Switch (6042) 345 kV | Benbrook Switch - Parker Switch (6005) 345 kV | RT | Planned | [6 empty] | MBDSW | CMBSW | 6017 | SMBDCMB5
AEP | Carrizo Springs - Crystal City | LN | 69 | 20/10 | Asherton-Bevo 138 kV | Bevo - Brundage Sub 69 kV | RT | Planned | Y, N | [5 empty] | CARRIZO | CRYSTAL | CARRIZ_CRYSTA11 | SCARCRY9
ONCOR,TNMP | Carrollton Northwest - Lakepointe Tnp | LN | 138 | 22/12, 23/4 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | South Tnp - Ti TNP 138 kV | RT | Planned | [6 empty] | CRLNW | LKPNT | 591_A | SLKPCRL8
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (105_A) | LN | 345 | 2018 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | ADD | [7 empty] | CRLNW | LWSSW | 105_A | SLWSCRL5
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (83) | LN | 345 | 17/3 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | CRLNW | LWSSW | 83 | SKRWCR25
AEP | Carver - Live Oak Aep | LN | 138 | 23/2 | DCKT Twin Buttes-DivideSwitchyard 345 kV | Hargrove - Twin Buttes 138 kV | RT | Forced | [6 empty] | LVOK | CARVER | CARVER_LVOK1 | SCARLVO8
LCRA | Castle Mountain - Crane Lcra | LN | 138 | 55/5, 22/7 | DCKT LCRA Crane - King Mountain West Tap & AND Castillo 138 kV, LCRA Crane - Castiollo 138 kV | Rio Pecos - LCRA crane Lcra 138 kV | RT | Planned | [6 empty] | LCRANE | CASTMO | 716T716 | SLC2CAS8
CNPE | Cedar Bayou Plant - Center | LN | 345 | 22/3 | Jordan - King 345 kV & Jordan - North Belt 345 kV, North Belt - Th Wharton 345 kV | Jefferson - South Channel 138 kV | RT | Planned | [6 empty] | CTR | CBY | CBYCTR97A | SCBYCTR5
ONCOR | Cedar Crest Switch - … - Industrial Blvd | LN | 138 | 19/3, 18/5 | DCKT Westmoreland - Cedar Hill Switch 138 kV & Mountain Creek Ses - Fish Creek Switch 69 kV | Saint Augustine Tap 2 - Sargent Road 138 kV | RT | Planned | [6 empty] | CMPST | CDCSW | 3130_A | SCMPIND8
ONCOR | Cedar Elm Switch - Krum West Switch | LN | 345 | 22/4 | Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned | [6 empty] | KRWSW | CDESW | 38020 | SANAKR25
ONCOR | Cedar Hill Switch - Courtland | LN | 345 | 19/10, 18/9, 18/5 | DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV | Cedar Hill Switch - Fish Crek Switch (3180) 138 kV | RT | Planned, Forced | [6 empty] | CRTLD | CDHSW | 6020_A, 6020_D | STVWCRT5
AEP | Celanese Bay City - Wadsworth | LN | 138 | 21/1 | DCKT Jones Creek-South Texas Project & Refuge 345 kV | Blessing - Pavlov 138 kV | RT | Planned | N | [5 empty] | CELANEBC | WADSWORT | CELANE_WADSWO11 | SCELWAD8
AEP, ETT | Cenizo - … - Del Sol | LN | 345 | 19/1, 18/5 | Basecase, Lobo - San Miguel Gen 345 kV | Valley GTC, North Laredo Switch - Piloncillo 138 kV | RT | Forced | [6 empty] | CENIZO | CABEZNTP | CABEZN_CENIZO1 | SCE2DEL5
ONCOR | Centerville Road Switch - … - Judd Court & Kirkland Park | LN | 138 | 19/9, 19/3 | DCKT Centerville Road Switch to Parkdale Switch 138 kV | Prairie Creek - Scyene Road 138 kV | RT | Planned | [6 empty] | CNRSW | GRLRD | 3250_A, 3250_I | SLKHCNR8
ONCOR | Centerville Road Switch - Forney Switch | LN | 345 | 2017 | DCKT Forney Switch - Royse Switch 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [7 empty] | CNRSW | FORSW | 110 | SCNRFOR5
CNPE | Chanel - Deepwater | LN | 138 | 21/11 | Eastside - Gable Stree 138 kV | Downtown - Polk 138 kV | RT | Planned | [6 empty] | DPW | CHL | CHLDPW70A | SCHLDPW8
ONCOR | China Grove Switch - Snyder | LN | 138 | 19/5 | DCKT Dermott Switch - Bluff Creek Switch & Ennis Creek Switch 138 kV | Morgan Creek SES - Sun Switch 138 kV | RT | Planned | [6 empty] | CGRSW | SNYDR | 6235 | SSNYCGR8
AEP, ONCOR | Clear Crossing - ... - Willow Creek Switch | LN | 345 | 21/11 | DBCKT Edith Clarke - Riley 345 kV, Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Long Creek 345 kV, Abilene Mulberry Creek - Bluff Creek 345 kV | RT | Planned | [6 empty] | CLEARCRO | WCSWS | 35150_A | SCLEWC25
AEP, ONCOR | Clear Crossing - … - Dermott Switch (CLEARC_KIRCHH2) | LN | 345 | 18/5, 18/4 | DCKT Dermott Switch to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH2 | SKIRDM35
AEP, ONCOR | Clear Crossing - … - Dermott Switch CLEARC_KIRCHH1) | LN | 345 | 18/12, 18/11, 18/9, 18/8, 18/7, 18/6, 18/5, 18/4 | DCKT Dermott Sw to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH1 | SKIRDMT5
AEP, ETT | Clear Crossing - … - Edith Clarke (CLEARC_GAUSS2) | LN | 345 | 17/9, 17/8, 17/7 | Basecase | Panhandle GTC | RT | Planned | [6 empty] | CLEARCRO | GAUSS | CLEARC_GAUSS2 | SGAUED35
ETT, TETRTX | Clear Crossing - West Shackelford (CLEARC_WSHACK1) | LN | 345 | 21/9, 19/3, 19/2, 19/1 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | WSHACK | CLEARC_WSHACK1 | SCLEWS15
ETT | Clear Crossing - West Shackelford (CLEARC_WSHACK2) | LN | 345 | 19/3, 19/2, 19/1 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | WSHACK | CLEARC_WSHACK2 | SCLEWS25
AEP | Coleto - Lon Hill | LN | 345 | 20/3, 17/3, 16/12, 16/1, 15/3 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Coleto Creek to Pawnee Sw 345 kV, Pawnee Sw to Lon Hill 345 kV, Goddard to Pawnee Switching Station 345 kV | Whitepoint - Rincon 138 kV, Kenedy Sw - Coleto Creek 138 kV, Magruder - Victoria 138 kV, Kenedy Sub - Kenedy Sw 69 kV, Callicoatte - Lon Hill 138 kV | RT, ST | Planned, Forced | Y, N | [5 empty] | COLETO | LON_HILL | COLETO_LON_HI1 | SCOLLON5
AEP | Coleto Creek - Euler | LN | 138 | 19/5 | Formosa to Lolita 138 kV | Victoria - Victoria Dupont Switch (VICTOR_V_DUPS1) 138 kV | RT | Forced | [6 empty] | COLETO | EULER | COLETO_EULER1 | SCO2EUL8
AEP | Coleto Creek - Victoria (COLETO_VICTOR1) | LN | 138 | 21/11, 22/3 | Coleto Creek - Pawnee Switching Station 345 kV | Coleto Creek - Victoria 138 kV | ADD | Planned | [6 empty] | COLETO | VICTORIA | COLETO_VICTOR1 | SVICCO28
AEP | Coleto Creek - Victoria (COLETO_VICTOR2) | LN | 138 | 21/11, 22/3, 22/10 | Coleto Creek - Pawnee Switching Station 345 kV, DCKT White Point to Angstrom & Lon Hill 345KV | Coleto Creek - Victoria 138 kV | ADD | Planned | [6 empty] | COLETO | VICTORIA | COLETO_VICTOR2 | SVICCOL8
ONCOR | Comanche Peak Ses - Comanche Switch | LN | 345 | 22/4, 21/4, 18/11 | DCKT Killeen Switch - Buckhorn Switch & Russell Gap Switch 345 kV | Comanche Tap - Comanche Switch 138 kV | RT | Planned, Forced | [6 empty] | CMNSW | CPSES | 662 | SCMNCPS5
ONCOR | Comanche Peak Ses - Mitchell Bend Switch | LN | 345 | 20/3 | DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV | Comanche Peak SES - Wolf Hollow 345 Switch 345 kV, Mitchell Bend Switch - Wolf Hollow 345 Switch 345 kV | RT | Planned | [6 empty] | CPSES | MBDSW | 6033 | SDCSCPS5
STEC | Cotulla Sub - … - Freer Sub | LN | 69 | 22/1 | Fowlerton - Lobo 345 kV | Bruni Sub 138/69 kV | RT | Planned | [6 empty] | COTULAS | HOLANDS | COT_HOLA | SFREBRU9
LCRA | Crane Lcra - King Mountain West Tap | LN | 138 | 22/5 | Crane LCRA - Castillo 138 kV | Rio Pecos - LCRA Crane 138 kV | RT | Planned | [6 empty] | LCRANE | KINGMO | 664T664 | SLCRKIN8
CNPE | Crosby - Power Systems Arco Cogen | LN | 138 | 19/3 | DCKT Chambers - King & Jordan - North Belt 345 kV | Bigvue - Power Systems Arco Cogen 138 kV | RT | Planned, Forced | [6 empty] | CS | HNY | CS_HL_08 | SHLC6S8
LCRA | Crosswinds - Turnersville | LN | 138 | 22/7 | DCKT McCarty Lane - Hunter & Hilltop 138kV | Turnersville - Buda 138 kV | RT | Planned | [6 empty] | CROSSWI | TURNER | 261T272 | STURCRO8
CNPE | Crown -Jefferson | LN | 138 | 23/3 | PAIR to BOGGY 138 kV | Conial - Philip 138 kV | RT | Planned | [6 empty] | JFS | CRN | CRNJFS94 | SCRNJFS8
AEP | Del Mar - Laredo Plant | LN | 138 | 19/10 | North Edinburg - Pomelo 345 kV | Laredo VFT North - Las Cruces 138 kV | RT | Planned | [6 empty] | DEL_MAR | LAREDO | DEL_MA_LAREDO1 | SDELLAR8
AEP | Del Sol - Pomelo | LN | 345 | 17/1, 16/10 | Basecase | Valley GTC | ST | Planned | Y | [5 empty] | DELSOL | POMELO | DELSOL_POMELO1 | SPOMDEL5
TETRTX | Dermott Switch - Figaro | LN | 345 | 21/10 | DBCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | DMTSW | FIGARO | DMTSW_FIGARO1 | SFIGDMT5
ONCOR,WETR | Dermott Switch - Mhos (T-301) | LN | 345 | 22/5, 22/9, 22/10 | Double Mountain Switch - Fiddlewood Switch 345 kV, Blackwater Draw Switch - Double Mountain Switch 345 kV | Holly Substation - Dunbar Substation 115 kV, MacKenzie Substation - Northeastern Substation 115 kV | RT | Forced | [6 empty] | MHOS | DMTSW | T-301 | SDMTW_15
ONCOR,WETR | Dermott Switch - Mhos (T-302) | LN | 345 | 22/5, 22/9, 22/10 | Double Mountain Switch - Fiddlewood Switch 345 kV, Blackwater Draw Switch - Double Mountain Switch 345 kV | Holly Substation - Dunbar Substation 115 kV, MacKenzie Substation - Northeastern Substation 115 kV | RT | Forced | [6 empty] | MHOS | DMTSW | T-302 | SDMTW_25
ONCOR | Dermott Switch - Scurry County South Switch (34540) | LN | 345 | 20/11 | DCKT Clear Crossing-…-Figaro & Clear Crossing-…-Dermott Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | N | [5 empty] | DMTSW | SCOSW | 34540_A | SDMTSC15
ONCOR | Dermott Switch - Scurry County South Switch (34550) | LN | 345 | 20/11 | DCKT Clear Crossing-…-Figaro & Clear Crossing-…-Dermott Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | N | [5 empty] | DMTSW | SCOSW | 34550_A | SDMTSC25
ONCOR, WETR | Dermott Switch - Wett_Cottonwood (T-301) | LN | 345 | 22/4, 21/12 | Blackwater Draw Switch - Double Mountain Switch 345 kV | MacKenzie Substation - Northeast Substation 115 kV | RT | Planned | [6 empty] | W_CW_345 | DMTSW | T-301 | SDMTW_15
ONCOR, WETR | Dermott Switch - Wett_Cottonwood (T-302) | LN | 345 | 22/4, 21/12 | Blackwater Draw Switch - Double Mountain Switch 345 kV | MacKenzie Substation - Northeast Substation 115 kV | RT | Planned | [6 empty] | W_CW_345 | DMTSW | T-302 | SDMTW_25
BREC,ONCOR | Desoto Switch -…- Sterrett | LN | 138 | 22/12 | JOHNSON SWITCH (ONCOR) to CONCORD 345 kV, ENNIS WEST SWITCH - ENNIS TRACTEBEL 138 kV, DCKT Kemp Ranch Switch - Sardis & Soap Creek Switch -Cedar Hill Tu 138 kV | Midlothian Txi - Midlothian South 138 kV, Wilmer Auto FMR1 138/69 kV | RT | Planned | [6 empty] | DESSW | GLNHT | 945_A | SGLNDES8
TNMP | Dickinson Tnp - League City Tnp | LN | 138 | 20/10 | North Alvin TNP-Hastings Tnp 138 kV | League City Tnp - Hidden Lakes Tnp 138 kV | RT | Planned | N | [5 empty] | DICKNSON | LEAGCITY | G138_091 | SLEADIC8
GEUS, TMPA | Diesel - Greenville Steam | LN | 69 | 15/7 | Shelby Auto BT1 138/69 kV | Greenville Steam Auto XT1 138/69 kV | ST | Planned | [6 empty] | DIESEL | GN_S_I | DIE_GNS | SDIEGN_9
AEP | Dolan Tap - Whiting | LN | 138 | 21/10 | Odlaw Switch -…- Uvalde AEP 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned | [6 empty] | DOLAN | WHITING | DOLAN_WHITIN1 | SCT2CAR8
CNPE | Dow Chemical - Oasis (DOWOAS18) | LN | 345 | 22/4, 21/4, 22/9 | Cedar Creek - WA Parish 345 kV & WA Parish - Wolf 345 kV, DCKT Jones Creek-South Texas Project & Refuge 345 kV | South Texas Project - WA Parish 345 kV, Bay City Sub - Sargent Sub 69 kV, Dow Chemical (DOWOAS27) - Oasis 345 kV | RT | Planned, Forced | N | [5 empty] | OAS | DOW | DOWOAS18A | SOASDO25
CNPE | Dow Chemical (DOWOAS27) - Oasis | LN | 345 | 22/4 | Cedar Creek - WA Parish 345 kV & WA Parish - Wolf 345 kV | South Texas Project - WA Parish 345 kV | RT | Forced | [6 empty] | OAS | DOW | DOWOAS27A | SOASDOW5
AEP, STEC | Downie Switching Station - … - Uvalde AEP | LN | 138 | 19/5 | Asphalt Mines to Odlaw Switchyard 138 kV | Hamilton - Maverick 138 kV | RT | Planned | [6 empty] | UVALDE | READING | READIN_UVALDE1 | SREAUVA8
STEC | Driscoll Sub - … - Loyola Sub | LN | 69 | 20/4 | Ajo-Nelson Sharpe 138 kV | Falfurrias - Premont 69 kV | RT | Planned | N | [5 empty] | DRSCOLS | RICRDOS | DRS_RICR | SRICLOY9
AEP | Dupont Switch Ingleside - Rincon (I_DUPS_RINCON1) | LN | 138 | 21/2 | DCKT Whitepoint-Nueces Bay & Whitepoint-Portland-Gibbs 138 kV | Ingleside - Dupont Switch - Ingleside 138 kV | RT | Forced | [6 empty] | I_DUPSW | RINCON | I_DUPS_RINCON11 | SRINI_D8
AEP | Dupont Switch Ingleside - Rincon (I_DUPS_RINCON2) | LN | 138 | 21/2 | DCKT Whitepoint-Nueces Bay & Whitepoint-Portland-Gibbs 138 kV | Ingleside - Dupont Switch - Ingleside 138 kV | RT | Forced | [6 empty] | I_DUPSW | RINCON | I_DUPS_RINCON21 | SRINI_28
AEP, ETT | Edith Clarke - Riley (Edithc_Riley1) | LN | 345 | 18/3, 18/2, 18/1, 17/12, 17/11, 17/10 | Basecase | Panhandle GTC | RT | Planned | [6 empty] | EDITHCLA | RILEY | EDITHC_RILEY1 | SRILED15
AEP, ETT | Edith Clarke - Riley (Edithc_Riley2) | LN | 345 | 18/3, 18/2, 18/1, 17/12, 17/11, 17/10 | Basecase | Panhandle GTC | RT | Planned | [6 empty] | EDITHCLA | RILEY | EDITHC_RILEY2 | SRILED25
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC3) | LN | 345 | 17/6, 17/5, 17/4, 17/3, 17/2, 17/1, 16/12, 16/11 | Basecase | Panhandle GTC | RT, ST | Planned, Forced | [6 empty] | EDITHCLA | W_CW_345 | COTTON_EDITHC3 | SW_CED55
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC4) | LN | 345 | 17/6, 17/5, 17/4, 17/3, 17/2, 17/1, 16/12, 16/11 | Basecase | Panhandle GTC | RT, ST | Planned, Forced | [6 empty] | EDITHCLA | W_CW_345 | COTTON_EDITHC4 | SW_CED45
AEP | El Campo - Corichi Tap - … - Victoria | LN | 138 | 19/10 | Victoria Auto 69A1 138/69 kV | Victoria Auto 69A2 138/69 kV | RT | Planned | [6 empty] | EL_CAMPO | CORICHI | CORICH_EL_CAM1 | SGANVIC8
AEP,LCRA | El Campo - Ricebird | LN | 138 | 23/3 | DCKT Vanderbilt Switching Station - Energy Transfer Partners 138kV & EL Toro Switching Station - Edna Substation 69kV | Danevang Switching Station Auto 138_69 138/69 kV | RT | Planned | [6 empty] | RICEBI | EL_CAMPO | 589T589 | SRICEL_8
ONCOR | Elkins Road Pod - Midland East | LN | 138 | 21/11 | Grady -…- Brown 138 kV | Big Spring West - Stanton East 138 kV | RT | Planned | [6 empty] | ERPOD | MDLNE | 6146_A | SSTAMDL8
ONCOR | Elkton - Martin Lake Ses | LN | 345 | 2017 | Martin Lake - Styker and - Enterprise DCKT | Martin Lake - Shamburger | ADD | [7 empty] | ELKTN | MLSES | 180 | SELKMLS5
ONCOR | Elkton - Tri Corner | LN | 345 | 18/12, 18/11, 2017, 17/11 | DCKT Trinidad Ses- Mt Enterprise & Stryker Creek Ses, DCKT Martin Lake Ses - Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3, Lufkin Switch - Nacogdoches South Tap 138 kV | ADD, RT | Planned | [6 empty] | ELKTN | TRCNR | 170 | SELKFOR5
CNPE, CPS | Elmcreek - South Texas Project | LN | 345 | 22/4 | Elmcreek - South Texas Project 345 kV & South Texas Project - WA Parish 345 kV | Hillje - South Texas Project 345 kV | RT | Planned | [6 empty] | STP | ELMCREEK | STPELM271 | SELMSTP5
GAR | Elmgrove - Wylie Switch | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | ELMGROVE | WYLIESW | WYL_ELMG | SWYLELM8
LCRA | Engle -…- Schulenburg | LN | 138 | 22/05 | Joslin - Formasa 138 kV | Lolita - Victoria 138 kV | RT | Planned | [6 empty] | ENGLE | FLATON | 145T112 | SENGFLA8
ONCOR | ENNIS WEST SWITCH -...- SHANKLE SWITCH (941) | LN | 138 | 19/6 | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | Ennis West Switch- Wahaxhachie - Sterrett | ADD | Planned | [6 empty] | ENSSW | ENWSW | 943_A | SENSEN28
ONCOR | Ennis West Switch -…- Sterrett (940) | LN | 138 | 18/11 | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (941) | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | ADD | Planned | [6 empty] | ENWSW | WXHCH | 940_C | SMGIENW8
ONCOR | Ennis West Switch -Ennis South (941_C) | LN | 138 | 19/4 | WXHCH-WXOCF_69kV & ENWSW-STERT_138kV | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | ADD | Planned | [6 empty] | ENWSW | ENSSO | 941_C | SENSENW8
AEP | Euler - Tuleta | LN | 138 | 19/8, 19/5 | DCKT Lon Hill to Coleto Creek 345 kV & Warburton Road Switching Station 138 kV, Coleto Creek to Pawnee Switching Station 345 kV | Normanna - Pettus 69 kV, Coleto Creek - Rosata Tap 138 kV | RT | Forced | [6 empty] | TULETA | EULER | EULER_TULETA1 | SEULTUL8
ONCOR | Everman Switch - Oakhill Tap 1 | LN | 138 | 22/2, 21/12 | Davis -…-Everman Switch 138 kV, DBCKT Deen Switch -…- Hicks Switch 138 kV | Hemphill - Mistletoe Heights 138 kV | RT | Planned, Forced | [6 empty] | EVRSW | OAKT1 | 6310_A | SOAKEVR8
ONCOR | Falcon Seaboard - Midland East | LN | 345 | 20/10 | DCKT Odessa EHV Sw-Moss Sw & Wolf Switching Station 345 kV | Odessa North - Odessa 138 kV | RT | Planned | N | [5 empty] | FLCNS | MDLNE | 6045_A | SFLCMDL5
d | Fayette Plant 3 - Lytton Springs | LN | 345 | 23/2 | DCKT Fayette Plant 1 and 2 - Lostpine & Winches 345kV | Fayetteville Auto AT2H 345/138 kV | RT | Planned | [6 empty] | FPPYD2 | LYTTON_S | 355T255 | SFPPLYT5
ONCOR | Forney Switch - Royse Switch (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [7 empty] | FORSW | RYSSW | 200 | SFORRYS5
ONCOR | Forney Switch - Royse Switch (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [7 empty] | FORSW | RYSSW | 210 | SFORRY25
AEP | Fort Mason - Mason AEP | LN | 138 | 19/5 | DCKT Ferguson to Granite Mountain 138 kV and Starcke to Wirtz 138 kV | Flat Rock LCRA - Wirtz 138 kV | RT | Planned | [6 empty] | MASN | FORTMA | FORTMA_MASN1 | SMA2FOR8
AEP,TAEP | Fort Mason - Yellow Jacket | LN | 138 | 22/11 | DCKT Bighill -Kendall 345kV | Yello Jacket - Hext LCRA 138 kV | RT | Forced | [6 empty] | YELWJCKT | FORTMA | FORTMA_YELWJC1 | SFORYEL8
STEC | Fowlerton - San Miguel Gen | LN | 345 | 21/2 | DCKT Dilley Sw (AEP)-San Miguel Sw & Dilley Sw (AEP)-Cotulla Sub 138 kV | Dilley Switch Aep - Cotulla Sub 69 kV | RT | Forced | [6 empty] | FOWLRTON | SANMIGL | FOWRTN_SMIGL | SSANFOW5
TNMP | Freeway Park Tnp - Mainland Tnp | LN | 138 | 22/4, 22/3, 21/2 | Meadow - Ph Robinson 345 kV, PH Robinson-Gaf Tnp 138 kV | Magnolia Tnp - Seminole Tnp 138 kV, Freeway Park Tnp - Dickinson Tnp 138 kV | RT | Planned | N | [5 empty] | MAINLAND | FRWYPARK | 138_FWP_MNL1 | SFRWMAI8
CNPE | Garrott - Kirby | LN | 138 | 21/11 | Eastside - Gable Stree 138 kV | Downtown - Polk 138 kV | RT | Planned | [6 empty] | GT | KB | GT_KB_37A | SGTKB8
AEP | Gateway and Wormser Road to North Laredo Switch | LN | 138 | 22/4 | Fowlerton - Lobo 345 kV | Gateway West Tnp - Wormser Road 138 kV | RT | Forced | [6 empty] | GATE_WAY | GATEWTP | GATEWT_GATE_W1 | SNLAGAT8
CNPE, CROSS, GAR, TMPA | Gibbons Creek - Limestone Plant (GIB_LIME181) | LN | 345 | 21/3 | DCKT Jewett-Singleton 345 kV | Gibbons Creek - Twin Oak Switch 345 kV | RT | Planned | N | [5 empty] | GIBCRK | LEG | GIB_LIME181 | SLE2GIB5
CNPE, CROSS, GAR, TMPA | Gibbons Creek - Limestone Plant (GIB_LIME501) | LN | 345 | 21/3 | DCKT Jewett-Singleton 345 kV | Gibbons Creek - Twin Oak Switch 345 kV | RT | Planned | N | [5 empty] | GIBCRK | LEG | GIB_LIME501 | SLEGGIB5
TMPA | Gibbons Creek - Twin Oak Switch | LN | 345 | 20/11, 20/5 | DCKT GibbonsCreek-Limestone 345 kV, DCKT Jewett-Singleton 345 kV | Jewett - Singleton 345 kV | RT | Planned | N | [5 empty] | GIBCRK | TOKSW | 256_A1 | SGIBTOK5
AEP | Gila -…- Whitepoint | LN | 138 | 23/2 | Whitepoint Auto 345_1 345/138 | Nueces_Bay - White Pt 138 kV | RT | Forced | [6 empty] | MAYO | GILA | GILA_MAYO1 | SMAYWHI8
AEP | Goddard - Pawnee Switching Station | LN | 345 | 21/12, 21/11 | Fowlerton - Lobo 345 kV | North Laredo Switch - Piloncillo Ranch 138 kV | RT | Forced, Planned | [6 empty] | PAWNEE | GODDARD | GODDAR_PAWNEE1 | SGODPAW5
AEP, STEC | Goddard - Tango | LN | 345 | 22/2, 22/1, 21/11 | Fowlerton - San Miguel Gen 345 kV, Grissom - Lon Hill 345 kV, Coleto Creek - Grissom 345 kV & Fannin Sub - Goliad 69 kV | George West Switch Station - Sigmor 138 kV, Choke Canyon Aep - San Miguel Gen 138 kV, North Carbide - Sea Drift Coke 138 kV | RT | Forced, Planned | [6 empty] | GODDARD | PAWNEE | GODDAR_TANGO1 | SGODTAN5
ONCOR | Golden Switch - Sun Switch | LN | 138 | 20/3 | DCKT Dermott Switch to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Forced | [6 empty] | GLDSW | SUNSW | 6438 | SGLDSUN8
ONCOR | Grady -...- Brown-Buzzard Draw Switch-...-Vealmoor | LN | 138 | 22/4, 22/3, 21/6, 21/5 | Big Spring Switch -…- Natural Dam 138 kV, Scurry County South Switch - Wett_Long_draw 345 kV & Wett_Faraday - Wett_Long_Draw 345 kV, DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Wett_Grelton - Wett_Long_Draw 345 kV, Odessa EHV Switch - Wett_Grelton 345 kV | Big Spring West - Stanton East 138 kV, Luther - Vealmoor 138 kV, Falcon Seaboard - Morgan Creek Ses 345 kV | RT | Planned | [6 empty] | GRADY | LNPOD | 15050_A | SLUTVEA8
ONCOR | Graham SES - Rice Switch | LN | 138 | 22/4 | Windthorst Switch -…- Wichita Falls South Switch 138 kV | Cottonwood Road Switch - Olney Pod 69 kV | RT | Planned | [6 empty] | GRSES | RICSW | 6560_A | SRICGRS8
ONCOR | Graham SES - Tonkawa Switch | LN | 345 | 21/11 | Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Bluff Creek 345 kV | RT | Planned | [6 empty] | GRSES | TKWSW | 6035_A | STKWGRS5
CROSS | Gray - Railhead | LN | 345 | 16/5, 16/3 | Basecase, DCKT Alibates to Tule Canyon 345 kV | Panhandle GTC, Low Voltage in Panhandle area | RT, ST | Planned | Y | [5 empty] | RAILHEAD | CTT_GRAY | RAILHD_GRAY | SRAICTT5
AEP, CROSS | Gray - Tesla (GRAY_TESLA_1) | LN | 345 | 17/1 | Basecase | Panhandle GTC | RT | Forced | [6 empty] | CTT_GRAY | TESLA | GRAY_TESLA_1 | SCTTTES5
CROSS | Gray South Bus (CB GY_BKR_G130, etc.) | BUS | 345 | 16/5 | DCKT Alibates to Tule Canyon 345 kV | Low Voltage in Panhandle area | ST | Planned | Y | [5 empty] | GTT_GRAY |  | 1002 | N/A
ONCOR | Gresham Road Switch - … - Nacogdoches Se | LN | 138 | 19/1, 18/12, 18/10, 18/8, 18/7, 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Nacogdoches Se - Redland Switch 138 kV, Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned | [6 empty] | CSHNG | GRDSW | 1450_F | SNCDCMI8
ONCOR | Gresham Road Switch - Stryker Creek Ses | LN | 138 | 18/6 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Nacogdoches Se - Redland Switch 138 kV | RT | Planned | [6 empty] | SCSES | GRDSW | 11010 | SGRDSCS8
AEP | Haine Drive - La Palma | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | HAINE_DR | LA_PALMA | HAINE__LA_PAL1 | SHAILA_8
LCRA | Hamilton Road - Pinto Creek | LN | 138 | 23/3, 23/4 | DCKT Bighill-Kendall 345kV | Hamilton Road - Maverick 138 kV, Escondido - Ganso 138 kV | RT | Planned | [6 empty] | PINTCR | HAMILTON | 464T464 | SBRAHAM8
AEP | Harlingen Switch - Raymondville 2 | LN | 138 | 21/2 | DCKT North Edinburg-Lon Hill & North Edinburg -…-El Trueno WInd 345 kV, DCKT South Santa Rosa-Rio Hondo 138 kV | Haine Drive - La Palma 138 kV | RT | Planned | N | [5 empty] | HARLNSW | RAYMOND1 | HARLNS_RAYMON11 | SRAYHAR8
LCRA | Harlingen Switch - Weslaco Switch | LN | 138 | 21/1, 20/11 | North Eninburg TRX 1382345/138 kV, DCKT North Edinburg-Lon Hill & North Edinburg -…-El Trueno WInd 345 kV, DCKT South Santa Rosa-Rio Hondo 138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | N | [5 empty] | WESLACO | NWESLACO | 207T4801 | SNWEWES8
LCRA | Hays Energy Center - Zorn (388T3881) | LN | 345 | 2021 | DCKT Cagnon - Kendal 345kV & Cico - Comfor 138kV | Hays Energy Center - Zorn 345 kV (6T227) | ADD | [7 empty] | HAYSEN | ZORN | 388T3881 | SHAYZO25
LCRA | Hays Energy Center - Zorn (6T227) | LN | 345 | 2021 | DCKT Cagnon - Kendal 345kV & Cico - Comfor 138kV | Hays Energy Center - Zorn 345 kV (388T3881) | ADD | [7 empty] | HAYSEN | ZORN | 6T227 | SHAYZOR5
AEP | Hecker - Whitepoint (HECKER_WHITE_1) | LN | 138 | 21/4, 21/2, 20/10, 20/9, 19/3, 19/2, 18/1, 17/3 | Whitepoint-…-Gibbs 138 kV, DCKT Whitepoint-Nueces Bay & Whitepoint-Portland-Gibbs 138 kV, Whitepoint-…-Gibbs 138 kV, Whitepoint-…-Gibbs 138 kV, DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Lon Hill to Coleto Creek 345 kV, McCampbell - … - Whitepoint 138 kV | Heckter - Whitepoint, Ingleside - Dupont Switch - Ingleside, Whitepoint- Rosenburg, Whitepoint- Rosenburg, Whitepoint - Rincon 138 kV, Warburton Road Switching Station - Victoria 138 kV, Whitepoint TRX 138_69A1 138/69 kV | RT | Planned, Forced | [6 empty] | HECKER | WHITE_PT | HECKER_WHITE_1 | SHECWH28
AEP | Hecker - Whitepoint (HECKER_WHITE_2) | LN | 138 | 21/5, 21/2, 20/10, 20/09, 19/3, 19/2, 18/1 | Gibbs -…-Whitepoint 138 kV & Neuces Bay - Whitepoint 138 kV, DCKT Whitepoint-Nueces Bay & Whitepoint-Portland-Gibbs 138 kV, Whitepoint-…-Gibbs 138 kV, Whitepoint-…-Gibbs 138 kV, Lon Hill to Coleto Creek 345 kV, McCampbell - … - Whitepoint 138 kV | Hecker - Whitepoint 138 kV, Ingleside - Dupont Switch - Ingleside, Whitepoint- Rosenburg, Whitepoint- Rosenburg, Warburton Road Switching Station - Victoria 138 kV, Whitepoint TRX 138_69A1 138/69 kV, Rincon - Whitepoint 138 kV | RT | Forced, Planned | [6 empty] | HECKER | WHITE_PT | HECKER_WHITE_2 | SHECWHI8
LCRA | Heines - Naval Base | LN | 69 | 19/4 | DCKT Whitepoint - Lon Hill & South Texas Project 345 kV | Lon Hill 345/138 kV Auto 382H | RT | Planned | [6 empty] | NVLBASE | HEINES | 685T685 | SNVLHEI9
TNMP, ONCOR | Highlands Tnp - Lewisville Switch | LN | 138 | 21/12, 20/12, 20/1, 20/3, 20/2 | Carrollton Northwest-Lakepoint Tnp 138 kV, DCKT Carrollton Northwest to Lewisville Switch 345 kV | South Tnp - Carrollton Northwest, Argyle - Highlands Tap 138 kV, TI Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | LWSSW | LWSVH | 593 | SLWSLWS8
LCRA | Hill Country - Marion | LN | 345 | 19/2, 23/2 | DCKT Elmcreek - Skyline 345 kV | Hill Country - Marion 345 kV | RT | Planned | [6 empty] | MARION | HILLCTRY | HILL_MAR_1 | SMARHI25
AEP | Holly - Westside Aep | LN | 138 | 18/11, 22/05 | Airline Aep - … - Westside Aep 138 kV | Arcadia - Southside 138 kV | RT | Planned, Forced | [6 empty] | HOLLY4 | WESTSIDE | HOLLY4_WESTSI1 | SHOLWES8
CNPE | Holmes - Plaza | LN | 138 | 21/10 | Eastside - Polk 138 kV | Downtown - Polk 138 kV | RT | Planned | [6 empty] | PZ | HM | HM_PZ_06A | SHMG1V8
CPS | Howard - Somerset | LN | 138 | 18/1, 17/12 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 kV | RT | Planned | [6 empty] | S1 | E3 | E3_S1 | SE3S18
ONCOR, TMPA | Jack_Creek - Twin Oak Switch | LN | 345 | 20/11 | DCKT GibbonsCreek-Limestone 345 kV | Jewett - Singleton 345 kV (260_A) | RT | Planned | N | [5 empty] | JK_CK | TOKSW | JK_TOKSW1 | SJK_TOK5
BRAZOS | Jaybird - Rw Miller | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | MIL | JAYBIRD | JYBRD_MIL | SSTVMIL8
BRAZOS | Jaybird - Stephenville Bepc | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | JAYBIRD | STV | JYBRD_STV | SJAYSTV8
CNPE | Jeanetta - WA Parish | LN | 345 | 21/12 | Meadow - Ph Robinson 345 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned | [6 empty] | WAP | JN | JN_WAP72A | SJNWA1P5
CNPE | Jeanetta - Westchase | LN | 138 | 23/2 | DCKT Bellaire -H O Clarke 138 kV | Jeanetta - Westwood 138 kV | RT | Planned | [6 empty] | JN | WZ | JN_WZ_05 | SWZJN8
ONCOR | Jewett - Singleton (260_A) | LN | 345 | 2018 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | ADD | [7 empty] | JEWET | SNG | 260_A | SSNGJE25
AEP | Jim Treece - Riley | LN | 345 | 16/11 | Basecase | Panhandle GTC | ST | Planned | [6 empty] | JIMTREEC | RILEY | JIMTRE_RILEY2 | SJIMRI25
AEP | Jim Treece - Tesla | LN | 345 | 17/2, 16/11 | Basecase | Panhandle GTC | ST | Planned | Y, N | [5 empty] | JIMTREEC | TESLA | JIMTRE_TESLA2 | SJIMTE25
ONCOR | Johnson Switch - Venus Switch | LN | 345 | 19/11, 19/10 | DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV, Concord Auto CRD1 345/138 kV | Cedar Hill Switch - Fish Creek Switch 138 kV (3180), Concord Auto CRD2 345/138 kV | RT | Planned | [6 empty] | JONSW | VENSW | 141 | SJONVEN5
CNPE | Jones Creek - South Texas Project | LN | 345 | 22/4. 22/6 | Elmcreek - South Texas Project 345 kV & South Texas Project - WA Parish 345 kV, DCKT BLUE-Bailey & Hillje - Wolf 345 kV | Hillje - South Texas Project 345 kV, Jones Creek - Refuge 345 kV | RT | Planned, Forced | [6 empty] | JCK | STP | JCKSTP18A | SJCKSTP5
TNMP | Jones Street Tnp - Lakepointe Tnp | LN | 138 | 20/3, 20/2, 20/1,19/3, 17/12, 17/11 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | Ti Tnp - West Tnp 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV, Argyle - Hihglands Tnp 138 kV | RT | Planned | [6 empty] | LWVJS | LKPNT | 590_B | SLWVLKP8
BRAZOS, TNMP | Jones Street Tnp - Lewisville Switch | LN | 138 | 20/3 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | TI Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | LWSSW | LWVJS | 590_A | SLWVLWS8
CNPE | Jordan - King | LN | 345 | 21/11, 22/11 | Jordan - King 345 kV & Jordan - North Belt 345 kV, DCKT Crown - Tanker 138 kV & Davson - ... - Greens Bayou 138 kV, DCKT Power System Arco Cogen - ... - Crosby & Riverside 138 kV | Lychem - Power Systems Arco Cogen 138 kV | RT | Planned | [6 empty] | KG | JOR | JORKG_97 | SKGJOR5
AEP | Joslin - Sand Crab | LN | 138 | 21/11 | Formosa G3 | Formosa - Lolita 138 kV | RT | Planned | [6 empty] | JOSLIN | SANDCRAB | JOSLIN_SANDCR1 | SJOSSAN8
LCRA | Kendall CTEC - Maenius Road | LN | 138 | 22/4 | Comfort - Kendall 138 kV | Hollmig - Kendall 138 kV | RT | Planned | [6 empty] | KENDCT | MAENRO | 22T342 | SMAEKEN8
ONCOR | Killeen Switch - Salado Switch (271) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | KLNSW | SALSW | 271 | SKLNSA25
ONCOR | Killeen Switch - Salado Switch (272) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | KLNSW | SALSW | 272 | SKLNSAL5
ONCOR | Killeen Switch Auto AXFMR1 345/138 kV | XF | 345 | 22/5, 22/4, 22/3, 22/2, 22/1 | DBCKT Salado Switch - Killeen Switch 345 kV | Killeen Switch Auto AXFMR2 345/138 kV | ADD | Planned | [6 empty] | KLNSW |  | AXFMR1 | XKLN58
ONCOR | Killeen Switch Auto AXFMR2 345/138 kV | XF | 345 | 2022 | DBCKT Salado Switch - Killeen Switch 345 kV | Killeen Switch Auto AXFMR1 345/138 kV | ADD | Planned | [6 empty] | KLNSW |  | AXFMR2 | XKLN358
ONCOR | Knob Creek Switch - Salado Switch | LN | 345 | 19/9 | DCKT Temple Elm Creek to Belton 138 kV | Temple Southeast - Temple Switch 138 kV | RT | Planned | [6 empty] | SALSW | KNBSW | 36040 | SKNBSAL5
AEP | La Palma - Military Highway Aep | LN | 138 | 22/6, 23/3 | STILLMAN - LOMA ALTA SUBSTATION 138 kV, WATERPORT SUBSTATION - LOMA ALTA SUBSTATION 138 kV | Titan_ Substation - Scarbi Carbide 138 kV, Paloa Alto Substation - Titan_ Substation 138 kV | RT | Forced | [6 empty] | LA_PALMA | VCAVAZOS | LA_PAL_VCAVAZ1 | SVCAMIL8
AEP | La Palma 138 kV bus #1 (CB 55, etc.) | BUS | 138 | 18/5 | DCKT Rio Hondo - North Edinburg 345 kV & Harlingen Switch 138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | LA_PALMA |  | 0BB1 | N/A
AEP | La Palma 138 kV bus #2 (CB 2015, etc.) | BUS | 138 | 18/5, 17/2 | DCKT Rio Hondo - North Edinburg 345 kV & Harlingen Switch 138 kV, North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | LA_PALMA |  | 8BB2 | N/A
AEP | Laquinta - Lobo | LN | 138 | 15/5 | Crestonio to Falfurrias 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y | [5 empty] | LOBO | LAQUINTA | LAQUIN_LOBO1 | SLAQLOB8
AEP | Laredo Vft North - … - Mines Road | LN | 138 | 18/4 | Molina to Wormser Road 138 kV, Lobo to Molina 138 kV | Del_Mar - Laredo Plant 138 kV | RT | Planned | [6 empty] | LARDVNTH | LASCRUCE | LARDVN_LASCRU1 | MNLALAR8
AEP | Laredo Vft North - Lobo (LARDVN_LOBO1) | LN | 138 | 21/4 | Fowlerton-Lobo 345 kV | North Laredo Switch - Piloncillo 138 kV | RT | Planned | N | [5 empty] | LOBO | LARDVNTH | LARDVN_LOBO11 | SLARLO28
AEP | Laredo VFT North - Lobo (LARDVN_LOBO2) | LN | 138 | 21/5 | Laredo Vft North - Lobo 138 kV | Molina - Sierra Vista 138 kV | RT | Planned | [6 empty] | LOBO | LARDVNTH | LARDVN_LOBO2 | SLARLOB8
AEP | Laredo VFT North ... North Laredo Switch | LN | 138 | 22/4, 22/5, 23/4 | Molina -…- Wormser Road 138 kV, Fowlerton - Lobo 345 kV | Del Mar - Laredo Plant 138 kV, Bruni Sub 138/69 kV, Wormser Road - Gateway West Tap 138 kV, Lardvnt Vft North - Las Cruces 138 kV | RT | Planned, Forced | [6 empty] | LARDVNTH | LASCRUCE | LARDVN_LASCRU1 | SMINNLA8
AEP | Las Pulgas - Raymondville 2 | LN | 138 | 21/12, 21/11, 21/10, 21/9, 17/4, 16/12 | Lon Hill - North Edinburg - Bonilla - El Trueno Wind Farm 345 kV & Primera-…- Rio Hondo 138 kV, Loyola Sub to Kleberg Aep 138 kV, DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Haine Drive - La Palma 138 kV, Loyola Sub Auto 69_1 138/69 kV, Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | RAYMND2 | LASPULGA | LASPUL_RAYMND1 | SRAYRI38
AEP | Las Pulgas - Rio Hondo | LN | 138 | 17/4, 16/12 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned | [6 empty] | LASPULGA | RIOHONDO | LASPUL_RIOHON1 | SRAYRI28
ONCOR | Lewisville Switch - Roanoke Switch | LN | 345 | 19/4, 19/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, Argyle - … - Lewisville Switch 138 kV | Argyle - Highlands Tap 138 kV | RT | Planned, Forced | [6 empty] | LWSSW | RNKSW | 105_B | SLWSRNK5
BRAZOS | Lewisville Switch Auto FMR2 345/138 kV | XF | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | LWSSW |  | FMR2 | XLWS158
BPUB,ONCOR | Loma Alta Substation - Stillman | LN | 138 | 23/3 | Millitary Highway Aep - Villa Cavazos 138 kV, DCKT La Palma - Villa Cavazos 138 kV & Rangerville 69 kV | Titan_ Substation - Scarbi Carbide 138 kV | RT | Forced | [6 empty] | LOMA_ALT | STILLMAN | STLLMN_LOMA | SSTILOM8
BPUB | Loma Alta Substation - Waterport Substation | LN | 138 | 18/1, 16/5 | Loma Alta Sub T1 138/69 kV, La Palma to East Harrison 69 kV | La Palma - Villa Cavazos 138 kV, Haine Drive - La Palma 138 kV | RT | Planned, Forced | [6 empty] | WATERPRT | LOMA_ALT | WP_LA | SWATLO28
AEP | Lon Hill - Nelson Sharpe | LN | 345 | 16/4, 16/3, 15/10, 15/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Ajo to Rio Hondo 345 kV | Bunsen - Lon Hill 138 kV, Celanese Bishop - Kleberg 138 kV | ST | Planned | Y | [5 empty] | LON_HILL | N_SHARPE | LON_HI_N_SHAR1 | SN_SLON5
AEP | Lon Hill - Whitepoint | LN | 345 | 18/2, 17/8 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Marion Auto AT2H 345/138 kV | RT | Forced | [6 empty] | LON_HILL | WHITE_PT | LON_HI_WHITE_1 | SWHILON5
AEP | Lon Hill Auto 69A2 138/69 kV | XF | 138 | 17/4 | Hecker to WhitePoint 138 kV, Lon Hill Auto 69A1 138/69 kV | Whitepoint - Rincon 138 kV, Koch Up River Auto 69A1 138/69 kV | RT | Planned | [6 empty] | LON_HILL |  | 69A2 | XLON489
AEP | Lon Hill-…- Weil Tract | LN | 138 | 22/12 | WEIL TRACT to LON HILL 138 kV | Lon_ Hill - Koch_ Hearns Ferry 138 kV | RT | Planned | [6 empty] | CLARK_WD | CHAMPLIN | CHAMPL_CLARK_1 | SCITWEI8
STEC | Loop 463 Sub - Victoria | LN | 138 | 22/4 | Coleto Creek - Victoria 138 kV (COLETO_VICTOR1) | Coleto Creek - Victoria 138 kV (COLETO_VICTOR2) | RT | Planned | [6 empty] | L_463S | VICTORIA | LOOP_VICTORIA | SL_4VIC8
ONCOR | Lufkin Switch - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Nacogdoches Se - Redland Switch 138 kV | RT | Planned | [6 empty] | LFKSW | NCSTP | 1350_E | SNCDNCD8
AEP | Magruder - Victoria | LN | 138 | 22/4, 19/10, 19/9 | Coleto Creek - Victoria 138 kV, Victoria Auto 69A1 138/69 kV | Coleto Creek - Victoria 138 kV, Victoria Auto 69A2 138/69 kV | RT | Planned, Forced | [6 empty] | MAGRUDER | VICTORIA | MAGRUD_VICTOR2 | SMAGVIC8
ONCOR | Martin Lake Ses - Mt Enterprise | LN | 345 | 2017 | Martin Lake - Elktion and Tyler Grande DCKT | Martin Lake - Shamburger | ADD | [7 empty] | MLSES | ENTPR | 360 | SENTMLS5
ONCOR | Martin Lake Ses - Styker Creek Ses | LN | 345 | 2017 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [7 empty] | MLSES | SCSES | 370 | SMLSSCS5
ONCOR | Martin Lake Ses - Tyler Grande | LN | 345 | 2017 | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [7 empty] | MLSES | TYGND | 340 | STYGMLS5
AEP | McCampbell - … - Whitepoint | LN | 138 | 18/10 | DCKT Hecker - Whitepoint 138 kV | Dupont Switch Ingleside - Rincon 138 kV | RT | Planned, Forced | [6 empty] | MCCAMPBE | PORTLAND | MCCAMP_PORTLA1 | SPORWH28
CLUBB | Mcdonald Substation - Northwest Substation | LN | 115 | 23/2, 23/4 | Blackwater Draw Switch - Double Mountain Switch 345 kV | MacKenzie Substation - Northeastern Substation 115 kV | RT | Planned | [6 empty] | LPLNW | LPLMD | LPLNW_LPLMD | SL18LPL0
LCRA | Mcneil - Wells Branch | LN | 138 | 22/6 | DCKT Hutto - RoundRock & Georgetown South 138 kV | Wells Branch - Howard Lane 138 kV | RT | Planned | [6 empty] | WELLBR | MCNEIL_ | 96T136 | SWELMCN8
CNPE | Meadow - Ph Robinson | LN | 345 | 22/11 | DCKT Gable Street -…- Greens Bayou 138 kV, NORTH ALVIN TNP - ALVIN TNP 138 kV , DCKT Davidson - ..-Greens Bayou BY21 & Crown - Tanker 138 kV, DCKT Power Syastems Arco Gen -..- Crosby & Riverside 138 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned | [6 empty] | MDO | PHR | MDOPHR99 | SMDOPHR5
AEP | Melon Creek - Rincon | LN | 138 | 18/11, 18/10 | DCKT Hecker - Whitepoint 138 kV, Airline Aep - … - Westside Aep 138 kV | Dupont Switch Ingleside - Rincon 138 kV, Arcadia - Southside 138 kV | RT | Planned, Forced | [6 empty] | RINCON | MELONCRE | MELONC_RINCON1 | SMELRIN8
STEC | Merett Sub - Palmhurst Sub | LN | 138 | 22/10 | DCKT North Edinburg -..- North Pharr & North McAllen 138 kV | Hec Energy Center - Azteca Sub 138 kV | RT | Planned | [6 empty] | MV_PALM4 | MERETT | MERETT_PLMHRST | SMERMV_8
CNPE | Miller -…- Rohmas | LN | 138 | 23/1 | Jefferson - College 138 kV | Conial - Philip 138 kV | RT | Forced | [6 empty] | BNS | MLR | BNSMLR88 | SRHMLR8
ONCOR | Mitchell Bend Switch - Rocky Creek | LN | 345 | 19/11, 19/10, 22/12 | DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV, DCKT Timberview Switch - Comanche Peak SES & Carmichael Bend Switch 345 kV | Carmichael Bend Switch - Mitchell Bend Switch 345 kV, Benbrook SW - Sycamore Creek 345 kV | RT | Planned, Forced | [6 empty] | RKCRK | MBDSW | 152_A | SRKCMB35
ONCOR | Mitchell Bend Switch - Wolf Hollow 345 Switch | LN | 345 | 22/3, 23/3 | Comanche Peak Ses - Johnson Switch (Oncor) 345 kV & Comanche Peak Ses - Timberview Switch 345 kV | Comanche Peak Ses - Mitchell Bend Switch 345 kV | RT | Forced | [6 empty] | WOFHO | MBDSW | 6034_A | SRKCMB25
ONCOR | Monticello Ses - … -Paris Switch | LN | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD | [7 empty] | PRSSW | MNSES | 390 | SMNSPRS5
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Tri Corner - Elkton & Tyler Grande 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | ENTPR | TRSES | 361 | SENTTR25
ONCOR | Nacogdoches Se - Redland Switch | LN | 138 | 18/12 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned | [6 empty] | HNRSW | NCDSE | 1170 | SHNRNCD8
AEP, LCRA | Naval Base - … - Port Aransas | LN | 69 | 18/11, 18/10, 17/4 | Hecker to WhitePoint 138 kV, Airline Aep - … - Westside Aep 138 kV, DCKT Citgo N Oak Park 0 Hiway 9 138 kV & Hiway 9 - Industrial Aep 69 kV, DCKT Hecker - Whitepoint 138 kV | Whitepoint - Rincon 138 kV, Arcadia - Southside 138 kV, Morris Street - Nueces Bay 138 kV, Dupont Switch Ingleside - Rincon 138 kV | RT | Planned | [6 empty] | NVLBASE | N_PADRE | NVLBAS_N_PADR1 | SSEAPO19
AEP | Nelson Sharpe Auto 345_138_AUTO 345/138 kV | XF | 345 | 23/3 | Barney Davis - Alazan 138 kV | Celanebi Bishop - Kleberg Aep 138 kV | RT | Forced | [6 empty] | N_SHARPE | N_SHARPE | 345_138_AUTO | XN_S58
CNPE | New Gulf - South Lane City | LN | 138 | 22/5 | STP SWITCH -…- STP Facilites HLP & Esperanza & Blessing 138 kV | Blessing - Pavlov 138 kV | RT | Forced | [6 empty] | LC | NEW | LC_NEW60 | SNEWGLF8
AEP | North Edinburg - Lon Hill | LN | 345 | 17/3, 16/3, 15/3 | Nelson Sharpe to Ajo 345 kV, Nelso Sharpe to Ajo 345 kV, DCKT Rio Hondo to North Edinburg 345 kV & Harlingen Sw 138 kV, Basecase | Raymondville 2 - Yturria Sub 138 kV, Celanese Bishop - Nelson Sharpe 138 kV, Burns Sub - Rio Hondo 138 kV, Valley GTC | RT, ST | Planned, Forced | [6 empty] | NEDIN | LON_HILL | LON_HI_NEDIN1 | SNEDLON5
AEP | North Edinburg - Pomelo | LN | 345 | 17/1, 16/10 | Basecase | Valley GTC | ST | Planned | Y | [5 empty] | NEDIN | POMELO | NEDIN_POMELO1 | SPOMNED5
AEP | North Edinburg - Rio Hondo | LN | 345 | 16/3 | North Edinburg to Lon Hill 345 kV | Burns Sub - Rio Hondo 138 kV | ST | Planned | [6 empty] | NEDIN | RIOHONDO | NEDIN_RIOHON1 | SNEDRIO5
AEP | North Edinburg Auto 138 345/138 kV | XF | 345 | 19/4, 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV, Haine Drive - La Palma 138 kV | RT | Planned, Forced | [6 empty] | NEDIN |  | 138H | XNED358
AEP | North Edinburg Auto 345_1382 345/138 | XF | 345 | 20/5 | DCKT Loss of North Edinburg Train 345 kV | North Edinburt Auto 345_138 345/138 kV | RT | Planned | Y, N | [5 empty] | NEDIN | NEDIN | 345_1382 | XNED258
AEP | North Laredo Switch - Piloncillo | LN | 138 | 21/10 | Fowlerton - Lobo 345 kV | Laredo Vft North - Las Cruces 138 kV | RT | Planned | [6 empty] | NLARSW | PILONCIL | NLARSW_PILONC1 | SPILNLA8
LCRA, ONCOR | North McCamey - … - Odessa Ehv Switch | LN | 345 | 2018 | Basecase | McCamey GTC | ADD | [7 empty] | NORTMC | ODEHV | MCCAMEY_ODESSA | SNORODE5
STEC | Oaks Sub - Poteet Sub | LN | 69 | 18/1, 17/12 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 Kv | RT | Planned | [6 empty] | POTEETS | OAKS9 | POT_OAKS | SPOTOAK9
CNPE | Oasis - WA Parish | LN | 345 | 21/5 | Jones Creek - Refuge 345 kV & Jones Creek - South Texas Project 345 kV | Oasis - WA Parish 345 kV | RT | Planned | [6 empty] | OAS | WAP | OASWAP18A | SOASWA25
CNPE | Obrien - Wa Parish (OB_WAP98) | LN | 345 | 22/8 | DCKT Wa Parish-Jeanetta 345 kV | Wa Parish - Obrien 345 kV | RT | Planned | [6 empty] | WAP | OB | OB_WAP98 | SOBWA2P5
CNPE | Obrien - Wa Parish (OB_WAP99) | LN | 345 | 20/8, 22/8 | DCKT Wa Parish-Jeanetta 345 kV | Wa Parish - Obrien 345 kV | RT | Forced, Planned | [6 empty] | WAP | OB | OB_WAP99A | SOBWAP5
ONCOR, WETR | Odessa EHV Switch - Wett_Grelton | LN | 345 | 22/4, 22/3 | DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Scurry County South Switch - Wett_Long_draw 345 kV & Wett_Faraday - Wett_Long_Draw 345 kV, DCKT Scurry County South Switch - Tonkawa Switch 345 kV | Gail Sub - Willow Valley Switch 138 kV, Dewey Lake Tap - Polecat Creek Switch 138 kV, Luther - Vealmoor 138 kV, Kocht Tap - Vealmoor 138 kV | RT | Planned | [6 empty] | W_GT_345 | ODEHV | T-306 | SW_GODE5
LCRA | Odlaw Switch - … - Uvalde Aep | LN | 138 | 19/2, 22/11, 22/12 | Bighill - Kendal 345 kV, Big Hill - Twin Buttes 345 kV | Hamilton Road - Maverick 138kV, Ganso - Maverick 138 kV | RT | Planned, Forced | [6 empty] | BLEWET | ASPHALT | 222T570 | SBRAUVA8
GAR | Olinger - Wylie Switch (WYL_OLI1) | LN | 138 | 16/4 | Greenville Steam to Shelby 138 kV | Shelby Auto BT1 138/69 kV | ST | Forced | [6 empty] | WYLIESW | OLINGR | WYL_OLI1 | SFIRWY18
GAR | Olinger - Wylie Switch (WYL_OLI2) | LN | 138 | 16/9, 15/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | WYLIESW | OLINGR | WYL_OLI2 | SOLIWY18
GAR | Olinger - Wylie Switch (WYL_OLI3) | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | WYLIESW | OLINGR | WYL_OLI3 | SOLIEL28
AEP | Paint Creek Bus #1 (CB 4135, etc.) | BUS | 138 | 17/1, 16/6, 16/5 | Scurry Sw to Sun Sw 138 kV, Salt Creek Bepc to Salt Creek Reactor 138 kV | Eskota Sw - Longworth 69 kV, Aspermont Auto 69T1 138/69 kV | ST | Planned | [6 empty] | PAINTCRE |  | 8BB1 | N/A
AEP, BPUB | Palo Alto Sub - Titan Sub | LN | 138 | 16/5 | Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned | [6 empty] | PALOALTO | TITAN_SU | PALOAL_TITAN_1 | SPALSCA8
ONCOR | Paris Switch - Valley Ses | LN | 345 | 22/11 | Woodward Switch - Monitcello Ses 345 kV | Paris Switch AXFMR1H 345/138 kV | RT | Forced | [6 empty] | PRSSW | VLSES | 391_A | SPRSVLS5
ONCOR | Paris Switch - Valley South | LN | 345 | 22/11 | Woodward Switch - Monitcello Ses 345 kV | Paris Switch AXFMR1H 345/138 kV | RT | Forced | [6 empty] | PRSSW | VLYSO | 403_A | SVLYPRS5
ONCOR | Paris Switch CB_8635 | CB | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD | [7 empty] | PRSSW |  | 8635 | N/A
AEP, STEC | Pawnee Switching Station - Tango | LN | 345 | 22/2, 22/1, 21/11 | Coleto Creek - Grissom 345 kV & Fannin Sub - Goliad 69 kV, Grissom - Lon Hill 345 kV, Fowlerton - San Miguel Gen 345 kV | North Carbide - Sea Drift Coke 138 kV, Choke Canyon Aep - San Miguel Gen 138 kV, George West Switch Station - Sigmor 138 kV | RT | Forced, Planned | [6 empty] | PAWNEE | TANGO | PAWNEE_TANGO1 | STANPAW5
AEP | Port Aransas - Seawall Aep | LN | 69 | 18/1, 17/3 | DCKT Whitepoint to McCambell & Dupons Sw Ingleside 138 kV, DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 Kv, Barney Davis to Nelson Sharpe 138 kV, Nelson Sharpe Auto Trx Xf1 345/138 kV | Whitepoint - Rincon 138 kV, Rodd Field - Holly 138 kV | RT | Planned, Forced | [6 empty] | PORT_A | SEAWALL | PORT_A_SEAWAL1 | SSEAPO29
AEP | Primera - Rio Hondo | LN | 138 | 20/7 | La Palma-Rangerville (MVEC) 138 kV | Haine Drive - La Palma 138 kV | RT | Forced | [6 empty] | S_SNROSA | PRIMERA | PRIMER_S_SNRO11 | SS_SPRI8
CPS | Randolph - Weiderstein | LN | 138 | 15/9 | DCKT Skyline to Harmony & Nachches 138 kV | Fratt - Parkway Lcra 138 kV | ST | Planned | Y | [5 empty] | WEIDER | W2 | WEIDER_RAND | SW2WEI8
AEP | Refugio - … - Rincon | LN | 69 | 19/10, 19/9 | Victoria Auto 69A1 138/69 kV | Victoria Auto 69A2 138/69 kV | RT | Planned | [6 empty] | BONIVIEW | RINCON | BONIVI_RINCON1 | SBONRIN9
AEP | Refugio - … - Victoria | LN | 69 | 20/5 | Gila-…-Whitpoint 138 kV | Nueces Bay - Whitepoint 138 kV | RT | Planned | N | [5 empty] | OCONNOR | VICTORIA | REFUG_VICTO_1C | SGREVI29
AEP | Riley - Tesla | LN | 345 | 21/11 | DBCKT Edith Clarke - Riley 345 kV | Abilene Mulberry Creek - Long Creek 345 kV | RT | Planned | [6 empty] | RILEY | TESLA | RILEY_TESLA1 | STESRI15
AEP | Rincon - Whitepoint | LN | 138 | 22/4, 19/2 | Dupont Switch Ingleside - Hecker 138 kV & Dupont Switch Ingleside McCampbell 138 kV, McCampbell - … - Whitepoint 138 kV | Dupont Switch Ingleside - McCampbell 138 kV, Whitepoint TRX 138_69A1 138/69 kV | RT | Planned | [6 empty] | WHITE_PT | RINCON | RINCON_WHITE_2 | SRINWHI8
ONCOR | Russell Gap Switch - Killeen Switch (35091) | LN | 345 | 22/9 | Comanche Switch (Oncor) to Comanche Peak SES 345 kV, DCKT Bighil-Kendal 345 kV | Comanche Tap - Comanche Switch (Oncor) 138 kV, Yellow Jacket - Treadwell 138 kV | RT | Forced | [6 empty] | KLNSW | BUCSW | 35095 | SBWNBUC5
AEP, BRAZOS | Salt Creek SS - … - Spur | LN | 138 | 19/5 | DCKT Dermott Switch to Bluff Creek Switch & Golden Switch 138 kV | Morgan Creek SES - Sun Switch 138 kV | RT | Planned | [6 empty] | SLTCRKSS | SCKR | SCKR_SCK | SSPUSLT8
STEC | Sam Rayburn Switch - Vanderbilt Switch | LN | 138 | 15/10 | Loop 463 to Sam Rayburn 138 kV | Sam Rayurn Swithcing Station Auto 69_2 138/69 kV | ST | Planned | [6 empty] | RAYBURN | VANBLTSS | RAY_VANB | SVANRAY8
AEP | San Angelo College Hills - … - San Angelo Power Station | LN | 138 | 19/9 | San Angelo Paulann to San Angelo Red Creek 138 kV | San Angelo Concho - San Angelo Emerson Street 69 kV | RT | Planned | [6 empty] | SAPOWER | SOUTHLAN | SAPOWE_SOUTHL1 | SSASSA28
AEP | San Angelo Power Station - … - SA Highland Street | LN | 138 | 19/9 | San Angelo Coke Street to San Angelo Red Creek 138 kV | San Angelo Power Station - San Angelo South 69 kV | RT | Planned | [6 empty] | SAPOWER | SAST | SAPOWE_SAST1 | SSASRED8
AEP | San Angelo Red Creek Auto T2 345/138 kV | XF | 345 | 16/10 | San Angelo Red Creek Auto T1 345/138 kV | Nicole - Orient 138 kV | RT | Planned | [6 empty] | REDCREEK |  | T2H | XSA3R58
BRAZOS, ONCOR | Sardis - Sterrett | LN | 138 | 22/2 | Corsicana -…- Montfort Switch 138 kV & Montfort Switch - Trinidad Ses 138 kV | Desoto Switch - Red Oak 138 kV | RT | Planned | [6 empty] | STERT | SARDIS | 951_A | SSARSTE8
ONCOR, WETR | Scurry County South Switch - Wett_Long_Draw | LN | 345 | 22/4, 22/5 | DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Odessa EHV Switch - Wett_Grelton 345 kV, Wett_Grelton - Wett_Long_Draw 345 kV | Falcon Seaboard - Morgan Creek Ses 345 Kv | RT | Planned | [6 empty] | W_LD_345 | SCOSW | T-304 | SW_LSCO5
AEP, BRAZOS | Scurry Switch - … - Spur | LN | 138 | 16/10, 16/3 | Aspermont Aep to Spur 138 kV | Spur Auto 69_1 138/69 kV | ST | Planned | Y, N | [5 empty] | SCURRYSW | SCK | SLTCRK_SCRYSW | SSPUMW18
BPUB | Sixth Street Substation - South Plant Substation | LN | 138 | 18/4, 18/3 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV; | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned | [6 empty] | SOUTH_PL | SIXTH_ST | 6ST_SP | SSIXSOU8
ONCOR | Snyder - … - Sun Switch (6240) | LN | 138 | 21/4 | DCKT Dermott Sw-…- Bluff Creek Sw & Ennis Creek Sw 138 kV | Morgan Creek Ses - Sun Switch 138 kV | RT | Planned | N | [5 empty] | SNYDR | DPCRK | 6240_A | SSACSUN8
CNPE | South Texas Project - WA Parish | LN | 345 | 22/3, 22/2, 21/12, 21/9, 23/2 | Jones Creek - Refuge 345 kV & Jones Creek - South Texas Project 345 kV, Jones Creek - South Texas Project 345 kV & Refuge - South Texas Project 345 kV, Hillje - Wolf 345 kV | Hillje - South Texas Project 345 kV, Blessing - Pavlov 138 kV, Jones Creek - South Texas Project 345 kV | RT | Planned | [6 empty] | STP | WAP | STPWAP39 | STPWAP39
BPUB, STEC | Southmost Sub - Waterport Sub | LN | 138 | 18/1 | Lon Hill to Coleto Creek 345 kV, La Palma to East Harrison 69 kV, DCKT Jewett to Singleton 345 kV | Warburton Road Switching Station - Victoria 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced | [6 empty] | WATERPRT | SOUTHMOS | WP_SM | SSOUWAT8
CNPE | Sr Bertron - Texas | LN | 138 | 21/2 | DCKT Chambers-King & Chambers Jordan-North Belt 345 kV | Exxon - Lynch 138 kV | RT | Forced | [6 empty] | SRB | TX | SRBTX_87A | STXSRB8
BRAZOS | Stephenville Bepc Auto FMR1 138/69 kV | XF | 138 | 15/3 | Oran Sub to Mineral Wells & RW Miller 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | STV |  | FMR1 | XSTV289
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Tri Corner & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | SCSES | TRSES | 480 | STRSSCS5
ONCOR | Tall City - Telephone Road | LN | 138 KV | 2023/4 | NATURAL DAM to BEALS CREEK 138 kV | Big Spring West - Stanton East 138 kV | RT | Planned | [6 empty] | TALLCITY | TELPH_RD | TALLCITY_TELPR | STALTEL8
CNPE | Th Wharton - Zenith (THWZEN71) | LN | 345 | 22/12 | DCKT Singleton to Tomball 345 kV and Kuykendahl to Roans Prairie 345 kV and Kuykendahl to Rothwood 345 kV | Thw Wharton - Zenith (THWZEN98) 345 kV | RT | Planned | [6 empty] | THW | ZEN | THWZEN71 | SZENTHW5
CNPE | TH Wharton - Zenith (THWZEN98) | LN | 345 | 22/4, 22/3, 20/4 | DCKT Singleton to Tomball 345 kV and Kuykendahl to Roans Prairie 345 kV and Kuykendahl to Rothwood 345 kV | TH Wharton - Zenith (THWZEN71) 345 kV | RT | Planned, Forced, Forced | [6 empty] | THW | ZEN | THWZEN98 | SZENTH35
TNMP | TI TNP - West TNP | LN | 138 | 21/10 | DBCKT Carrollton Northwest - Lewisville Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV | RT | Planned | [6 empty] | LWVTI | LWSVW | 588_A | SLWSLW48
ONCOR | Tri Corner - Tyler Grande | LN | 345 | 2017 | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | TRCNR | TYGND | 341 | STYGTRC5
ONCOR | Tri Corner - Watermill Switch (215) | LN | 345 | 20/2, 19/10, 19/9 | DCKT Centerville Road Switch to Parkdale Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Prairie Creek - Scyene Road 138 kV, Kleberg Tap - Seagoville 138 kV | RT | Planned | [6 empty] | TRCNR | WTRML | 215 | STRCWTR5
ONCOR | Tri Corner - Watermill Switch (515) | LN | 345 | 20/2, 19/10, 19/9 | DCKT Parkdale Switch - Centerville Road Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Prairie Creek - Scyene Road 138 kV, Kleberg Tap - Seagoville 138 kV | RT | Planned | [6 empty] | TRCNR | WTRML | 515 | STRSWTR5
AEP | Weil Tract - Westside Aep | LN | 138 | 18/11 | DCKT Citgo N Oak Park 0 Hiway 9 138 kV & Hiway 9 - Industrial Aep 69 kV | Morris Street - Nueces Bay 138 kV | RT | Planned | [6 empty] | SEIL_TRC | WESTSIDE | WEIL_T_WESTSI1 | SWEIWES8
WETR | Wett_Bearkat - Wett_Sand_Bluff | LN | 345 | 22/4 | Longshore Switch - Morgan Creek Ses 345 kV & Morgan Creek Switch - Quail Switch 345 kV, Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV, Midessa South Sw - Spraberry Switch 138 kV & Odessa EHV Switch - Spraberry Switch 138 kV | Forest Creek and Sand Bluff Wind Farms - Morgan Creek Ses 138 kV | RT | Planned | [6 empty] | W_SB_345 | W_BK_345 | T-309 | SW_BW_25
WETR | Wett_Grelton - Wett_Long_Draw | LN | 345 | 22/4 | DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses | Gail Sub - Key Sub 138 kV | RT | Planned | [6 empty] | W_GT_345 | W_LD_345 | T-305 | SW_GW_L5
AEP | Whitepoint Auto 345A 345/138 kV | XF | 345 | 18/3 | Lon Hill Auto Trx Lon_Hill_3_2 345/138 kV | Lon Hill Auto 381H 345/138 kV | RT | Forced | [6 empty] | WHITE_PT |  | 345A | XWHI58

## Removal Requests
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Contingency | Overload | Addition or Removal Requestor | Reason for Addition or Removal
AEN | Aen Hidden Valley - Riverplace | LN | 138k | DCKT Barton - Salem & HICROSS AEN - Marshall Ford 138kV | Barton - Vega 138 kV | AEN | This was a Feb 2023 Ice Storm forced outage, a relay operation due to a failed shield wire. It's a forced outage that overlapped with a planned outage and another forced outage shown on the MTE worksheet that also impact the identified contingency loading. It also overlapped with a forced outage not shown in the MTE worksheet but that occurred in the same substation (Hidden Valley) that also impacts the identified contingency loading. The unlisted forced outage, found in the consolidated outage report from the MIS was LCRA's 626T6261 Hidden Valley to Balcones Research Tap.
AEN | Cistern - Lytton Springs | LN | 345 | DCKT Fayette Plant 1 and 2 - Lostpine & Winches 345kV | Fayetteville Auto AT2H 345/138 kV | AEN | This was a Feb 2023 Ice Storm forced outage, a relay operation due to a failed shield wire. It's a forced outage that overlapped with a planned outage shown on the MTE worksheet that also impacts the identified contingency loading.
AEN | Garfield Aen - Hicross Aen | LN | 138 | DCKT Austro - Daffin & Dunlap - Decker 138kV | Garfield Aen - Stoney_ Ridge 138 kV | AEN | This was a planned outage that lasted 39 days and produced a single day of congestion in October 2022. I’m unable to find an overlapping forced or planned outage that also contributed to this congestion. We also had the line out in May 2022 for 4 days, a particularly warm May and that outage also produced no congestion.
LCRA AEN | Hillje - Holman Aen | LN | 345 | SOUTH TEXAS PROJECT to HILLJE (HLJSTP64) 345 kV | Hillje - South Texas Project 345 kV | AEN | This was a forced outage 6-hr outage following a relay operation due to contaminated isulators. I'm unable to find simultaneous outages contributing to this one day of congestion but there were 13 additional days of congestion on this same line during the month.
LCRA | Bergheim - Antler | LN | 138 | DCKT Cagnon-Kendal 345 & Cico-Comfor 138 | Bergheim Auto AT1H 345/138 kV | LCRA | This MTE should be removed because the congestion was due to other simultaneous outage: T389 Bergheim-Hays Energy. | BERGHE | ANTLER | 493T493 | SANTBER8
LCRA | Cibolo - Scherz | LN | 138 | DCKT Hill Country-Marion 345 kV | Cibolo - Schertz 138 kV | LCRA | This MTE should be removed because the congestion was due to multiple simultaneous outages: T302 CIBOLO-MARION and T304 CIBOLO-SCHERTZ. | CIBOLO | SCHERT | 293T304 | SSCHCI28
LCRA | Fayetteville - Frelsburg | LN | 138 | DCKT VANBLT-ETP 138kV&ELTORSS-EDNAS 69kV | Danevang Switching Station Auto 138_69 138/69 kV | LCRA | This MTE should be removed because the congestion was due to multiple simultaneous outages in the FAYETT area: T177 FAYETT-SALEM; T274 FAYETT-PISEK; T247 FAYETT-ROUNTO; T210 FAYETT-FPPYD1; T216 FAYETT-WILLSP; T253 FAYETT-FPP138; FAYETT AT2 | FAYETT | FRELSB | 154T176 | SFAYFRE8
LCRA | Glidden - Weimar | LN | 138 | DCKT Vanderbelt Switching Station - Energy Transfoer Partners 138 kV & EL Toro Switching Station - Edna Substation 69kV | Danevang Switching Station Auto 138_69 138/69 kV | LCRA | This MTE should be removed because the congestion was due to multiple simultaneous outages: T177 FAYETT-SALEM; T274 FAYETT-PISEK; T247 FAYETT-ROUNTO; T210 FAYETT-FPPYD1; T216 FAYETT-WILLSP; T253 FAYETT-FPP138; FAYETT AT2 | GLIDDE | WEIMAR | 704T704 | SWE2GLI8
LCRA | Graphite Mine -…- Lampasas | LN | 138 | Joslin - Formasa 138 kV | Lolita - Victoria 138 kV | LCRA | This MTE should be removed because the congestion was due to multiple simultaneous outages: T635 CORONA_BUBORA, T365 WIRTZ-FLATRO | DOBYVI | LAMPAS | 717T715 | SLAMGRA8
LCRA | Harper Road -Jack Furman | LN | 138 | Yellow Jacket PS_1 138/138, DCKT Cagnon - Kendall 345 & Cico - Comfor 138 kV, Kendall - Kendal CTEC 138 kV | Hollmig - Kendall 138 kV | LCRA | This MTE should be removed because the congestion was due to the following simultaneous outage: DSW_2084 at KERRST | JACKFU | HARPRO | 62T368 | SHARJAC8
LCRA | Hilltop - Strahan | LN | 138 | DCKT Zorn - Austro & Lytton Springs 345kV | Redwood - Sanm Marcos 138 kV | LCRA | This MTE should be removed because the status of breakers 9660 and 4230 at MCCALA are being changed to N.O. to reduce the flow from MCCALA-RATTLE-REDWOO-SANMAR | HILLTO | STRAHAT1 | 445T445 | SHILSTR8
LCRA,ONCOR | Hutto Switch - Zorn | LN | 345 | DCKT Zorn - Austro & Lytton Springs 345kV | Redwood - Sanm Marcos 138 kV | LCRA | This MTE should be removed because the status of breakers 9660 and 4230 at MCCALA are being changed to N.O. to reduce the flow from MCCALA-RATTLE-REDWOO-SANMAR | ZORN | HUTTO | 510T510 | SHUTZOR5
LCRA | Lakeway Aen -…- Marshall Ford | LN | 138 | Kendall - Kendall CTEC 138 kV | Hollmig - Kendall 138 kV | LCRA | This MTE should be removed because of multiple simultaneous outages: T123 KERRST-KENDAL, T225 KERRST-VERDCR, T383 KERRST-KERRTR, DSW 2084 at KERRST, High wind | MARSFO | PALEPE | 231T323 | SBEEMA28
LCRA | Marshall Ford - Mcneil | LN | 138 | DCKT Barton - Salem & Hicross Aen - Marshall Ford 138kV | Barton - Vega 138 kV | LCRA | This MTE should be removed because the congestion was due to other simultaneous outages: CKT_965 Hidden Valley-River Place and T626 Hidden Valley-Balcones Research Tap. | MARSFO | MCNEIL_ | 212T197 | SMARMCN8
LCRA,ONCOR | Round Rock - Spanish Oak | LN | 138 | DCKT Barton - Salem1 & Hicross-Marshall Ford 138kV | Barton - Vega 138 kV | LCRA | This MTE should be removed because the congestion was due to other simultaneous outages: CKT_965 Hidden Valley-River Place and T626 Hidden Valley-Balcones Research Tap. | SPANOA | RNDRK | 642T642 | SRNDSPA8
LCRA | Smithville … Sim Gideon | LN | 138 | AEN Dunlap - Lost Pines AEN 345 kV & Austrop - Lost Pines AEN 345 kV | Sim Gideon - Winchester 138 kV | LCRA | This MTE should be removed because of multiple simultaneous outages: T255 FPPYD2-LYTTON, CKT_3121 HOLMAN-LYTTON | ALUMCR | SMITHV | 200T150 | SSMIGID8
LCEC, ONCOR, RAYBN | Bonham Lake POI -…- Paris Switch | LN | 138 | Woodward Switch - Monitcello Ses 345 kV | Comsw Switch - Commerce 138 kV | Oncor (Multiple Outages) | The congestion experienced in Nov of 2022 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in Nov of 2022 is due to multiple simultaneous outages in the area: * COMMERCE SWITCH - ENLOE POI (875_F) (ONC00492910 - 11/03/2022 - 11/14/2022) * DELTA SUB SWT 14943 - ENLOE TAP PS1 (871_C) (ONC00492916 - 11/03/2022 - 11/14/2022) * PARIS SWITCH SWT 8627 - VALLEY SES BKR 4150 (391_A) (ONC00544646 - 11/04/2022 - 11/21/2022) * PARIS SWITCH SWT 8642 - VALLEY SOUTH SWT 8417 (403_A) (ONC00544647 - 11/04/2022 - 11/21/2022)
ONCOR | Burnet Switch Auto AXFMR1 138/69 kV | XF | 138 | DCKT Riley - Krum Switch 345 kV | Riley - Oklaunion (OKLA_RILEY2) 345 kV | Oncor (LODF Analysis) | Per Oncor review, this MTE has 0% impact on the constraint. So, Oncor is requesting removal this MTE.
ONCOR | Corsicana -…- Trinidad SES | LN | 138 | Montfort Switch - Chatfield 138 kV | Hubbard - Haney Bepc 138 kV | Oncor (Multiple Outages) | The congestion experienced in Feb of 2023 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in Feb of 2023 is due to multiple simultaneous outages in the area: * BOSQUE SWITCH BKR 2715 - ROGERS HILL BEPC SWT 2745 AND SWT 2744 (1030_B) (23-06664 - 02/28/2023 - 02/28/2023) * TRINIDAD SES 138 KV BUS-NORTH (ONC00557537- 02/27/2023 - 03/03/2023)
ONCOR | Deen Switch -…- Hicks Switch (6271_A) | LN | 138 | DCKT Eagle Mountain Ses - Deen Switch 138 kV | Wagley Robertson - Hicks Switch 138 kV (6270_D) | Oncor (Multiple Outages) | The congestion experienced in March of 2023 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in March of 2023 is due to multiple simultaneous outages in the area: * HORSEMAN SWT 22725 - SUMMERFIELD SWT M10/M70 (6271_C) (ONC00554312 - 03/20/2023 - 04/03/2023) * PARK VISTA POI SWT 13265 - ROANOKE SWITCH BKR 3835 (1055_D) (ONC00542446 - 03/21/2023 - 04/06/2023) * PARK VISTA POI SWT 13267 - ROANOKE SWITCH BKR 3865 (1060_F) (ONC00559034 - 03/21/2023 - 04/05/2023)
ONCOR | Deen Switch -…- Hicks Switch (6271_C) | LN | 138 | DCKT Eagle Mountain Ses - Deen Switch 138 kV | Wagley Robertson - Hicks Switch 138 kV (6270_D) | Oncor (Multiple Outages) | The congestion experienced in March of 2023 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in March of 2023 is due to multiple simultaneous outages in the area: * HICKS SWITCH BKR 13600/13605 - WAGLEY ROBERTSON SWT 7088/7089 (6271_A) (ONC00562526 - 03/20/2023 - 04/03/2023) * PARK VISTA POI SWT 13265 - ROANOKE SWITCH BKR 3835 (1055_D) (ONC00542446 - 03/21/2023 - 04/06/2023) * PARK VISTA POI SWT 13267 - ROANOKE SWITCH BKR 3865 (1060_F) (ONC00559034 - 03/21/2023 - 04/05/2023)
ONCOR | Falcon Seaboard - Morgan Creek Ses | LN | 345 | ODESSA EHV SWITCH to QUAIL SWITCH 345 kV | Midessa South SW AXFMR1H 345/138 kV | Oncor (Transmission Project Complete) | Remove overload element "Midessa South SW AXFMR1H 345/138 kV" and its associated contingency "ODESSA EHV SWITCH to QUAIL SWITCH 345 kV" due to completion of TPIT project 66530 (Add Consavvy 345/138 kV Switch).
ONCOR | Grey Well Draw Switch -...- Pronghorn & South Midland | LN | 138 | Skywest - Spraberry Switch 138 kV | South Midland - Consavvy Switch 138 kV | Oncor (Transmission Project Complete) | Remove this MTE as no overload expected on this constraint due to completion of TPIT project 66530 (Add Consavvy 345/138 kV Switch)
ONCOR | Handley SES -…- Sherry Switch (6410_B) | LN | 138 | DBCKT Deen Switch -…- Hicks Switch 138 kV, DBCKT Everman Switch -…- Handley Ses 138 kV | Hemphill - Mistletoe Heights 138 kV | Oncor (Multiple Outages) | The congestion experienced in Dec of 2021 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in Dec of 2021 is due to multiple simultaneous outages in the area: * HANDLEY SES BKR 4190 - LAKEWOOD (ONCOR) SWT 4215 (6410_D) (ONC00499726 - 11/22/2021 - 12/15/2021) * ARLINGTON SWT J-531 (On circuit 6415) (21-09456 - 09/25/2021 - 01/30/2022) The congestion experienced in Oct of 2021 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in Oct of 2021 is due to multiple simultaneous outages in the area: * HANDLEY SES BKR 4190 - LAKEWOOD (ONCOR) SWT 4215 (6410_D), LAKEWOOD (ONCOR) SWT 4215 - PANTEGO SWT 4694 (6410_E) (ONC00465085, ONC00465086 - 09/26/2021 - 10/25/2021) * ARLINGTON SWT J-531 (On circuit 6415) (21-09456 - 09/25/2021 - 01/30/2022) * CENTURY BKR 6190/SWT 6203 - SHERRY SWITCH SWT 6248 (160_B) (ONC00496529 - 10/23/2021 - 10/24/2021) * SHERRY SWITCH AUTO #2 (ONC00496516 - 10/23/2021 - 10/24/2021) The congestion experienced in Sep of 2022 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in Sep of 2022 is due to multiple simultaneous outages in the area: * EULESS TRINITY BLVD SWT 10701 - INTERNATIONAL AIRPORT SWT 4205/4218 (1320_C) (ONC00512004 - 09/19/2022 - 10/08/2022) * BROOKHOLLOW 2 TAP - EULESS TRINITY BLVD SWT 10694 (6435_E) (ONC00512012 - 09/19/2022 - 10/12/2022) * PANTEGO SWT 4692 (ONC00509791 - 09/20/2022 - 10/25/2023) * CALMONT SWITCH 138KV WEST BUS (ONC00518470, ONC00518471, ONC00518472 - 09/26/2022 - 10/14/2022)
ONCOR | Handley Ses -…- Sherry Switch (6415_B) | LN | 138 KV | DBCKT Everman Switch -…- Handley Ses 138 kV | Hemphill - Mistletoe Heights 138 kV | Oncor (Multiple Outages) | The congestion experienced in Sep of 2022 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in Sep of 2022 is due to multiple simultaneous outages in the area: * EULESS TRINITY BLVD SWT 10701 - INTERNATIONAL AIRPORT SWT 4205/4218 (1320_C) (ONC00512004 - 09/19/2022 - 10/08/2022) * BROOKHOLLOW 2 TAP - EULESS TRINITY BLVD SWT 10694 (6435_E) (ONC00512012 - 09/19/2022 - 10/12/2022) * PANTEGO SWT 4692 (ONC00509791 - 09/20/2022 - 10/25/2023) * CALMONT SWITCH 138KV WEST BUS (ONC00518470, ONC00518471, ONC00518472 - 09/26/2022 - 10/14/2022)
LCRA,ONCOR | Hutto Switch - Zorn | LN | 345 | DCKT Zorn - Austro & Lytton Springs 345kV | Redwood - Sanm Marcos 138 kV | LCRA | Per LCRA comment "This MTE should be removed because the status of breakers 9660 and 4230 at MCCALA are being changed to N.O. to reduce the flow from MCCALA-RATTLE-REDWOO-SANMAR."
ONCOR | Liggett Switch - Venus Switch (528) | LN | 345 | Liggett Switch to Venus Switch 345 kV | Britton Road - Venus Switch 345 kV (530_C) | Oncor (Transmission Project Complete) | Remove Britton Road - Venus Switch 345 kV (530_C) overload element and its associated contingency Liggett Switch to Venus Switch 345 kV as the overload element Britton Road - Venus Switch 345 kV (530_C) was upgraded as a part of TPIT project 6273 "Upgrade existing Venus - Webb/Cedar Hill Sw. Sta. 345 kV Double Ckt Line" (ISD - 12/12/2022)
ONCOR | Liggett Switch - Venus Switch (529) | LN | 345 | DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV | Britton Road - Venus Switch 345 kV (530_C) | Oncor (Transmission Project Complete) | Remove Britton Road - Venus Switch 345 kV (530_C) overload element and its associated contingency DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV as the overload element Britton Road - Venus Switch 345 kV (530_C) was upgraded as a part of TPIT project 6273 "Upgrade existing Venus - Webb/Cedar Hill Sw. Sta. 345 kV Double Ckt Line" (ISD - 12/12/2022)
ONCOR | Midessa South Sw -…- Midland East | LN | 138 | Manual Single Midland East -Falcon Seaboard 345 kV & Midland East Auto AMR2, Midland East Auto AXFMR2 345/138, Natural Dam - Beals Creek Sub 138 kV | Midalnd County Northwest - Mockingbird 138 kV, Big Spring West - Stanton East 138 kV | Oncor (Transmission Project Complete) Oncor (LODF Analysis) | Remove Midalnd County Northwest - Mockingbird 138 kV overload element and its associated contingency Manual Single Midland East -Falcon Seaboard 345 kV & Midland East Auto AMR2, MIDLAND EAST Auto AXFMR2 345/138 due to "Add Midland County NW - Texaco Mabee Tap 138 kV Double-Circuit Line Section Rebuild (ISD - 12/2022)" as a part of TPIT project 57925. Remove overload element "Big Spring West - Stanton East 138 kV" and associated contingency "NATURAL DAM - BEALS CREEK SUB 138 kV" as this MTE is reducing the flow on the contraint as per LODF analysis.
ONCOR | Odessa … Odessa EHV Switch | LN | 138 | Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 kV | General Tire Switch - Rexall 138 kV, Midessa South SW AXFMR1 345/138 kV | Oncor (Transmission Project Complete) | Remove this MTE as no congetion expected on this constraints due to completion of TPIT project 66530 (Add Consavvy 345/138 kV Switch)
ONCOR | Odessa EHV Switch - Quail Switch | LN | 345 | Falcon Seaboard - Midland East 345 kV & Falcon Seaboard - Morgan Creek Ses 345 kV, ODESSA EHV SWITCH to MIDESSA SOUTH SW | Morgan Creek Ses AXFMR1 345/138 kV | Oncor (LODF Analysis) | This MTE has minimum impact (less than 2%) on the constarint as per LODF analysis. With completion of (TPIT project 66530) Consavvy project, it reducing the flow on the constraint.
LCRA,ONCOR | Round Rock - Spanish Oak | LN | 138 | DCKT Barton - Salem1 & Hicross-Marshall Ford 138kV | Barton - Vega 138 kV | LCRA | Per LCRA comment "This MTE should be removed because congetion was due to other simultaneous ouatges: CKT_965 Hidden Valley-River Place and T626 Hidden Valley-Balcones Research Tap." Per Oncor's review this MTE and contingency are reducing the flow on the constraint. So, Oncor is requesting validation of this MTE association with the constraint.
ONCOR | Salt Flat Road (Su_1956) - Skywest | LN | 138 | Natural Dam - Beals Creek 138 kV | Big Spring West - Stanton East 138 kV | Oncor (LODF Analysis) | Per Oncor review, this MTE is not impacting the constraint.
ONCOR | Timberview Switch - Venus Switch | LN | 345 | Timberview Switch - Courtland 138 kV | Park Row - Sherry Switch Switch 138 kV | Oncor (Multiple Outages) | The congestion experienced in Novermber of 2022 is due to multiple simultaneous outages in the area: This MTE is not the only contributor, the congestion experienced in November of 2022 is due to multiple simultaneous outages in the area: * SHERRY SWITCH AUTO #1 (ONC00510473 - 09/16/2022 - 11/20/2022) *CEDAR HILL SWITCH BKR 342 - WEBB SUB BKR 7680/SWT 7684 (530_A) (ONC00507755 - 09/19/2022 - 11/12/2022) * GRAND PRAIRIE SWT 4401, SWT 4402 (ONC00528322 - 10/13/2022 - 04/01/2023) * SHERRY SWITCH BKR 4690, SWT 4689, SWT 4691 (ONC00523616 - 10/25/2022 - 11/23/2022)
AEP, CNPE | Angstrom - South Texas Project | LN | 345 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV, Dyann to Wharton 138 kV, Danevang Switching Station to Blessing 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Blessing Auto 69A1 138/69 kV, El_Campo - Lane City Pump 138 kV | AEP/RT | Refugio - Melon Creek - Seadrift lines were rebuilt following Hurricane Harvey. As well as multiple other lines/forced outages at the time that were repaired
AEP | Blessing Auto 1382 345/138 kV | XF | 345 | Lane City - South Lane City 138 kV | Franklins Camp Sub - Sargent Sub 69 kV | AEP/RT | STEC built new station Cayce tying AEP Markham into STEC Van Vleck - Shropshire line
AEP | Blessing Auto 69A1 138/69 kV | XF | 138 | Coleto Creek to Victoria 138 kV, DCKT San Miguel Gen to Elmcreek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 | Coleto Creek - Victoria 138 kV, Pawnee Switching Station - Calaveras 345 kV, San Miguel Auto ATAH 345/138 KV | AEP/RT | Coincides with Hurricane Harvey damage being repaired
AEP | Melon Creek - Refugio | LN | 138 | DCKT Hecker - Whitepoint 138 kV, Formosa - Lolita 138 kV | Rincon - Whitepoint 138 kV, Victoria - Victoria Dupont Switch 138 kV | AEP/RT | Rincon - white point line rebuilt Fall 23
AEP | Victoria 69A2 138/69 kV | XF | 138 | Victoria Auto 69A1 138/69 kV | Magruder - Victoria 138 kV | AEP/RT | Victoria PS was undergoing rebuild outages during this time
AEP | Victoria Auto 69A1 138/69 kV | XF | 138/69 | Melon Creek-Rincon line 1 138 kV, Victoria Auto 69A2 138/69 kV | Bonnieview - Ricon, Magruder - Victoria 69 kV | AEP/RT | Victoria PS was undergoing rebuild outages during this time
AEP | Albany Aep -…- Throckmorton | LN | 69 | DCKT RILEY TO KRWSW 345 DBLCKT | Riley - Oklaunion 345 kV |  | Not seeing overloads on 69kV system for the loss of 345kV lines
AEP, ETT, ONCOR | Krum West Switch - Riley (37030) | LN | 345 | DCKT Clear Crossing-Coulomb & Clear Crossing-Smoky Hill 345 kV | Fisher Road Switch - Riley 345 kV |  | ONCOR is replacing approx 16 miles of OPGW
AEP | Asherton - Bevo | LN | 138 | Basecase | Low Voltage from Dimmit to DC Eagle Pass | Remove | Basecase will be resolved after Brackettville - Escondido line in service
AEP | Ajo … Bruennings Breeze | LN | 345 | Lon Hill - North Edinburg 345 kV & Lon Hill - Orange Grove Switching Station 138 kV, Lon Hill - North Edinburg - Bonilla - El Trueno Wind Farm 345 kV & Primera-…- Rio Hondo 138 kV, Lon Hill - Nelson Sharpe 345 kV | Falfurrias - Premont 69 kV, Burns Sub - Rio Hondo 138 kV, Las Pulgas - Raymondville 2 138 kV, Celanese Bishop - Kleberg Aep 138 kV | AEP/RT | Line no longer exists
AEP, CNPE | Angstrom - South Texas Project | LN | 345 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV, Dyann to Wharton 138 kV, Danevang Switching Station to Blessing 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Blessing Auto 69A1 138/69 kV, El_Campo - Lane City Pump 138 kV | AEP/RT | Refugio - Melon Creek - Seadrift lines were rebuilt following Hurricane Harvey. As well as multiple other lines/forced outages at the time that were repaired
AEP | Dupont Switch Ingleside - Hecker (HECKER_I_DUPS2) | LN | 138 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | AEP/RT | line being rebuilt
AEP | Hiway 9 - Javelina | LN | 138 | DCKT Hecker - Whitepoint 138 kV | Rincon - Whitepoint 138 kV | AEP/RT | Line being rebuilt
AEP | Hiway 9 Auto 69A2 138/69 kV | XF | 138 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | AEP/RT | New 138 Champlin - Valero East line
AEP | Industrial Aep - Nueces Bay | LN | 69 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | AEP/RT | New 138 Champlin - Valero East line
AEP | Kleberg Aep - Loyola Sub | LN | 138 | Ajo-Nelson Sharpe 138 kV | Falfurrias - Premont 69 kV | AEP/RT | Line rebuilt Spring 23
CNPE | Bailey - Hillje | LN | 345 | Jones Creek - Refuge 345 kV & Jones Creek - South Texas Project 345 kV | Blessing - Pavlov 138 kV | CNPE (Removal) | This MTE should be removed. MTE (Bailey - Hillje) was modified to add a new 345kV Substation (Blue) on 10/2022. Bailey - Hillje Line was split into Bailey to Blue and Blue to Hillje Line.
CNPE | Bellaire - Jeanette | LN | 345 | Bellaire - Smithers 345 kV & Bellaire - WA Parish 345 kV | Bellaire - Sharpstown 138 kV | CNPE (Removal) | This MTE should be removed. As of 5/5/2023, upgrades to Bellaire - Sharpstown 138 kV should mitigate this issue.
CNPE | Bellaire - Smithers (BI_SMR98) | LN | 345 | DCKT Wa Parish to Jeanetta 345 kV | Bellaire - Wa Parish 345 kV (LN 50) | CNPE (Removal) | This MTE should be removed. As of 12/31/2023, upgrades to Bellaire - Wa Parish 345 kV (LN 50) should mitigate this issue.
CNPE | Cedar Bayou Plant - Center | LN | 345 | Jordan - King 345 kV & Jordan - North Belt 345 kV, North Belt - Th Wharton 345 kV | Bigvue - Lyondell 138 kV, Jefferson - South Channel 138 kV, Airline - White Oak 138 kV | CNPE (Removal) | This MTE should be removed. As of 7/31/2023, upgrades to Bigvue - Lyondell 138 kV should mitigate this issue. Not valid. As of 7/31/2023, upgrades to Airline - White Oak 138 kV should mitigate this issue.
CNPE | Citfil - Normandy | LN | 138 | Jordan - King 345 kV & Jordan - North Belt 345 kV | Bigvue - Lyondell 138 kV | CNPE (Removal) | This MTE should be removed. As of 7/31/2023, upgrades to Bigvue - Lyondell 138 kV should mitigate this issue.
CNPE | Dow Chemical - Oasis (DOWOAS18) | LN | 345 | Cedar Creek - WA Parish 345 kV & WA Parish - Wolf 345 kV, DCKT Jones Creek-South Texas Project & Refuge 345 kV | South Texas Project - WA Parish 345 kV, Bay City Sub - Sargent Sub 69 kV, Dow Chemical (DOWOAS27) - Oasis 345 kV, Angleton - Winmil 138 kV | CNPE (Removal) | This MTE should be removed. As of 4/30/2023, upgrades to Angleton - Winmil 138 kV should mitigate this issue.
CNPE | Jones Creek - Refuge | LN | 345 | Hillje - Wolf 345 kV | Refuge - South Texas Project 345 kV | CNPE (Removal) | This MTE should be removed. This MTE would create a radial line Peyton - Refuge and Refuge - South Texas Project 345 KV. An outage of this element would not contribute to system congestion.
CNPE | Jordan - King | LN | 345 | Jordan - King 345 kV & Jordan - North Belt 345 kV, DCKT Crown - Tanker 138 kV & Davson - ... - Greens Bayou 138 kV, DCKT Power System Arco Cogen - ... - Crosby & Riverside 138 kV | Bigvue - Lyondell 138 kV, Lychem - Power Systems Arco Cogen 138 kV | CNPE (Removal) | This MTE should be removed. As of 7/31/2023, upgrades to Bigvue - Lyondell 138 kV should mitigate this issue.
CNPE | Meadow - Oasis | LN | 345 | DCKT Jordan - King & Jordan - Northbelt 345 kV | Bigvue - Lyondell 138 kV | CNPE (Removal) | This MTE should be removed. As of 7/31/2023, upgrades to Bigvue - Lyondell 138 kV should mitigate this issue.
CNPE | Meadow - Ph Robinson | LN | 345 | DCKT Gable Street -…- Greens Bayou 138 kV, NORTH ALVIN TNP - ALVIN TNP 138 kV , DCKT Davidson - ..-Greens Bayou BY21 & Crown - Tanker 138 kV, DCKT Power Syastems Arco Gen -..- Crosby & Riverside 138 kV | Bigvue - Lyondell 138 kV, Magnolia Tnp - Seminole Tnp 138 kV | CNPE (Removal) | This MTE should be removed. As of 7/31/2023, upgrades to Bigvue - Lyondell 138 kV should mitigate this issue.
CNPE | Roans Prairie - Singleton | LN | 345 | North Belt - Th Wharton 345 kV | Airline - White Oak 138 kV | CNPE (Removal) | This MTE should be removed. As of 7/31/2023, upgrades to Airline - White Oak 138 kV should mitigate this issue.

## Oncor Comments
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Commentor | Comment | OCITF Consensus | Decision | Discussion Items
LCRA, STEC | Bakersfield - Cedar Canyon | LN | 345 | 22/4 | Midessa South Sw - Odessa EHV Switch 345 kV & Morgan Creek Ses -…- Quail Switch 345 kV, Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV, Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 kV | Midessa South SW AXFMR1 345/138 kV, Dewey Lake Tap - Polecat Creek Switch 138 kV, Falcon Seaboard - Morgan Creek Ses 345 kV, Odessa - Odessa North 138 kV | RT | Planned | Oncor | Oncor Comments: Change contingency from "Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV" to "DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses" due to completion of consavvy project.
WETR | Bernoulli - Wett_Bearkat | LN | 345 | 23/4 | SKYWEST to SPRABERRY SWITCH 138 kV | South Midalnd - Consw Switch 138 kV | RT | Planned | Oncor | Oncor Comments: No overload expected on this constraint due to completion of TPIT project 66530 (Add Consavvy 345/138 kV Switch)
WETR | Wett_Grelton - Wett_Long_Draw | LN | 345 | 22/4 | Longshore Switch - Morgan Creek Ses 345 kV & Morgan Creek Switch - Quail Switch 345 kV | Gail Sub - Key Sub 138 kV | RT | Planned | Oncor | Oncor Comments: Change contingency from "Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV" to "DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses" due to completion of consavvy project.
ONCOR | Austrop - Sandow Switch (440) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV (1661_A), Gilleland Creek - Mcneil 138 kV | RT | Planned | Oncor | Add LCRA in TDSP column.
ONCOR | Austrop - Sandow Switch (450) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV (1661_A), Gilleland Creek - Mcneil 138 kV | RT | Planned | Oncor | Add LCRA in TDSP column.
ONCOR | Big Spring Switch -…- Natural Dam | LN | 138 | 21/11, 21/10 | Grady - Brown 138 kV, Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV | Big Spring West - Stanton East 138 kV | RT | Planned | Oncor | Change contingency from "Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV" to "DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses" due to completion of TPIT project 66530 (Add Consavvy 345/138 kV Switch).
AEP, ONCOR | Bowman Switch - Riley (34570) | LN | 345 | 21/3 | DCKT Clear Crossing-Coulomb & Clear Crossing-Smoky Hill 345 kV | Fisher Road Switch - Riley 345 kV | RT | Planned | Oncor | Change contingency from ‘DCKT Clear Crossing-Coulomb & Clear Crossing-Smoky Hill 345 kV’ to 'DCKT Clear Crossing-Coulomb & Clear Crossing-Pendulo 345 kV'
ONCOR, ETT | Bowman Switch -…- Riley (34560) | LN | 345 | 21/3 | DCKT Clear Crossing-Coulomb & Clear Crossing-Smoky Hill 345 kV | Fisher Road Switch - Riley 345 kV | RT | Planned | Oncor | Change contingency from ‘DCKT Clear Crossing-Coulomb & Clear Crossing-Smoky Hill 345 kV’ to 'DCKT Clear Crossing-Coulomb & Clear Crossing-Pendulo 345 kV'
ONCOR | Brown Switch - Killeen Switch | LN | 345 | 21/6, 20/12, 22/9, 22/12 | Comanche Sw (Oncor)-Comanche Peak 345 kV, DCKT Bighil-Kendall 345kV | Comanche Tap - Comanche Switch (oncor) 138 kV, Yellow Jacket - Treadwell 138 kV | RT | Planned, Forced | Oncor | Change MTE from 'Brown Switch - Killeen Switch' to 'Brown Switch -…- Killeen Switch' due to tapping of Russell Gap Switch. Overloaded element (Yellow Jacket - Treadwell 138 kV) owned by AEP, AEP to provide comments as necessary.
ONCOR | Buckhorn Switch- Killeen Switch (35095) | LN | 345 | 22/9 | Comanche Switch (Oncor) to Comanche Peak SES 345 kV, DCKT Bighil-Kendal 345 kV | Comanche Tap - Comanche Switch (Oncor) 138 kV, Yellow Jacket - Treadwell 138 kV | RT | Forced | Oncor | Change MTE from 'Buckhorn Switch- Killeen Switch (35095)' to 'Russell Gap Switch to Killeen Switch (35091)' Overloaded element (Yellow Jacket - Treadwell 138 kV) owned by AEP, AEP to provide comments as necessary.
ONCOR | Cedar Hill Switch - Courtland | LN | 345 | 19/10, 18/9, 18/5 | DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV, DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV | Britton Road - Venus Switch 345 kV (530_C), Cedar Hill Switch - Fish Crek Switch (3180) 138 kV | RT | Planned, Forced | Oncor | Remove Britton Road - Venus Switch 345 kV (530_C) overload element and its associated contingency DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV as the overload element Britton Road - Venus Switch 345 kV (530_C) was upgraded as a part of TPIT project 6273 "Upgrade existing Venus - Webb/Cedar Hill Sw. Sta. 345 kV Double Ckt Line" (ISD - 12/12/2022)
AEP, ONCOR | Clear Crossing - Willow Creek Switch | LN | 345 | 21/11 | DBCKT Edith Clarke - Riley 345 kV, Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Long Creek 345 kV, Abilene Mulberry Creek - Bluff Creek 345 kV | RT | Planned | Oncor | Change MTE from 'Clear Crossing - Willow Creek Switch' to 'Clear Crossing - ... - Willow Creek Switch' due to tapping of Thomas Price Switch. Overloaded element (Abilene Mulberry Creek - Bluff Creek 345 kV) owned by AEP, AEP to provide comments as necessary.
ONCOR | Comanche Peak Ses - Comanche Switch | LN | 345 | 22/4, 21/4, 18/11 | DCKT Brown Switch - Buckhorn Switch & Killen Switch 345 kV | Comanche Tap - Comanche Switch 138 kV | RT | Planned, Forced | Oncor | Change contingency from 'DCKT Brown Switch - Buckhorn Switch & Killen Switch 345 kV' to 'DCKT Killeen Switch - Buckhorn Switch & Russell Gap Switch 345 kV'
ONCOR,WETR | Dermott Switch - Mhos (T-301) | LN | 345 | 22/5, 22/9, 22/10 | DCKT Dermott Switch -Scurry County South Switch 345 kV, Double Mountain Switch - Fiddlewood Switch 345 kV, Blackwater Draw Switch - Double Mountain Switch 345 kV | Holly Substation - Dunbar Substation 115 kV, Knapp - Scurry Chevron 138 kV, MacKenzie Substation - Northeastern Substation 115 kV | RT | Forced | Oncor | Remove overload element "Knapp - Scurry Chevron 138 kV" and associated contingency "DCKT Dermott Switch -Scurry County South Switch 345 kV" as this MTE is reducing the flow on contraint as per LODF analysis. Overloaded element (Holly Substation - Dunbar Substation 115 kV and MacKenzie Substation - Northeastern Substation 115 kV) owned by City of Lubbock, City of Lubbock to provide comments as necessary.
ONCOR,WETR | Dermott Switch - Mhos (T-302) | LN | 345 | 22/5, 22/9, 22/10 | DCKT Dermott Switch -Scurry County South Switch 345 kV, Double Mountain Switch - Fiddlewood Switch 345 kV, Blackwater Draw Switch - Double Mountain Switch 345 kV | Holly Substation - Dunbar Substation 115 kV, Knapp - Scurry Chevron 138 kV, MacKenzie Substation - Northeastern Substation 115 kV | RT | Forced | Oncor | Remove overload element "Knapp - Scurry Chevron 138 kV" and associated contingency "DCKT Dermott Switch -Scurry County South Switch 345 kV" as this MTE is reducing the flow on contraint as per LODF analysis. Overloaded element (Holly Substation - Dunbar Substation 115 kV and MacKenzie Substation - Northeastern Substation 115 kV) owned by City of Lubbock, City of Lubbock to provide comments as necessary.
ONCOR, WETR | Dermott Switch - Wett_Cottonwood (T-301) | LN | 345 | 22/4, 21/12 | Blackwater Draw Switch - Double Mountain Switch 345 kV | MacKenzie Substation - Northeast Substation 115 kV | RT | Planned | Oncor | Overloaded element "MacKenzie Substation - Northeastern Substation 115 kV" owned by City of Lubbock, City of Lubbock to provide comments as necessary.
ONCOR, WETR | Dermott Switch - Wett_Cottonwood (T-302) | LN | 345 | 22/4, 21/12 | Blackwater Draw Switch - Double Mountain Switch 345 kV | MacKenzie Substation - Northeast Substation 115 kV | RT | Planned | Oncor | Overloaded element "MacKenzie Substation - Northeastern Substation 115 kV" owned by City of Lubbock, City of Lubbock to provide comments as necessary.
ONCOR | Grady -...- Brown-Buzzard Draw Switch-...-Vealmoor | LN | 138 | 22/4, 22/3, 21/6, 21/5 | Big Spring Switch -…- Natural Dam 138 kV, Scurry County South Switch - Wett_Long_draw 345 kV & Wett_Faraday - Wett_Long_Draw 345 kV, Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV, Wett_Grelton - Wett_Long_Draw 345 kV, Odessa EHV Switch - Wett_Grelton 345 kV | Big Spring West - Stanton East 138 kV, Luther - Vealmoor 138 kV, Falcon Seaboard - Morgan Creek Ses 345 kV | RT | Planned | Oncor | Change contingency from "Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV" to "DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses" due to completion of TPIT project 66530 (Add Consavvy 345/138 kV Switch).
ONCOR | Graham SES - Tonkawa Switch | LN | 345 | 21/11 | Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Bluff Creek 345 kV | RT | Planned | Oncor | Overloaded element (Abilene Mulberry Creek - Bluff Creek 345 kV) owned by AEP, AEP to provide comments as necessary.
BPUB,ONCOR | Loma Alta Substation - Stillman | LN | 138 | 23/3 | Millitary Highway Aep - Villa Cavazos 138 kV, DCKT La Palma - Villa Cavazos 138 kV & Rangerville 69 kV | Titan_ Substation - Scarbi Carbide 138 kV | RT | Forced | Oncor | Overload element "Titan_ Substation - Scarbi Carbide 138 kV" is owned by AEP, AEP to provide comments as necessary.
ONCOR | Mitchell Bend Switch - Rocky Creek | LN | 345 | 19/11, 19/10, 22/12 | DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV, DCKT Timberview Switch - Comanche Peak SES - Carmichael Bend Switch 345 kV | Carmichael Bend Switch - Mitchell Bend Switch 345 kV, Benbrook SW - Sycamore Creek 345 kV | RT | Planned, Forced | Oncor | Change contingency from "DCKT Timberview Switch - Comanche Peak SES - Carmichael Bend Switch 345 kV" to "DCKT Timberview Switch - Comanche Peak SES & Carmichael Bend Switch 345 kV".
ONCOR, WETR | Odessa EHV Switch - Wett_Grelton | LN | 345 | 22/4, 22/3 | Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV, Scurry County South Switch - Wett_Long_draw 345 kV & Wett_Faraday - Wett_Long_Draw 345 kV, DCKT Scurry County South Switch - Tonkawa Switch 345 kV | Gail Sub - Willow Valley Switch 138 kV, Dewey Lake Tap - Polecat Creek Switch 138 kV, Luther - Vealmoor 138 kV, Kocht Tap - Vealmoor 138 kV | RT | Planned | Oncor | Change contingency from "Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV" to "DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses" due to completion of TPIT project 66530 (Add Consavvy 345/138 kV Switch).
ONCOR | Paris Switch - Valley Ses | LN | 345 | 22/11 | Woodward Switch - Monitcello Ses 345 kV | Commerce Switch - Commerce 138 kV, Paris Switch AXFMR1H 345/138 kV | RT | Forced | Oncor | Remove overload element "Commerce Switch - Commerce 138 kV" as MTE has minimum impcat on it as per LODF analysis and this MTE is not the only contributor, the congestion experienced in Nov of 2022 is due to multiple simultaneous outages in the area: * COMMERCE SWITCH - ENLOE POI (875_F) (ONC00492910 - 11/03/2022 - 11/14/2022) * DELTA SUB SWT 14943 - ENLOE TAP PS1 (871_C) (ONC00492916 - 11/03/2022 - 11/14/2022) * ALLENS CREEK POI SWT 17848/(N.O.)17850 - BROOKSTON TAP SWT 6136 (1530_E) (ONC00544677 - 11/04/2022 - 11/11/2022) * PARIS SWITCH SWT 8642 - VALLEY SOUTH SWT 8417 (403_A) (ONC00544647 - 11/04/2022 - 11/21/2022)
ONCOR | Paris Switch - Valley South | LN | 345 | 22/11 | Woodward Switch - Monitcello Ses 345 kV | Commerce Switch - Commerce 138 kV, Paris Switch AXFMR1H 345/138 kV | RT | Forced | Oncor | Remove overload element "Commerce Switch - Commerce 138 kV" as MTE has minimum impcat on it as per LODF analysis and this MTE is not the only contributor, the congestion experienced in Nov of 2022 is due to multiple simultaneous outages in the area: * COMMERCE SWITCH - ENLOE POI (875_F) (ONC00492910 - 11/03/2022 - 11/14/2022) * DELTA SUB SWT 14943 - ENLOE TAP PS1 (871_C) (ONC00492916 - 11/03/2022 - 11/14/2022) * ALLENS CREEK POI SWT 17848/(N.O.)17850 - BROOKSTON TAP SWT 6136 (1530_E) (ONC00544677 - 11/04/2022 - 11/11/2022) * PARIS SWITCH SWT 8627 - VALLEY SES BKR 4150 (391_A) (ONC00544646 - 11/04/2022 - 11/21/2022)
ONCOR, WETR | Scurry County South Switch - Wett_Long_Draw | LN | 345 | 22/4, 22/5 | Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV, Odessa EHV Switch - Wett_Grelton 345 kV, Wett_Grelton - Wett_Long_Draw 345 kV | Falcon Seaboard - Morgan Creek Ses 345 kV, Luther - Vealmoor 138 kV | RT | Planned | Oncor | Change contingency from "Longshore Switch - Midessa South Sw 345 kV & Morgan Creek Ses-…-Quail Switch 345 kV" to "DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses" due to completion of TPIT project 66530 (Add Consavvy 345/138 kV Switch). Remove overload element " Luther - Vealmoor 138 kV" and associated contingency "Odessa EHV Switch - Wett_Grelton 345 kV, Wett_Grelton - Wett_Long_Draw 345 kV" as MTE is reducing the flow on the constraint.
ONCOR | Tri Corner - Watermill Switch (215) | LN | 345 | 20/2, 19/10, 19/9 | DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV, DCKT Centerville Road Switch to Parkdale Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Britton Road - Venus Switch 345 kV (530_C), Prairie Creek - Scyene Road 138 kV, Kleberg Tap - Seagoville 138 kV | RT | Planned | Oncor | Remove Britton Road - Venus Switch 345 kV (530_C) overload element and its associated contingency DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV as the overload element Britton Road - Venus Switch 345 kV (530_C) was upgraded as a part of TPIT project 6273 "Upgrade existing Venus - Webb/Cedar Hill Sw. Sta. 345 kV Double Ckt Line" (ISD - 12/12/2022)
ONCOR | Tri Corner - Watermill Switch (515) | LN | 345 | 20/2, 19/10, 19/9 | DCKT Parkdale Switch - Centerville Road Switch 138 kV,DCKT Big Onion - Watermill Switch 345 kV & Elrod Switch - Watermill Switch 345 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Prairie Creek - Scyene Road 138 kV, Britton Road - Venus Switch 345 kV (530_C), Kleberg Tap - Seagoville 138 kV | RT | Planned | Oncor | Remove Britton Road - Venus Switch 345 kV (530_C) overload element and its associated contingency DCKT Watermill Switch - Big Onion & Elrod Switch 345 kV as the overload element Britton Road - Venus Switch 345 kV (530_C) was upgraded as a part of TPIT project 6273 "Upgrade existing Venus - Webb/Cedar Hill Sw. Sta. 345 kV Double Ckt Line" (ISD - 12/12/2022)