## Slide 1
Item 7.1.2.3: ERCOT Comments on NPRR1186
Dan Woodfin
Vice President, System Operations
Board of Directors Meeting
ERCOT Public
August 31, 2023

## Slide 2: Overview
Key Takeaway: This presentation will describe the reliability risks that ERCOT foresees with increasing growth in ESRs and the proposed approach to mitigate the risk until Real-Time Co-optimization with Battery Single Model (RTC+B) is implemented.
Summary of changes in NPRR1186
  Updates inputs to Reliability Unit Commitment (RUC) studies so that RUC considers an Energy Storage Resource’s (ESR’s) State Of Charge (SOC);
  Clarifies SOC requirements when ESRs are providing AS and specifies compliance requirements for SOC; and
  Updates inputs to Security Constrained Economic Dispatch (SCED) such that ESR Base Points preserve the SOC needed to fulfill the ESR’s AS obligation in the remainder of the Operating Hour.
Purpose of Presentation
  Provide rationale for NPRR1186
Voting Items / Requests
  Remand to TAC with instructions to provide recommendation on one limited issue which Eolian has raised and ERCOT agrees should be addressed; otherwise, ERCOT requests approval of the TAC-recommended version of NPRR1186.

## Slide 3: NPRR1186 Introduction
Installed capacity of batteries (ESRs) and their penetration in provision of Ancillary Services (AS) is growing rapidly.
  Every hour, ESRs are already providing more than 60% of ERCOT’s Regulation Up (Reg Up) and Responsive Reserve Service (RRS) Ancillary Services (AS).
ERCOT’s current systems, studies and processes including Day Ahead Market (DAM), RUC and SCED are not designed to account for Resources with limited state of charge (SOC).
  RUC may incorrectly assume an ESR’s capacity as being available in future hours. This could result in ERCOT failing to commit sufficient generation.
  ESRs may offer to provide AS for several consecutive hours and DAM may clear them for those hours. If an extended deployment situation occurs, the ESR/QSE may not be able to fulfill its AS obligation.
  SCED Base Points may deplete an ESR’s SOC that should be preserved for its AS obligation in the remainder of the hour. This could result in ESRs not being able to provide obligated reserves if deployed.
Key Takeaway: ERCOT’s current tools/studies do not account for limited duration of Resources. With growing reliance on ESRs, the operational reliability risks will increase significantly without improvements in ERCOT capabilities related to ESRs.

## Slide 4: Timing
RTC+B (with additional Market Rules changes to allow SOC accounting) is expected to mitigate these problems in a more efficient manner but will not be in place until late 2026.
NPRR1186 was proposed to reduce reliability risks associated with supporting a growing fleet of short-duration ESRs in the interim period until RTC+B is implemented.
  The tool changes associated with NPRR1186 are planned to be in place in Q2 2024.
  RTC+B cannot begin until development resources associated with this interim solution have completed NPRR1186-related work.
  If NPRR1186 is implemented as planned, the RTC+B schedule can be maintained.
The changes proposed in NPRR1186 have been strategically designed so that these can be completed in a small window of project implementation availability and not slow down RTC+B development.
Key Takeaway: NPRR1186 was designed to mitigate the reliability risks from ERCOT systems not recognizing the SOC of limited duration resources until the RTC+B project is completed and to be able to be implemented in the limited window where development resources are available.

## Slide 5: ESR Dispatch in RUC
RUC analysis may count on capacity from ESRs to serve load in several consecutive hours because RUC does not currently consider SOC.
However, often the RUC dispatched ESRs have insufficient SOC to serve the energy that RUC is expecting those ESRs to inject in the future hours (red points on chart to right).
NPRR1186 will better account for this limited duration SOC in RUC analyses.
April 2023
x = y
Key Takeaway: With increasing dependence on ESR capacity to serve load and reserves, NPRR1186 is needed to better account for limited SOC in RUC analyses, so that it is not counted on for more energy than it has the SOC to provide.

## Slide 6: Importance of Defining Performance Requirements for AS Products
ERCOT procures AS on an hourly basis through the DAM. In any hour, to provide the obligated AS, a Resource must have sufficient capability to provide a full deployment for the duration of the service.
Ancillary Services like RRS, ERCOT Contingency Reserve Service (ECRS) and Non-Spinning Reserve Service (Non-Spin) can be deployed for several consecutive hours. It is essential that at the start of every Operating Hour, an ESR that is being used to provide a particular AS must position its SOC to be able to meet the duration requirements of the AS it is providing.
QSEs can manage their portfolios to provide the service by moving the designation of which Resource(s) are being used to provide each AS.
  Ultimately, ERCOT needs some type of measurement to determine whether the ESRs designated to provide AS have the capability to provide the service that ERCOT procured.
  NPRR1186 is intended to provide the measurement that will be used by ERCOT to assess whether the designated ESRs maintained the capability to provide the service that ERCOT procured.
Key Takeaway: NPRR1186 does not restrict the QSE's ability to manage its portfolio but defines how ERCOT will assess whether the QSE designated appropriate ESRs to provide the Ancillary Services that ERCOT procured from the QSE.

## Slide 7: Consistent Insufficient SOC for AS
In real time, many ESRs that are designated as providing AS have been consistently short in maintaining sufficient SOC for the AS obligation that is being provided, based on the current business practice metrics for assessing sufficiency.
NPRR1186 clarifies the metrics to be used in assessing whether the ESRs providing AS in real time are maintaining sufficient SOC to provide the service they have sold to ERCOT.
  NPRR1186 relaxes the current metrics to allow less energy to have to be maintained to provide the AS, as compared to the current practice.
Key Takeaway: 50% of the time at the beginning of peak hours, the total shortfall in SOC preserved by ESRs to meet their AS obligation being carried in real time exceeds 500 MWh.
During first 15 min of every Operating Hour between June 1 and Aug 24, 2023, an average of up to 34% of the ESRs providing AS were short in meeting SOC requirement by 1 MWhh or more. Median hourly total shortfall was as high as 6.9% of the SOC needed to meet their total hourly AS obligation – which was over 500 MWhh in peak hours.

## Slide 8: SOC Requirement for ECRS and Non-Spin
Per Protocol Section 3.17, Resources providing ECRS and Non-Spin, must be capable of sustaining full response at that MW level for 2 hours and 4 hours, respectively. For example,
  When providing 50 MW of ECRS in real time, an ESR is required to have the capability to sustain a full response at 50 MW for 2 hours.
  The 2-hour duration requirement does not mean that
    every time an ESR provides ECRS, it must provide it for two consecutive hours. Or
    an ESR that has a non-zero ECRS Responsibility for only 1 hour, if a deployment occurs, must provide a response for ECRS in the next hour where it doesn’t have an ECRS obligation.
Recognizing that a lower amount of energy is needed to fulfill a deployment as the hour progresses, NPRR1186 sets the minimum SOC requirement for all AS to reduce as a function of time.
  However, based on the example above, if the ESR is also being used to provide 50 MW of ECRS in the next hour, its minimum SOC requirement goes back up to 100 MWh at the beginning of that next hour (solid line in graph above). Note that the QSE is able to designate another ESR with sufficient SOC or other Resource to provide this 50 MW ECRS responsibility.
Key Takeaway: NPRR1186 does not force ESRs to charge at the end of every hour. It specifies the minimum amount of SOC needed at every point in the hour if an ESR intends to provide AS. The risk of getting deployed for several hours in a row must be taken into account when an ESR plans to provide AS in consecutive hours.

## Slide 9: SOC for ECRS and Non-Spin during Scarcity Deployment
As described, NPRR1186 provides incentives for ESRs to manage their portfolios to maintain sufficient SOC to meet the requirements of the AS products they have chosen to offer and are selected to provide.
Eolian has raised one issue (the “scarcity deployment issue”), which deserves further consideration on a limited basis:
  During scarcity conditions, when all other Resources are being used to serve load, it would be in the best interest of reliability to use the SOC that an ESR would otherwise be required to maintain for ECRS and Non-Spin per the 2 and 4 hour duration requirements, respectively.
  ERCOT is open to modifying the NPRR1186 compliance obligation solely during these very limited conditions.
If the Board agrees that the NPRR should be remanded to TAC for further consideration of this issue, it would be important to tightly limit any further discussion to this one issue and to solutions that fit into the limited development window because of the potential to delay the RTC+B project.

## Slide 10: Summary
ERCOT tools do not adequately account for the limited duration of ESR deployment capabilities.
QSEs are not adequately managing their portfolios to preserve sufficient SOC on ESRs they are designating to meet their AS Obligations in real time.
With increasing numbers of ESRs providing Ancillary Services, this is an increasing reliability risk.
RTC+B (with SOC accounting) is expected to mitigate many of these reliability concerns related to provision of AS from ESRs, but this will not be in place for over 3 years.
NPRR1186 is essential to reduce these reliability risks in the interim.
To avoid impacting RTC+B development timeline, the changes in NPRR1186 have been strategically designed so that these can be completed in a small window of resource availability.
Among other things, NPRR1186 clarifies the metrics that ERCOT will use to assess whether a QSE that is providing AS with ESRs in real time is meeting its obligations for the products it has offered and been selected to provide.
Eolian has identified one limited issue that ERCOT agrees deserves more consideration relating to the deployment of energy from ESRs providing ECRS and Non-Spin during scarcity conditions. If the Board chooses to remand the NPRR to TAC for further language changes, any further debate should be tightly limited to that one issue so as to avoid delays to the RTC+B project.
Key Takeaway: ERCOT requests that the Board remand the NPRR to TAC to address the limited "scarcity deployment issue"; otherwise, ERCOT requests approval of the TAC-recommended version of NPRR1186.

## Slide 11
Questions?

## Slide 12
Appendix

## Slide 13: Shorter Duration ESRs provide AS in several Consecutive Hours
Most ESRs interconnected or planning to interconnect are less than 2-hour batteries.
In reviewing the AS that these ESRs provided in real time between June 1 and Aug 24, 2023,
  98.6% of ESRs with an RRS obligation carried that obligation for more than 4 consecutive hours.
  67.6% of ESRs with an ECRS obligation carried that obligation for more than 4 consecutive hours.
  64.7% of ESRs with a Regulation Up obligation carried that obligation for more than 4 consecutive hours.
ECRS and Non-Spin are Ancillary Services that are utilized to cover risks associated with net load forecast errors that may last for multiple hours.
  Non-Spin may also be used to cover risks associated with thermal Resource intra-day Forced Outages, which may also last several consecutive hours.
Key Takeaway: With (a) the consistent provision of up AS from short-duration ESRs in several consecutive hours and (b) the lack of appropriate tools to monitor ESRs to support the expected growth in ESRs, the 2- and 4-hour duration requirements for ECRS and Non-Spin continue to be essential.

## Slide 14: Example SOC shortfall results in inability to follow dispatch
Example of an ESR that was providing up AS on Aug 17 between 1800 and 2000. This ESR at start of HE20 did not have sufficient SOC for the total up AS (Reg Up & RRS) requirement that it was providing and was eventually unable to follow its total dispatch instruction.
Key Takeaway: Today’s status quo is not ensuring ESRs that carry AS maintain sufficient SOC to fulfill the ESR’s remaining obligation in the hour.
*In this image Yellow shade signifies an active ECRS deployment and gray shade signifies an active RRS deployment.
Notes: SOC and SOC Req