## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS
Vice Chair: Vacant
ROS
September 7th, 2023

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of July
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 8/16/2023
  NOGRR255, High Resolution Data Requirements
  DRRS Design Ideas, Workshop Review
  Review ROS Assignments
  ERCOT Reports
  TRE Report

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in July
  7/6/2023 21:05:10
    Loss of 751 MW of Generation
    Interconnection Frequency Response: 1192 MW/0.1 Hz
    91 Resources were evaluated. These includes,
      27 Generation Resources
      3 Controllable Load Resources
      61 Energy Storage Resources
    7 of 91 Evaluated Resources had less than 75% of their expected Initial Primary Frequency Response.
    9 of 91 Evaluated Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 463 MW/0.1 Hz
IMFR Performance currently
1298.68 MW/0.1HZ

## Slide 7
Questions?

## Slide 8: Frequency Control Report
July 2023

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency
Notes: 14.78 mHz on avg for July 2023

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy
Notes: 47,640,022 MWh

## Slide 14: ERCOT Total Energy from Wind Generation
Notes:   8,956,722 MWH

## Slide 15: ERCOT % Energy from Wind Generation
Notes: 18.80%
of total energy was provided by wind generation

## Slide 16: ERCOT Total Energy from Solar Generation
Notes: 3,907,818 MWh

## Slide 17: ERCOT % Energy from Solar Generation
Notes: 8.20%

## Slide 18: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia =255,073 MW*s on 7/7/2023
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 304,815 MW*s
Min: 255,073 MW*s on July 7th
Max: 344,239 MW*s on July 23rd

## Slide 19: ERCOT Inertia Trend
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.