| NOGRR Number | 245 | NOGRR Title | Inverter-Based Resource (IBR) Ride-Through Requirements |
| --- | --- | --- | --- |

| Date | July 31, 2023 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Gary Chmiel |
| E-mail Address | Gary.chmiel@ge.com |
| Company | GE Vernova (Onshore Wind) |
| Phone Number | 518-852-1150 |
| Cell Number |  |
| Market Segment | Not applicable |

Comments

GE Vernova, our portfolio of energy businesses, appreciates the opportunity to submit the following comments to ERCOT on Nodal Operating Guide Revision Request (NOGRR) 245, Inverter-Based Resource (IBR) Ride-Through Requirements.  As the nation’s leading energy and technology innovation company, GE Vernova is committed to supporting ERCOT’s efforts on ensuring and maintaining reliability.

GE Vernova has pioneered technologies that have spurred world‐transforming changes and improved the lives of billions.  We are a world leader in power generation, transmission, and distribution energy solutions.  Our technology produces one‐third of the world’s electricity, and our power generation equipment is deployed in more than 140 countries.  In addition, GE Vernova equips 90% of transmission utilities worldwide, and 40% of the world’s electricity flows via our software.  GE Vernova is actively involved in all segments of the energy sector and has long manufactured products designed to meet stringent government standards, while meeting customer requirements for efficient, reliable, resilient, and affordable energy.

GE Vernova is unique among U.S. companies in designing and manufacturing industry‐leading wind, gas, steam, and hydro‐powered turbines, nuclear power generation technologies, power quality equipment, and hybrid power solutions, while incorporating the latest digital innovation.  GE Vernova leads grid modernization and resilience efforts with a defense‐in‐depth approach to the design, development, deployment, and service of the world’s most critical power systems.  We service the products we sell, and we offer equipment upgrades that increase our products’ efficiency and availability.  Finally, through our Advanced Research Center (“ARC”), our scientists and engineers are focused on developing and improving breakthrough technologies to accelerate the energy transition including hydrogen, carbon capture and sequestration, and small modular reactors.  We have always embraced our diverse portfolio of energy products and solutions across GE Vernova.  In 2024, as we launch GE Vernova as a new, independent company, we will focus entirely on succeeding in the energy transition, will be represented by approximately 70,000 employees worldwide, and will use the combination of our technologies and expertise to ensure a reliable, affordable, sustainable and secure energy system.

Overall, our concerns with NOGRR245 are the risks associated with the aggressive timelines being proposed.  The following comments detail these concerns, along with two technical comments to the NOGRR language.

Note that all comments related to compatibility and timing are estimated only at this time, GE cannot be certain all depictions below are accurate without analysis and confirmation of equipment and parameters on site.  GE also cannot make any claims of compliance for any plant as most requirements are applicable at the Point of Interconnection Bus (POIB), rather than the “Point of Connection” (POC) of each turbine.

Timeline of Capability Report Date:  Compatibility to these performance standards requires design and validation of the power path, auxiliaries, mechanical structure, and drivetrain systems.  Based on the significant analysis required to make final determination of compatibility, including electromechanical requirements, the March 2024 date is not achievable across the GE fleet.

Timing of Delivery:  Per previous comments, GE is not able to comply with the timing proposed. Adding to the significant design and development efforts, simulation, lab and field testing is the readiness of the Institute of Electrical and Electronics Engineers (IEEE) P2800.2 - Recommended Practice for Test and Verification Procedures for Inverter-based Resources (IBRs) Interconnecting with Bulk Power Systems (“IEEE P2800.2 Recommended Practice”) that will define compliance to the 2800 -2022 – IEEE Standard for Interconnection and Interoperability of Inverter-Based Resources (IBRs) Interconnecting with Associated Transmission Electric Power Systems (“IEEE 2800-2022 standard”).  GE urges reconsideration with the following in mind:

- For new installations: GE is prioritizing the compatibility of the Sierra and Cypress platforms to meet preferred ERCOT and IEEE 2800-2022 standard requirements of paragraph (1) of Section 2.6.2.1, Frequency Ride-Through Requirements for Transmission -Connected Inverter-Based Resources (IBRs) and Section 2.9.1.1, Preferred Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs), with the proposed exceptions as given in items below.  However, these efforts will not be completed to support all project timelines with an Standard Generation Interconnection Agreement (SGIA) executed after June 1, 2023.  GE proposes a tiered approach such that new units are compatible with only the single dip IEEE 2800-2022 standard frequency and voltage ride through curves at the time of commissioning, and the remainder of IEEE 2800-2022 standard compatibility would follow at a later date.

- For legacy 1.x and 2.x ESS units, GE expects that these platforms can be made compatible with the single dip current voltage ride through capabilities of Table A in Section 2.9.1.2, Legacy Voltage Ride-Through Requirements for Transmission-Connected Inverted-Based Resources (IBRs), and the preferred frequency ride through capabilities of paragraph (1) of Section 2.6.2.1, with limited modifications, and earlier than the specificity requirements.  Developing an upgrade solution for compatibility with the NOGRR245 specificity requirements for all configurations will not be completed until after the 2027 requirement deadline.  Software and hardware upgrades are expected to be required.

- For legacy non-ESS units, it is not anticipated that these can be made compatible with the current ride-through curves and the NOGRR245 specificity by providing minor modifications.  Major retrofits would likely be required and will not be available until after the 2027 requirement deadline.

Timing of model provision:  Since the NOGRR requires compatibility for units that have SGIAs executed after June 1, 2023, please clarify when the associated plant models will be required, and if revised models will be incorporated into the study periods that would already be underway.

IEEE 7.2.2.3.5, Table 13 fault responses:  In the proposed NOGRR245 comments, section 7.2.2.3.5 including Table 13 of the IEEE 2800-2022 are now included as part of the voltage ride-through requirements for units with an SGIA executed or a Generator Interconnection or Modification (GIM) initiated after June 1, 2023.  This table requires aggressive, 6-cycle responses with a very tight tolerance band, applied at the POC of each turbine.  GE Wind Turbine Generators  have long been supplied with advanced stabilizing features that help to provide stable operation, particularly in regions with high wind penetration, series capacitors that risk Subsynchronous Control Interactions (SSCIs), or weak grid regions.  Application of this section will require disabling of these features, which will be detrimental to stability for weak grids.  GE recommends that this section 7.2.2.3.5 be listed as an Exception in the NOGRR language that references section 7, which is in paragraph (2)(b) of Section 2.9.1, Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs).

Current Injection Requirements:  Related to paragraph (4) of Section 2.9.1.1 and paragraph (4) of Section 2.9.1.2 on active and reactive response requirements during ride through events, it was communicated by ERCOT and is understood that active current reductions should be limited during fault events as immediate and total reductions may cause undesired frequency shifts on the grid.  However, since reactive current priority is generally most beneficial, some reduction of active current will be required so the unit has additional reactive current available for voltage support.  Rather than requiring delivery of “pre-disturbance active current”, GE suggests that these Sections directly allow for the IBR to maintain automatic voltage control (within its VAR capability) during ride through.  Suggested language would be “…When the POIB voltage is outside the continuous operating voltage range, an IBR may maintain pre-disturbance active current, or gradually reduce active current to allow for voltage support, unless otherwise specified by ERCOT or the interconnecting TSP.  Any reductions in active current to prioritize reactive current shall be relative to the voltage change at the POIB.”

We appreciate the time and attention the ERCOT staff has provided GE Vernova, to date. We welcome the opportunity to continue discussions with ERCOT staff to determine requirements within a feasible timeframe that takes into consideration the level of analysis, design development, certification, and validation for a solution across various product lines.

Revised Cover Page Language

None

Revised Proposed Guide Language

- 2.6.2	Frequency Ride-Through Requirements for Generation Resources and Energy Storage Resources

(1)	Except for Generation Resources and Energy Storage Resources (ESRs) subject to Sections 2.6.2.1, Frequency Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs) or 2.6.2.2, Frequency Ride-Through Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs), if under-frequency relays are installed and activated to trip the Generation Resource or ESR, these relays shall perform such that the automatic removal of individual Generation Resources or ESRs from the ERCOT System meets or exceeds the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Above 59.4 Hz | No automatic tripping (continuous operation) |
| Above 58.4 Hz up to and including 59.4 Hz | Not less than 9 minutes |
| Above 58.0 Hz up to and including 58.4 Hz | Not less than 30 seconds |
| Above 57.5 Hz up to and including 58.0 Hz | Not less than 2 seconds |
| 57.5 Hz or below | No time delay required |

(2)	Except for Generation Resources subject to Sections 2.6.2.1 or 2.6.2.2, if over-frequency relays are installed and activated to trip the Generation Resource or ESR, they shall perform such that the automatic removal of individual Generation Resources or ESRs from the ERCOT System meets or exceeds the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Below 60.6 Hz down to and including 60 Hz | No automatic tripping (continuous operation) |
| Below 61.6 Hz down to and including 60.6 Hz | Not less than 9 minutes |
| Below 61.8 Hz down to and including 61.6 Hz | Not less than 30 seconds |
| 61.8 Hz or above | No time delay required |

(3)	If installed and activated to trip a Generation Resource or ESR, frequency protection schemes shall use filtered quantities or add sufficient time delays to prevent misoperations while providing the desired equipment protection.  Protection schemes shall not trip a Generation Resource or ESR based on an instantaneous frequency measurement.

(4)	This Section shall not affect the Resource Entity’s responsibility to protect Generation Resources or ESRs from damaging operating conditions.  The Resource Entity for a Generation Resource or ESR subject to paragraphs (1) and (2) above that is unable to remain reliably connected to the ERCOT System as set forth in paragraphs (1) and (2), shall provide to ERCOT the reason(s) for that inability, including study results or manufacturer advice.  The limitation description shall include the Generation Resource’s or ESR’s frequency ride-through capability in the format shown in the tables in paragraphs (1) and (2) above.The Resource Entity that owns Generation Resources that are unable to comply shall provide to ERCOT an explanation of the limitations including, but not limited to, study results or manufacturer’s advice.

2.6.2.1 	Frequency Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs)

(1)	All IBRs interconnected to the ERCOT Transmission Grid shall ride through the frequency conditions at the IBR’s Point of Interconnection Bus (POIB) specified in the following table:

| Frequency (f) in (Hz) | Minimum Ride-Through Time (seconds) |
| --- | --- |
| f > 61.8 | May ride-through or trip |
| 61.6 < f ≤ 61.8 | 299 |
| 61.2 < f ≤ 61.6 | 540 |
| 58.8 ≤ f ≤ 61.2 | continuous |
| 58.4 ≤ f < 58.8 | 540 |
| 57.0 ≤ f < 58.4 | 299 |
| f < 57.0 | May ride-through or trip |

(2)	Nothing in paragraph (1) above shall be interpreted to require an IBR to trip for frequency conditions beyond those for which ride-through is required.

(3)	If installed and activated to trip the IBR, all protection systems (including, but not limited to protection for over-/under-frequency, rate-of-change of frequency, anti-islanding, and phase angle jump) shall enable the IBR to ride through frequency conditions beyond those defined in paragraph (1) above to the maximum extent possible.  An IBR shall ride through frequency excursions during which ride-through is required and the absolute rate-of-change of frequency magnitude does not exceed 5.0 Hz/second.  The rate-of-change of frequency shall be considered the average rate of change of frequency over a period of at least 0.1 seconds unless ERCOT or the interconnecting Transmission Service Provider (TSP) specifies otherwise.

(4)	An IBR shall inject electric current during all periods requiring ride-through.

(5)	IBR plant controls or inverter controls shall not disconnect the IBR from the ERCOT System or reduce IBR output during frequency conditions where ride-through is required unless necessary for providing appropriate frequency response or prevent equipment damage.  If an IBR requires any setting that would prevent it from riding through the frequency conditions as required in paragraph (1) above, the IBR operation may be restricted as set forth in paragraph (8) below.

(6)	An IBR with a Standard Generation Interconnection Agreement (SGIA) executed prior to June 1, 2023, must comply with paragraphs (1) through (5) above as soon as practicable but no later than December 31, 2025.  Such IBRs shall comply with the frequency ride-through requirements specified in Section 2.6.2.1.1, Temporary Frequency Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs). until the IBR implements changes to comply with paragraphs (1) through (5).

The Resource Entity or Interconnecting Entity (IE) for an IBR with an SGIA executed prior to June 1, 2023 that cannot comply with paragraphs (1) through (5) above shall, by March 1, 2024, submit to ERCOT a report and supporting documentation containing the following:

(a)	The current and potential future IBR frequency ride-through capability (including any associated adjustments to improve frequency ride-through capability) in a format similar to the table in paragraph (1) above;

(b)	The proposed modifications to maximize the IBR frequency ride-through capability and allow the IBR to comply with the frequency ride-through requirements in paragraphs (1) through (5) above;

(c)	A schedule for implementing those modifications as soon as practicable but no later than December 31, 2025; and

(d)	Any limitations on the IBR’s frequency ride-through capability making it technically infeasible to meet the requirements in paragraphs (1) through (5) above.

Based on the information provided by the Resource Entity or IE, if ERCOT determines in its sole and reasonable discretion an IBR cannot comply with all applicable frequency ride-through requirements, the IBR operation may be restricted as set forth in paragraph (8) below. 4.

[NOGRR245: Replace paragraph (6) above with the following on January 1, 2026.] (6) The Resource Entity or Interconnecting Entity (IE) for an IBR with a Standard Generation Interconnection Agreement (SGIA) executed prior to June 1, 2023 that cannot comply with Section 2.6.2.1 paragraphs (1) through (5) shall, by March 1, 2024, submit to ERCOT a report and supporting documentation containing the following: (a) The current and potential future IBR frequency ride-through capability (including any associated adjustments to improve frequency ride-through capability) in a format similar to the table in paragraph (1) above; (b) The proposed modifications to maximize the IBR frequency ride-through capability and/or allow the IBR to comply with the frequency ride-through requirements in Section 2.6.2.1 paragraphs (1) through (5); (c) A schedule for implementing those modifications as soon as practicable but no later than December 31, 2025; and (d) Any limitations on the IBR’s frequency ride-through capability making it technically infeasible to meet the requirements in Section 2.6.2.1 paragraphs (1) through (5). Based on the information provided by the Resource Entity or Interconnecting Entity, if ERCOT determines in its sole and reasonable discretion that an IBR cannot comply with all applicable frequency ride-through requirements, the IBR operation may be restricted as set forth in paragraph (8) below.

(7)	If an IBR fails to perform in accordance with the applicable frequency ride-through requirements, the IBR operation may be restricted as set forth in paragraph (8) below.  Additionally, the Resource Entity for the IBR shall investigate the event and report to ERCOT the cause of the IBR’s failure.  All impacted TSPs shall provide available information to ERCOT to assist with event analysis.

(8)	Any IBR that cannot comply with the applicable frequency ride-through requirements may be restricted or may not be permitted to operate on the ERCOT System unless ERCOT, in its sole and reasonable discretion, allows it to do so.  Each Qualified Scheduling Entity (QSE) shall, for each IBR not permitted to operate, reflect in its Current Operating Plan (COP) and Real-Time telemetry a Resource Status of OFF, OUT, or EMR in accordance with Protocol Sections 3.9.1, Current Operating Plan (COP) Criteria, and 6.5.5.1, Changes in Resource Status, as appropriate.  If the Resource Entity can implement IBR modifications to resolve the technical limitations or performance failures preventing compliance with applicable frequency ride-through requirements, the Resource Entity shall submit to ERCOT a report and supporting documentation containing the following:

(a)	The current technical limitations and IBR frequency ride-through capability in a format similar to the table in paragraph (1) above;

(b)	The proposed modifications and frequency ride-through capability allowing the IBR to comply with the frequency ride-through requirements in a format similar to the table in paragraph (1) above; and

(c)	A schedule for implementing those modifications.

In its sole and reasonable discretion, ERCOT may accept the proposed modification plan.  Upon completion of the accepted modification plan, ERCOT will remove the restrictions placed on the IBR unless the IBR experiences additional unresolved technical limitations or performance failures.  ERCOT may allow the IBR to operate at reduced output prior to the implementation of an accepted modification plan if the reduced output allows the IBR to comply with the applicable ride-through requirements.

2.6.2.1.1	Temporary Frequency Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs)

(1)	This Section applies only to certain IBRs with an SGIA executed prior to June 1, 2023 in accordance with paragraph (6) of Section 2.6.2.1, Frequency Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs).

(2)	If under-frequency relays are installed and activated to trip the Generation Resource or ESR, the relays shall perform such that the automatic removal of individual Generation Resources or ESRs from the ERCOT System meets or exceeds the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Above 59.4 Hz | No automatic tripping (continuous operation) |
| Above 58.4 Hz up to and including 59.4 Hz | Not less than 9 minutes |
| Above 58.0 Hz up to and including 58.4 Hz | Not less than 30 seconds |
| Above 57.5 Hz up to and including 58.0 Hz | Not less than 2 seconds |
| 57.5 Hz or below | No time delay required |

(3)	If over-frequency relays are installed and activated to trip the Generation Resource or ESR, they shall perform such that the automatic removal of individual Generation Resources or ESRs from the ERCOT System meets or exceeds the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Below 60.6 Hz down to and including 60 Hz | No automatic tripping (continuous operation) |
| Below 61.6 Hz down to and including 60.6 Hz | Not less than 9 minutes |
| Below 61.8 Hz down to and including 61.6 Hz | Not less than 30 seconds |
| 61.8 Hz or above | No time delay required |

(4)	This Section shall not affect the Resource Entity’s responsibility to protect Generation Resources or ESRs from damaging operating conditions.  The Resource Entity for a Generation Resource or ESR subject to paragraphs (2) and (3) above that is unable to remain reliably connected to the ERCOT System as set forth in paragraphs (2) and (3), shall provide to ERCOT the reason(s) for that inability, including study results or manufacturer advice.  The limitation description shall include the Generation Resource’s or ESR’s frequency ride-through capability in the format shown in the tables in paragraphs (2) and (3) above.

[NOGRR245: Delete Section 2.6.2.1.1 above on January 1, 2026.]

2.6.2.2	Frequency Ride-Through Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs)

(1)	For any short-circuit fault or open-phase condition that occurs on the circuit to which the DGR or DESR is connected, the DGR or DESR will cease to energize and trip offline, and this will take priority over the frequency ride-through function.

(2)	DGRs and DESRs must have over-/under-frequency relays set to ride through frequency conditions as specified in the following table:

| Frequency (Hz) | Ride-Through Mode | Minimum Ride-through Time (seconds) |
| --- | --- | --- |
| f > 61.8 | No ride-through requirements |  |
| 61.2 < f ≤ 61.8 | Mandatory Operation | 299 |
| 58.8 ≤ f ≤ 61.2 | Continuous Operation | continuous |
| 57.0 ≤ f < 58.8 | Mandatory Operation | 299 |
| f < 57.0 | No ride-through requirements |  |

(3)	Any Resource Entity with a DGR or DESR utilizing inverter-based generation that achieved Initial Synchronization before April 1, 2020 that is not capable of complying with the requirements of paragraph (2) above may request an exemption from those requirements.  Such a request shall be submitted by November 2, 2020 and shall include documentation that demonstrates the DGR’s or DESR’s frequency ride-through capability to ERCOT’s satisfaction.  If, after reviewing the request and documentation, ERCOT determines the DGR or DESR is not capable of complying with the requirements of paragraph (2), then the DGR or DESR shall be exempt from those requirements, but shall be required to comply with those requirements to the greatest degree possible within its capability, as determined in writing by ERCOT.  Upon replacement or retirement of the inverter, the DGR or DESR shall no longer be exempt and shall at that time be required to comply with the requirements of paragraph (2) or other applicable requirement.

2.9	Voltage Ride-Through Requirements for Generation Resources

(1)	Except for Generation Resources and Energy Storage Resources (ESRs) subject to Sections 2.9.1, Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs), or 2.9.2, Voltage Ride-Through Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs), each Generation Resource or ESR must remain reliably connected to the ERCOT Transmission Grid during the following:

(a)	Generator terminal voltages are within 5% of the rated design voltage and volts per hertz are less than 105% of generator rated design voltage and frequency;

(b)	Generator terminal voltage deviations exceed 5% but are within 10% of the rated design voltage and persist for less than ten seconds;

(c)	Generator volts per hertz conditions are less than 116% of generator rated design voltage and frequency and last for less than 1.5 seconds;

(d)	A transmission system fault (three-phase, single-phase or phase-to-phase), but not a generator bus fault, is cleared by the protection scheme coordinated between the Generation Entity and the Transmission Service Provider (TSP) on any line connected to the generator’s transmission interconnect bus, provided such lines are not connected to induction generators described in paragraph (12) of Protocol Section 3.15, Voltage Support; and

(e)	In the case of a generator bus fault or a primary transmission system relay failure, the generator protective relaying may clear the generator independent of the operation of any transmission protective relaying.

(2)	During operating conditions listed in paragraph (1) above, each Generation Resource and ESR subject to paragraph (1) shall not, during and following a transient voltage disturbance, cease providing real or reactive current except to the extent needed to provide frequency support or aid in voltage recovery.

(3)	Synchronous Generation Resources required to provide Voltage Support Service (VSS) shall have and maintain the following capability:

(a)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least 80% of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so over-excitation protection operates only for failure of the voltage regulator/limiter.

(b)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment malfunction.

(4)	Generation Resources and ESRs shall have protective relaying necessary to protect equipment from abnormal conditions and be consistent with protective relaying criteria described in Section 6.2.6.3.4, Generator Protection and Relay Requirements.

(5)	The voltage ride-through requirements do not apply to faults between the generator terminals and the transmission voltage side of the Main Power Transformer (MPT), or when clearing the fault effectively disconnects the Generation Resource from the ERCOT System.

(6) 	A Generation Resource or ESR may be tripped Off-Line or curtailed after the fault clearing period if part of an approved Remedial Action Scheme (RAS).

(7)	Each Generation Resource and ESR shall provide to ERCOT technical documentation of voltage ride-through capability upon request.

[NOGRR204: Replace Section 2.9 above with the following upon system implementation of NPRR989:] - 2.9 Voltage Ride-Through Requirements for Generation Resources and Energy Storage Resources (1) Except for Generation Resources and Energy Storage Resources (ESRs) subject to Sections 2.9.1, Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs), or 2.9.2, Voltage Ride-Through Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs), each Generation Resource and ESR must remain reliably connected to the ERCOT Transmission Grid during the following: (a) Generator or inverter terminal voltages are within 5% of the rated design voltage and volts per hertz are less than 105% of generator rated design voltage and frequency; (b) Generator or inverter terminal voltage deviations exceed 5% but are within 10% of the rated design voltage and persist for less than ten seconds; (c) Generator or inverter volts per hertz conditions are less than 116% of rated design voltage and frequency and last for less than 1.5 seconds; and (d) A transmission system fault (three-phase, single-phase or phase-to-phase), but not a unit bus fault, is cleared by the protection scheme coordinated between the Resource Entity and the Transmission Service Provider (TSP) on any line connected to the Resource’s Point of Interconnection (POI), provided such lines are not connected to induction generators described in paragraph (12) of Protocol Section 3.15, Voltage Support. (2) In the case of a unit bus fault or a primary transmission system relay failure, the unit protective relaying may clear the unit independent of the operation of any transmission protective relaying. (3) During operating conditions listed in paragraph (1) above, each Generation Resource and ESR subject to paragraph (1) shall not, during and following a transient voltage disturbance, cease providing real or reactive current except to the extent needed to provide frequency support or aid in voltage recovery. Each ESR, if it is consuming active power from the ERCOT System when operating in the charging mode, shall reduce or cease power consumption as necessary to aid in voltage recovery during and following transient voltage disturbances. (4) Synchronous Generation Resources required to provide Voltage Support Service (VSS) shall have and maintain the following capability: (a) Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least 80% of the unit design standard (ANSI C50.13-1989), as follows: Time (seconds) 10 30 60 120 Field Voltage % 208 146 125 112 After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating. Return to normal AC voltage regulation after current reduction shall be automatic. The over-excitation limiter shall be coordinated with the over-excitation protection so over-excitation protection operates only for failure of the voltage regulator/limiter. (b) Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment malfunction. (5) Generation Resources and ESRs shall have protective relaying necessary to protect equipment from abnormal conditions and be consistent with protective relaying criteria described in Section 6.2.6.3.4, Generation Resource and Energy Storage Resource Protection and Relay Requirements. (6) The voltage ride-through requirements do not apply to faults at or behind the POI, when clearing the fault effectively disconnects the Resource from the ERCOT System. (7) A Generation Resource or ESR may be tripped Off-Line or curtailed after the fault clearing period if part of an approved Remedial Action Scheme (RAS). (8) Each Generation Resource and ESR shall provide to ERCOT technical documentation of voltage ride-through capability upon request.

- 2.9.1	Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs)

(1)	All Inverter-Based Resources (IBRs) interconnected to the ERCOT Transmission Grid shall comply with voltage ride-through requirements as follows:

(a)	Section 2.9.1.1, Preferred Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs) shall apply to:

(i)	IBRs with a Standard Generation Interconnection Agreement (SGIA) executed on or after June 1, 2023.

(ii)	IBRs that implement any modification, as described in paragraph (1)(c) of Planning Guide Section 5.2.1, Applicability, for which a Generator Interconnection or Modification (GIM) was initiated on or after June 1, 2023.

(iii)	Certain IBRs after December 31, 2027 in accordance with paragraph (8) of Section 2.9.1.2, Legacy Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs).

(b)	Section 2.9.1.2 shall apply to IBRs not subject to Section 2.9.1.1.

(2) 	IBRs: (i) with an SGIA executed on or (ii) after June 1, 2023 or that implement any modification, as described in paragraph (1)(c) of Planning Guide Section 5.2.1, Applicability, for which a Generator Interconnection or Modification (GIM) was initiated on or after June 1, 2023, shall meet or exceed the capability and performance requirements in the following sections of Institute of Electric Engineers (IEEE) 2800-2022, Standard for Interconnection and Interoperability of Inverter-Based Resources (IBRs) Interconnecting with Associated Transmission Electric Power Systems or any successor IEEE standard, including any intra-standard cross references or definitions, unless otherwise clarified, modified, or exempted in the ERCOT Protocols, these Operating Guides, or Planning Guide:

(a) 	Section 5, Reactive power-voltage control requirements within the continuous operation region;

(b)	Section 7, Response to TS abnormal conditions; and

(c)	Section 9, Protection.

All IBR plant requirements and all IBR unit requirements described in the standard are to be applied at the Point of Interconnection Bus (POIB) and the individual inverter based unit terminal respectively unless otherwise clarified, modified, or exempted in the ERCOT Protocols.

- 2.9.1.1	PreferredVoltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs)

(1)	All IBRs subject to this Section in accordance with paragraph (1) of Section 2.9.1, Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs), shall ride through the root-mean-square voltage conditions in Tables A or B below, as applicable, and the instantaneous phase voltage conditions in Table C below, as measured at the IBR’s Point of Interconnection Bus (POIB):

Table A:  Applicable to Wind-powered Generation Resource (WGR) IBRs

| Root-Mean-Square Voltage (p.u. of nominal) | Minimum Ride-Through Time (seconds) |
| --- | --- |
| V > 1.20 | May ride-through or trip |
| 1.10 < V ≤ 1.20 | 1.0 |
| 0.90 ≤ V ≤ 1.10 | continuous |
| 0.70 ≤ V < 0.90 | 3.0 |
| 0.50 ≤ V < 0.70 | 2.5 |
| 0.25 ≤ V < 0.50 | 1.2 |
| V < 0.25 | 0.16 |

Table B:  Applicable to PhotoVoltaic Generation Resources (PVGR) and ESR IBRs

| Root-Mean-Square Voltage (p.u. of nominal) | Minimum Ride-Through Time (seconds) |
| --- | --- |
| V > 1.20 | May ride-through or trip |
| 1.10 < V ≤ 1.20 | 1.0 |
| 0.90 ≤ V ≤ 1.10 | continuous |
| 0.70 ≤ V < 0.90 | 6.0 |
| 0.50 ≤ V < 0.70 | 3.0 |
| 0.25 ≤ V < 0.50 | 1.2 |
| V < 0.25 | 0.32 |

In the event of multiple excursions, the minimum ride-through time in Tables A or B is a cumulative time over a ten second time window.

Table C

| Instantaneous Phase-to-Phase or Phase-to-Ground Voltage (p.u. of nominal) | Minimum Ride-Through Time (milliseconds) |
| --- | --- |
| V > 1.80 | May ride-through or trip |
| 1.70 < V ≤ 1.80 | 0.2 |
| 1.60 < V ≤ 1.70 | 1.0 |
| 1.40 < V ≤ 1.60 | 3.0 |
| 1.20 < V ≤ 1.40 | 15.0 |

The instantaneous voltages in Table C above are the residual voltages with surge arrestors, if applied.  During the conditions identified in Table C, an IBR should continue injecting current, but need not respond to the sub-cycle transient overvoltage.  If required by equipment limitations, the IBR may operate in current blocking mode when instantaneous voltage exceeds 1.20 p.u. at the POIB.  If the IBR operates in current blocking mode, it shall restart current exchange in less than or equal to five cycles following instantaneous voltage falling below, and remaining below, 1.2 p.u. at the POIB.  In the event of multiple excursions, the minimum ride through time in Table C is a cumulative time over a one minute time window.

(2)	Nothing in paragraph (1) above shall be interpreted to require an IBR to trip for voltage conditions beyond those for which ride-through is required.

(3)	If installed and activated to trip the IBR, all protection systems (including, but not limited to protection for over-/under-voltage, rate-of-change of frequency, anti-islanding, and phase angle jump) shall enable the IBR to ride through voltage conditions beyond those defined in paragraph (1) above to the maximum extent possible.  An IBR shall ride-through any grid disturbance during which ride-through is required and the positive-sequence angle change within a sub-cycle-to-cycle time frame does not exceed 25 electrical degrees.  In addition, the IBR shall ride-through any change in the phase angle of individual phases caused by occurrence and clearance of unbalanced faults, provided the positive-sequence angle change does not exceed the stated criterion.  Positively damped active and reactive current oscillations in the post-disturbance period are acceptable in response to phase angle changes.

(4)	An IBR shall inject electric current during all periods requiring ride-through.  When the POIB voltage is outside the continuous operating voltage range, an IBR may maintain pre-disturbance active current, or gradually reduce active current to allow for voltage support, unless otherwise specified by ERCOT or the interconnecting TSP. currreactAny necestions in active current to prioritize reactive current shall be relativepropohe voltage change at the POIB.  An IBR shall return to its pre-disturbance level of real power injection as soon as possible but no more than one second after POIB voltage recoversing tormal operating range.

(5)	IBR plant controls or inverter controls shall not disconnect the IBR from the ERCOT System or reduce IBR output during voltage conditions where ride-through is required unless necessary to provide appropriate frequency response or prevent equipment damage.  If an IBR requires any setting that would prevent it from riding through a voltage event as required in paragraph (1) above, the IBR operation may be restricted as set forth in paragraph (9) below.

(6) 	If installed and activated to trip the IBR, instantaneous over-current or over-voltage protection systems shall use filtered quantities to prevent misoperation while providing the desired equipment protection.  Any instantaneous over-voltage protection that could disrupt IBR power output shall use a measurement window of at least one cycle of fundamental frequency.

(7)	The IBR shall ride through multiple excursions outside the continuous operation range in Tables A or B in paragraph (1) above as applicable, unless the conditions and situations specified below exist, in which case the IBR may trip to protect equipment from the cumulative effect of successive voltage deviations:

(a)	More than four voltage deviations at the POIB outside the continuous operation zone within any ten second period.

(b)	More than six voltage deviations at the POIB outside the continuous operation zone within any 120 second period.

(c)	More than ten voltage deviations at the POIB outside the continuous operation zone within any 1,800 second period.

(d)	Voltage deviations outside of continuous operation zone following the end of a previous deviation outside of continuous operation zone by less than twenty cycles of system fundamental frequency.

(e)	More than two individual voltage deviations at the POIB below 50% of the nominal voltage (including zero voltage) within any ten second period.

(f)	More than three individual voltage deviations at the POIB below 50% of the nominal voltage (including zero voltage) within any 120 second period.

(g)	Individual wind turbines may trip for consecutive voltage deviations resulting in stimulation of mechanical resonances exceeding equipment limits.

Individual voltage deviations begin when the voltage at the POIB drops below the lower limit of the continuous operation range or exceeds the upper limit of the continuous operation range.  Individual voltage deviations end when the root-mean-square voltage magnitude at the POIB, for the previous one-cycle period of fundamental frequency, returns to the continuous operation region.

(8)	If an IBR fails to perform in accordance with the voltage ride-through requirements of paragraphs (1) through (7) above, the IBR operation may be restricted as set forth in paragraph (9) below.  Additionally, the Resource Entity for the IBR shall investigate the event and report to ERCOT the cause of the IBR failure.  All impacted TSPs shall provide available information to ERCOT to assist with event analysis.

(9)	Any IBR that cannot comply with the voltage ride-through requirements of paragraphs (1) through (7) above, may be restricted or may not be permitted to operate on the ERCOT System unless ERCOT, in its sole and reasonable discretion, allows it to do so.  Each Qualified Scheduling Entity (QSE) shall, for each IBR not permitted to operate, reflect in its Current Operating Plan (COP) and Real-Time telemetry a Resource Status of OFF, OUT, or EMR in accordance with Protocol Sections 3.9.1, Current Operating Plan (COP) Criteria and 6.5.5.1, Changes in Resource Status, as appropriate.  If the Resource Entity can implement IBR modifications to resolve the technical limitations or performance failures preventing compliance with applicable voltage ride-through requirements, the Resource Entity shall submit to ERCOT a report and supporting documentation containing the following:

(a)	The current technical limitations and IBR voltage ride-through capability in a format similar to the tables in paragraph (1) above;

(b)	The proposed modifications and voltage ride-through capability allowing the IBR to comply with the voltage ride-through requirements in a format similar to the tables in paragraph (1) above; and

(c)	A schedule for implementing those modifications.

In its sole and reasonable discretion, ERCOT may accept the proposed modification plan.  Upon completion of the accepted modification plan, ERCOT will remove the restrictions placed on the IBR unless the IBR experiences additional unresolved technical limitations or performance failures.  ERCOT may allow the IBR to operate at reduced output prior to the implementation of an accepted modification plan if the reduced output allows the IBR to comply with the applicable ride-through requirements.

- 2.9.1.2	Legacy Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs)

(1)	All IBRs subject to this Section in accordance with paragraph (1) of Section 2.9.1, Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs), shall ride through the root-mean-square voltage conditions in Table A below as measured at the IBR’s Point of Interconnection Bus (POIB):

Table A

| Root-Mean-Square Voltage (p.u. of nominal) | Minimum Ride-Through Time (seconds) |
| --- | --- |
| V > 1.20 | May ride-through or may trip |
| 1.175 < V ≤ 1.2 | 0.2 |
| 1.15 < V ≤ 1.175 | 0.5 |
| 1.10 < V ≤ 1.15 | 1.0 |
| 0.90 ≤ V ≤ 1.10 | continuous |
| 0.0 < V < 0.90 | (V+0.084375)/0.5625 |
| V = 0.0 | 0.15 |

For voltage between zero and 0.9 pu the minimum ride-through time in Table A above is defined by a straight line mathematical function where the duration is 0.15 seconds at zero voltage and 1.75 seconds at 0.9 pu voltage.  In the event of multiple excursions, the minimum ride-through time in Table A is a cumulative time over ten seconds.

(2)	Nothing in paragraph (1) above shall be interpreted to require an IBR to trip for voltage conditions beyond those for which ride-through is required.

(3)	If installed and activated to trip the IBR, all protection systems (including, but not limited to protection for over-/under-voltage, rate-of-change of frequency, anti-islanding, and phase angle jump) shall enable the IBR to ride through voltage conditions beyond those defined in paragraph (1) above to the maximum extent possible.  An IBR shall ride-through any grid disturbance during which ride-through is required and the positive-sequence angle change within a sub-cycle-to-cycle time frame does not exceed 25 electrical degrees.  In addition, the IBR shall ride-through any change in the phase angle of individual phases caused by occurrence and clearance of unbalanced faults, provided the positive-sequence angle change does not exceed the stated criterion.  Positively damped active and reactive current oscillations in the post-disturbance period are acceptable in response to phase angle changes.

(4)	An IBR shall inject electric current during all periods requiring ride-through.  When the POIB voltage is outside the continuous operating voltage range, an IBR may maintain pre-disturbance active current, or gradually reduce active current to allow for voltage support, unless otherwise specified by ERCOT or the interconnecting TSP.  Any reductions in active current to prioritize reactive current shall be relative to the voltage change at the POIB.  An IBR shall return to its pre-disturbance level of real power injection as soon as possible but no more than one second after POIB voltage recovers to normal operating range.

(5)	IBR plant controls or inverter controls shall not disconnect the IBR from the ERCOT System or reduce IBR output during voltage conditions where ride-through is required unless necessary for providing appropriate frequency response, or to prevent equipment damage.  If an IBR requires any setting that would prevent it from riding through voltage conditions as required in paragraph (1) above, the IBR operation may be restricted as set forth in paragraph (10) below.

(6)	If installed and activated to trip the IBR, instantaneous over-current or over-voltage protection systems shall use filtered quantities to prevent misoperation while providing the desired equipment protection.  Any instantaneous over-voltage protection that could disrupt IBR power output shall use a measurement period of at least one cycle (of fundamental frequency).

(7)	The IBR shall ride through multiple excursions outside the continuous operation range in Table A in paragraph (1) above, unless the conditions and situations specified below exist, in which case the IBR may trip to protect equipment from the cumulative effect of successive voltage deviations:

(a)	More than four voltage deviations at the POIB outside the continuous operation zone within any ten second period.

(b)	More than six voltage deviations at the POIB outside the continuous operation zone within any 120 second period.

(c)	More than ten voltage deviations at the POIB outside the continuous operation zone within any 1,800 second period.

(d)	Voltage deviations outside of continuous operation zone following the end of a previous deviation outside of continuous operation zone by less than twenty cycles of system fundamental frequency.

(e)	More than two individual voltage deviations at the POIB below 50% of the nominal voltage (including zero voltage) within any ten second period.

(f)	More than three individual voltage deviations at the POIB below 50% of the nominal voltage (including zero voltage) within any 120 second period.

(g)	Individual wind turbines may trip for consecutive voltage deviations resulting in stimulation of mechanical resonances exceeding equipment limits.

Individual voltage deviations begin when the voltage at the POIB drops below the lower limit of the continuous operation range or exceeds the upper limit of the continuous operation range.  Individual voltage deviations end when the root-mean-square voltage magnitude at the POIB, for the previous one-cycle period of fundamental frequency, returns to the continuous operation region.

(8)	The Resource Entity or Interconnecting Entity (IE) for each IBR shall maximize voltage ride-through capability with existing equipment as soon as practicable but no later than December 31, 2025, and shall by March 1, 2024, submit to ERCOT a report and supporting documentation containing the following:

(a)	The current and potential future IBR voltage ride-through capability (including any associated adjustments to improve voltage ride-through capability) in a format similar to Table A in paragraph (1) above;

(b)	The proposed modifications to maximize the IBR voltage ride-through capability and allow the IBR to comply with the voltage ride-through requirements in paragraphs (1) through (7) above;

(c)	A schedule for implementing those modifications as soon as practicable but no later than December 31, 2025;

(d)	Any limitations on the IBR’s voltage ride-through capability making it technically infeasible to meet the requirements in paragraphs (1) through (7) above; and

(e)	A plan (e.g., replacing inverters, turbines, or power converters, etc.) to comply with the voltage ride-through requirements of Section 2.9.1.1, Preferred Voltage Ride-Through Requirements for Transmission-Connected Inverter-Based Resources (IBRs), as soon as practicable but no later than December 31, 2027 for any IBR that will be unable to comply with all of the requirements of paragraphs (1) through (7) above by December 31, 2025.

Based on the information provided by the Resource Entity or IE, if ERCOT determines in its sole and reasonable discretion an IBR cannot comply with all applicable voltage ride-through requirements, the IBR operation may be restricted after December 31, 2025 as set forth in paragraph (10) below.  Any IBR that will be upgraded pursuant to paragraph (8)(e) above, may operate without restrictions until December 31, 2027, if it does not have any subsequent ride-through failures according to the voltage ride-through requirements of paragraphs (1) through (7) above.

(9)	If an IBR fails to perform in accordance with the voltage ride-through requirements of paragraphs (1) through (7) above, the IBR operation may be restricted as set forth in paragraph (10) below.  Additionally, the Resource Entity for the IBR shall investigate the event and report to ERCOT the cause of the IBR failure.  All impacted TSPs shall provide available information to ERCOT to assist with event analysis.

(10)	Any IBR that cannot comply with the voltage ride-through requirements of paragraphs (1) through (7) above, may be restricted or may not be permitted to operate on the ERCOT System unless ERCOT, in its sole and reasonable discretion, allows it to do so.  Each QSE shall, for each IBR not permitted to operate, reflect in its Current Operating Plan (COP) and Real-Time telemetry a Resource Status of OFF, OUT, or EMR in accordance with Protocol Sections 3.9.1, Current Operating Plan (COP) Criteria and 6.5.5.1, Changes in Resource Status, as appropriate.  If the Resource Entity can implement IBR modifications to resolve the technical limitations or performance failures preventing compliance with applicable voltage ride-through requirements, the Resource Entity shall submit to ERCOT a report and supporting documentation containing the following:

(a)	The current technical limitations and IBR voltage ride-through capability in a format similar to Table A in paragraph (1) above;

(b)	The proposed modifications and voltage ride-through capability allowing the IBR to comply with the voltage ride-through requirements in a format similar to Table A in paragraph (1) above; and

(c)	A schedule for implementing those modifications.

In its sole and reasonable discretion, ERCOT may accept the proposed modification plan.  Upon completion of the accepted modification plan, ERCOT will remove the restrictions placed on the IBR unless the IBR experiences additional unresolved technical limitations or performance failures.  ERCOT may allow the IBR to operate at reduced output prior to the implementation of an accepted modification plan if the reduced output allows the IBR to comply with the applicable ride-through requirements.