## Slide 1
LFLTF Meeting – Discussion of NPRR1191 and Related Revision Requests
September 6, 2023

## Slide 2
Antitrust Admonition
To avoid raising concerns about antitrust liability, participants in ERCOT activities should refrain from proposing any action or measure that would exceed ERCOT’s authority under federal or state law. For additional information, stakeholders should consult the Statement of Position on Antitrust Issues for Members of ERCOT Committees, Subcommittees, and Working Groups, which is posted on the ERCOT website.1
Disclaimer
All presentations and materials submitted by Market Participants or any other Entity to ERCOT staff for this meeting are received and posted with the acknowledgement that the information will be considered public in accordance with the ERCOT Websites Content Management Operating Procedure.
1The document is available at http://www.ercot.com/about/governance/index.html.

## Slide 3: LFLTF Meeting Agenda
Welcome and Antitrust Admonition – Bob Wittmeyer
ERCOT History of New Design Topics – Bob Wittmeyer
Queue Update – Posted on the Meeting Page – Agee Springer
Responses to Stakeholder Questions and Comments – ERCOT Staff
Overview of Topics for 9/25 LFLTF

## Slide 4: Feedback on Large Load Revision Requests
Today’s meeting will cover feedback received on the following topics:
  New Large Load Interconnection Process
  RCL Registration and Deployment
  Ramp Rate Restrictions
  Registration of Loads 25 MW or More
Not all questions and comments received on these topics will be addressed today due to ongoing internal discussions.
  ERCOT is committed to discussing these comments at future LFLTF meetings.

## Slide 5: New Interconnection Process

## Slide 6: New Interconnection Process
Submitted by CPS Energy
ERCOT Comments:
  As currently drafted, the fee would be assessed on the Customer. The Customer likely would not have selected a QSE at the time the LLIS is initiated.
Will the LLIS Study Fee be assessed on the Customer or the Customer’s QSE?
References – NPRR1191 Fee Schedule

## Slide 7: New Interconnection Process
Submitted by Lancium, Satoshi Energy
ERCOT Comments:
  Section 9.1 of the Board Policies and Procedures authorizes fees for "services provided by ERCOT." It is unclear that this would qualify as a service.
In addition to the proposed fee to cover ERCOT’s costs, an additional large fee should be required that is refundable when the Large Load energizes. The goal is to rationalize the interconnection request queue.
References – NPRR1191 Fee Schedule

## Slide 8: New Interconnection Process
Submitted by CPS Energy
ERCOT Comments:
  ERCOT’s goal is to ensure its NERC obligations are met for Large Loads requesting interconnection within 24 months. This is also true for the current interim interconnection process.
Is ERCOT's goal to speed up interconnection or to get more time to assess these projects with more detail to preserve reliability?
References – PGRR111 Section 9

## Slide 9: New Interconnection Process
Submitted by AEP
ERCOT Comments:
  The LLIS timelines were developed with the concept of an accelerated interconnection process for Loads wishing to interconnect in less than 24 months.
  ERCOT is open to revisions to this timeline to address the needs of all stakeholders.
3 Business Days is too quick of a turnaround for many steps of the LLIS. We would like to extend those to 10 Business Days or have the LLIS timeline match the response times of the generation interconnection process.
References – PGRR111 Section 9

## Slide 10: New Interconnection Process
Submitted by AEP
ERCOT Comments:
  Only additions within 24 months would be subject to the LLIS.
  ERCOT recognizes this concern and is open to further feedback on this topic to determine the best approach.
In PGRR111 section 9.2.1 (1) (b) (iii) and (iv) does this imply if a load is 70 MW today and wants to add 5 MW, then they will have to go through the LLIS process?
References – PGRR111 9.2.1

## Slide 11: New Interconnection Process
Submitted by AEP
ERCOT Comments:
  The ability of CLRs to connect additional MWs is based on their ability to be dispatched by SCED.
  SCED does not resolve voltage violations. Therefore, CLRs are not given credit for resolving voltage violations in the Steady State Study.
In evaluating the LLIS Steady State Study, should a CLR also be allowed to connect more MWs for voltage violations?
References – PGRR111 9.4.3.1 (6)(b)

## Slide 12: Feedback – New Interconnection Process
Submitted by Priority Power
ERCOT Comments:
  Please refer to PGRR111 Section 9.3.4.1.
ERCOT should provide more specifics on when an interruptible large load would be allowed to connect more MWs.
References – PGRR111 9.3.4.1

## Slide 13: New Interconnection Process
Submitted by Satoshi Energy
ERCOT Comments:
  PGRR111 Section 9.3.4.1 allows for CLRs to be dispatched for thermal basecase, N-1, and N-1-1 conditions.
  There is no redispatch allowed for voltage violations as SCED does not solve for those.
Language should be added to allow loads to be constraints that create a SCED re-dispatch after the n-1 event or other acceptable solution to ensure resilience in n-1-1 scenarios. This will provide better reliability than installing significant reactive systems that are rarely required.
References – PGRR111 9.3.4.1

## Slide 14: SSO Mitigation
Submitted by Lancium
ERCOT Comments:
  The responsibility would be assigned to the entity that created the SSO concern
    If the addition of a Large Load created an SSO concern that did not previously exist, the Load would bear responsibility for mitigation.
    If a future transmission upgrade created an SSO concern that did was not present in the LLIS, the TSP would bear responsibility for the mitigation.
Who is ultimately responsible for the execution of the SSO Mitigation Plan? TSP or Load? Who pays for what?
References – NPRR1191 3.22.1.3

## Slide 15: Clarifying Questions – New Interconnection Process
Submitted by Lancium
ERCOT Comments:
  This information would be identified during the LLIS by the lead TSP. It would be included in the final study reports.
  These upgrades would then need to be included in the updated Load Commissioning Plan submitted after an interconnection agreement is signed.
When is information about necessary transmission upgrades for future Demand increases required by ERCOT?
References – PGRR111 9.4

## Slide 16: New Interconnection Process
Submitted by AEP
ERCOT Comments:
  The intention is for this to be documented in RIOO and reflected in the Load Commissioning Plan submitted after an interconnection agreement with the TSP is signed.
On completion of the LLIS, will the ERCOT approval and the amount of approved MWs be documented in RIOO?
References – PGRR111 9.4 (7), 9.5, 9.6 (3)

## Slide 17: Clarifying Questions – New Interconnection Process
Submitted by Lancium
ERCOT Comments:
  ERCOT is required to maintain the confidentiality of individual Customer usage information under PURA sec. 17.004(a)(6), as well as the ERCOT Nodal Protocols.
Why are LLIS study reports marked as “Certified” and are only accessible to TSPs, whereas Generator FIS reports have been marked as “Secure” and have been even available to other types of market participants?
References – PGRR111 9.4

## Slide 18: Registration and Deployment of RCLs

## Slide 19: Registration of RCLs
Submitted by CPS Energy
ERCOT Comments:
  ERCOT would appreciate some additional context behind this question.
For RCLs, how is the QSE designated? This may need to accommodate differences in Muni and other NOIE areas.
References – NPRR1191 16.20

## Slide 20: Discussion – Deployment of RCLs
Submitted by Oncor
ERCOT Comments:
  Telemetry may be needed to monitor these loads for compliance.
Participation as a RCL should not be limited to transmission connected loads.
References – NPRR1191 16.20, 6.5.9.4.1, NOGRR256 4.5.3.4, 4.5.3.5

## Slide 21: Discussion – Deployment of RCLs
Submitted by Texas Oil and Gas
ERCOT Comments:
  ERCOT would appreciate some additional context behind this comment.
More information on RCLs is needed, including how these loads would interact with critical load designation.
References – NPRR1191 6.5.9.4.1, NOGRR256 4.5.3.4, 4.5.3.5

## Slide 22: Deployment of RCLs
Submitted by Lancium
ERCOT Comments:
  ERCOT would like to clarify if this question is related to the calculation of the Reliability Deployment Price Adder (RDPA) or for measuring compliance with the RCL deployment instruction.
How are RCL “deployed MWs” calculated? Telemetry or nameplate capacity? What if RCL has already been turned down voluntarily for high prices?
References – NPRR1191 6.5.7.3.1

## Slide 23: Discussion – Deployment of RCLs
Submitted by Priority Power
ERCOT Comments:
  The intention is for the TO to restore service to the RCL when the deployment is ended by ERCOT. There may be additional language needed to clarify this.
Greater specificity is needed about the process for restoring of a RCL after disconnection by the TO for failing to comply with a deployment instruction.
References – NPRR1191 6.5.9.4.1, NOGRR256 4.5.3.4, 4.5.3.5

## Slide 24: Ramp Rate Limitations

## Slide 25: Ramp Rate Limitations
Submitted by CPS Energy, Steel Mills
ERCOT Comments:
  These Revision Requests are intended to address behaviors that represent reliability risks to the system, regardless of the end use of the energy.
Is ERCOT open to differentiating ramp rate restrictions and grandfathering allowances by load type?
References – NPRR1191 6.5.7.12

## Slide 26: Ramp Rate Limitations
Submitted by Texas Blockchain Council
ERCOT Comments:
  ERCOT would appreciate some additional context behind this question.
How will ramp rates apply to net-metered loads?
References – NPRR1191 6.5.7.12 (3)

## Slide 27: Ramp Rate Limitations
Submitted by Galaxy Digital
ERCOT Comments:
  The intent mirrors the same requirement for IRRs, which also are capable of ramping faster than 20% per minute.
What is the rationale for the proposed ramp rate limitations of 20% per minute of registered peak demand for Controllable Load Resources (CLRs)? If a CLR can ramp up or down at a rate exceeding 20% per minute of its registered peak demand while still following base points, what is the purpose of limiting the CLR ramp rate to 20% per minute?
References – NPRR1191 6.5.7.12

## Slide 28: Ramp Rate Limitations
Submitted by Priority Power
ERCOT Comments:
  The 20% permitted ramp rate is a hard limitation. SCED will account for the available ramping resources when determining the basepoint for the CLR.
  The intention is to allow the CLR to ramp from 0 MW to full consumption within a single 5-minute interval unless available system ramping capability cannot accommodate that during the interval.
Is the 20% per min a hard limitation or is it subject to the availability of ramping resources available to SCED? The status quo is that a CLR can ramp from minimum load to maximum load (or vice-versa) within one SCED interval.
References – NPRR1191 6.5.7.12

## Slide 29: Ramp Rate Limitations
Submitted by Priority Power
ERCOT Comments:
  This language mirrors language establishing a PFR requirement for IRRs.
  ERCOT is open to additional feedback on this language.
ERCOT should specify criteria for a compliance plan
References – NPRR1191 6.5.7.12

## Slide 30: Ramp Rate Limitations
Submitted by Texas Blockchain Council, Steel Mills, Priority Power, TIEC
ERCOT Comments:
  ERCOT is open to stakeholder input to further develop this language.
Clarification is needed on what constitutes a “material change” that would potentially affect a Load’s grandfathered status.
References – NPRR1191 6.5.7.12

## Slide 31: Ramp Rate Limitations
Submitted by Steel Mills, TIEC
ERCOT Comments:
  ERCOT recognizes this concern and is open to additional feedback on this issue.
Many industrial sites must ramp up and down quickly—and often—based on the fundamental nature of their processes. For other industrial sites to ramp at a prescribed rate, they would have to make substantial investments in batteries or some type of behind-the-meter generation to offset the fundamental nature of their operations.
References – NPRR1191 6.5.7.12

## Slide 32: Ramp Rate Limitations
Submitted by Texas Blockchain Council, Priority Power, Satoshi Energy, Galaxy Digital
ERCOT Comments:
  Non-CLR Large Loads are, by definition, not dispatchable outside of AS and ERS deployments.
  ERCOT has no visibility into factors setting the strike price for individual loads.
  ERCOT has observed multiple instances during Summer 2023 where Large Load behavior was contrary to ERCOT expectations given system prices.
Restrictions on non-CLR Large Load are extremely restrictive from a risk and collateral perspective. Non-CLR Large Loads can be dispatched effectively and in a knowable way through the scarcity-based pricing mechanism.
References – NPRR1191 6.5.7.12

## Slide 33: Ramp Rate Limitations
Submitted by Texas Oil and Gas
ERCOT Comments:
  ERCOT would appreciate some additional context behind this comment.
Ramp rate limitations present a potential burden on customers with multiple points of interconnection.
References – NPRR1191 6.5.7.12 (3)

## Slide 34: Ramp Rate Limitations
Submitted by TIEC
ERCOT Comments:
  ERCOT would appreciate some additional context behind this comment.
This may make it infeasible for many loads to provide Responsive Reserve Service (RRS), and potentially other ancillary services, because curtailing to provide the obligated megawatts will require the load to violate ramp requirements for the remainder of its load.
References – NPRR1191 6.5.7.12

## Slide 35: Registration of Loads Greater than 25 MW

## Slide 36: Registration of Loads ≥ 25 MW
ERCOT received feedback from multiple stakeholders objecting to the requirement that Loads 25 MW or larger provide additional information to ERCOT.
ERCOT also recognizes the concerns expressed by stakeholders:
  Loads have historically not interfaced directly with ERCOT.
  Submission of information would be an administrative burden on Customers.
  Any information submitted to ERCOT must be treated as confidential.
ERCOT does not agree that information currently provided by the TDSPs or the State Estimator is sufficient for proper situational awareness and forecasting.

## Slide 37: Registration of Loads ≥ 25 MW
Submitted by Lancium, Satoshi Energy
ERCOT Comments:
  ERCOT intends for this information to be sorted into broad categories.
  ERCOT is open to additional input to ensure that these categories capture different segments without being overly burdensome.
Primary/secondary end-use activities are likely to change over time. If Customers are required to identify end-uses, it should be in a manner general enough to mitigate frequent updates.
References – NPRR1191 16.20, PGRR111 9.2, RRGRR036

## Slide 38: Topics for the 9/25 LFLTF Meeting

## Slide 39: Topics for the 9/25 LFLTF Meeting
New Large Load Interconnection Process
Ramp Rate Restrictions
Voltage Ride-Through
Additional topics identified in today’s meeting