## Slide 1
Telemetered ESR Auxiliary Load Calculation Methodologies
Donald Maul – Supervisor Meter Engineering
September 6, 2023

## Slide 2: Telemetered Internal Auxiliary Load for ESR
  NPRR 1020 added a process to allow auxiliary load that is internal to an Energy Storage Resource (ESR) to be calculated using internal sensors and telemetered to the WSL EPS Meter.
    Telemetered aux load is deducted from the EPS-measured value and a calculated WSL value is recorded and used for market settlement.
10.2.4 Resource Entity Calculation and Telemetry of ESR Auxiliary Load Values
(1) When the Resource Entity certifies, the interconnecting TDSP confirms by approving the metering design, and, based on the information provided by the TDSP as part of the EPS Design Proposal, ERCOT agrees that metering of an ESR’s WSL separate from the ESR’s auxiliary Load is not feasible based on the ESR’s physical design, the Resource Entity for that ESR shall be permitted to calculate the auxiliary Load using measurements from its own internal sensors and telemeter a Real-Time aggregated value for that Load to the TDSP’s EPS Meter. The Resource Entity may telemeter a zero Load value only when the ESR is discharging more than the calculated auxiliary Load. The methodology by which the auxiliary Load is calculated is subject to ERCOT approval.

## Slide 3: Aux Load Calculation Methodologies
  Two methodologies have been used to date to calculate an ESR’s internal auxiliary load:
    Direct, real-time internal measurement of the voltage and current of the internal aux load; or
    A fixed maximum aux load value is multiplied by a factor determined from real-time internal on/off signals.
      Example of second methodology:
        An ESR has 10 inverters, each of which may be on or off depending on the ESR’s level of operation.
        A real-time internal signal indicates whether each inverter is on or off during an interval (i.e. indicating whether the inverter is being used for ESR charging/operation).
        The maximum possible auxiliary load for any individual inverter has been determined to be 150 watts.
        To determine aux load during an interval, the number of inverters that are on based on the signal is multiplied by 150 watts.
        If 6 inverters are on and the other 4 are off, then the telemetered aux load for that interval would be 900 watts (6*150 watts).

## Slide 4: Methodology Requirements
  Use of the fixed value for the internal aux load methodology is permissible under the NPRR1020 paradigm when used with an on/off signal from the ESR’s internal unit.
  Protocol § 10.2.4(2) requires the ESR to demonstrate that the proposed calculation will not understate the auxiliary load.
    This demonstration must be included both during the EPS Design Proposal submittal stage and annually as part of the ESR’s required attestation that is reviewed and approved by a Texas Professional Engineer before being submitted to ERCOT.
  Please refer to the ERCOT Nodal Protocols for additional requirements related to ESR auxiliary load.