## Slide 1
NPRR1191 – Overview
DSWG
September 15, 2023

## Slide 2: Scope of Proposed Changes in Large Load Revision Requests
A package of Revision Requests to formalize the interim interconnection process and establish operational requirements for Large Loads (≥ 75 MW)
Require certain basic information about all Loads ≥ 25 MW (size, contact info, registration type, etc.)
Creation of a new ERCOT team to manage the interconnection process, analyze Large Load behavior and compliance, and support other affected ERCOT teams
  FTE impact is accounted for in ERCOT’s 2024 budget
ERCOT systems affected: RIOO, EMS, MMS, NMMS, PI, Grid-Geo, reporting and data replication
Preliminary IA: ~$1M

## Slide 3: Revision Request Package – Structure
NPRR1188 – CLR Nodal Settlement
Future CLR-related NPRR
NPRR1191
Definitions
Provision of Information
Ramp rate limits
Changes to SSO/SSR terminology
Interconnection fee and other changes
PGRR111
Handling of Large Loads in Planning studies
New interconnection process for Large Loads
  Studies
  Quarterly Stability Assessment
  Modeling
  Approval to Energize
Ongoing obligations for Large Loads
NOGRR256
Large Load voltage ride-through requirements
Curtailing of RCLs prior to EEA
Exemption of RCLs from TSP firm load shed obligations
Requires CLRs to be in SCED when consuming energy
Changes non-battery CLRs to Nodal settlement
CLR AS bids co-optimized in DAM
Could remove requirement that CLRs provide PFR if they are not providing AS
Could address impacts to outage coordination and Ops studies/systems
RRGRR036
New sections added to RIOO
New RIOO fields to support the interconnection process
Large Load RR Package
These RRs directly address Large Load issues
and will be covered at today’s workshop
Related NPRRs
These NPRRs may impact some Large Loads but are not
included in this package and will not be covered in detail today

## Slide 4: Revision Request Package – Contents
NPRR1188 – CLR Nodal Settlement
Future CLR-related NPRR
NPRR1191
Definitions
Provision of Information
Ramp rate limits
Changes to SSO/SSR terminology
Interconnection fee and other changes
PGRR111
Handling of Large Loads in Planning studies
New interconnection process for Large Loads
  Studies
  Quarterly Stability Assessment
  Modeling
  Approval to Energize
Ongoing obligations for Large Loads
NOGRR256
Large Load voltage ride-through requirements
Curtailing of RCLs prior to EEA
Exemption of RCLs from TSP firm Load shed obligations
Requires CLRs to be in SCED when consuming energy
Changes non-battery CLRs to Nodal settlement
CLR AS bids co-optimized in DAM
Could remove requirement that CLRs provide PFR if they are not providing AS
Could address impacts to outage coordination and Ops studies/systems
RRGRR036
New sections added to RIOO
New RIOO fields to support the interconnection process

## Slide 5: New Defined Terms
Large Load – One or more Facilities at a single site with an aggregate peak Demand greater than or equal to 75 MW behind one or more common Points of Interconnection (POIs) or Service Delivery Points
Interconnecting Large Load Entity (ILLE) – Any Entity that has submitted a request to interconnect a Large Load to the ERCOT system. Equivalent to an Interconnecting Entity in the generation interconnection process
Large Load Interconnection Study (LLIS) – The set of interconnection studies done by the TSP for a Large Load connecting in 2 years or less
Registered Curtailable Load (RCL) – A Load registered with ERCOT that has agreed to curtail its consumption on instruction from ERCOT prior to EEA
Load Commissioning Plan – A schedule furnished by the ILLE detailing dates and peak Demand amounts from the Initial Energization date to the date peak consumption is reached
Other New or Modified Terms – Subsynchronous Ferroresonance (SSFR), Torque Amplification, Controllable Load Resource
References – NPRR1191 2.1, PGRR111 2.1

## Slide 6: New Defined Load Type – Registered Curtailable Load (RCL)
New category of Loads developed in response to feedback from Large Load Customers that wish to help ERCOT avoid EEA events.
RCLs may be directed to curtail by ERCOT prior to entering emergency operations and must have a QSE to receive ERCOT instructions.
RCLs are not counted toward Transmission Operator EEA 3 firm Load shed obligations.
RCLs are eligible to participate in ERS.
RCLs are not a Resource and are not eligible to carry Ancillary Services.
References – NPRR1191 6.5.9.4.1, 16.20.1, NOGRR256 4.5.3.1
Firm
RCL
(new category)
NCLR
CLR
Types of “flexible” Load
Least Flexible
More
Flexible

## Slide 7: Load Shed by RCL Prior to EEA
ERCOT may curtail any Registered Curtailable Loads (RCLs) that are still consuming energy when PRC drops below 3,100 MW and is not expected to recover within 30 minutes
  Occurs before ERS may be deployed
QSEs with RCLs will shed their share of 100 MW blocks at the instruction of ERCOT. RCLs must comply with the instruction from their QSE to curtail.
Deploying RCLs will trigger the Reliability Deployment Price Adder (RDPA)
RCLs are not counted toward Transmission Operator EEA 3 firm Load shed obligations
References – NPRR1191 6.5.7.3.1, 6.5.9.4.1, NOGRR256 4.5.3.4, 4.5.3.5
PRC
1000 MW
1500 MW
2000 MW
2500 MW
3000 MW
3500 MW
PRC <1000 MW
Firm Load shed
in 100 MW blocks
PRC <1430 MW
EEA Level 3
PRC <1750 MW
EEA Level 2
PRC <2300 MW
EEA Level 1
PRC <3100 MW – May deploy Registered Curtailable Loads
PRC <3000 MW
May deploy ERS
PRC <1500 MW
EEA Level 3 and firm Load shed in 100 MW blocks
PRC <2000 MW
EEA Level 2
PRC <2500 MW
EEA Level 1
PRC <3000 MW
May deploy ERS
PRC <3100 MW – May deploy Registered Curtailable Loads
Current
Post-NPRR1176
(Expected October 1, 2023)

## Slide 8: Ramp Rate Limits
Similar to intermittent Resources, Large Loads registered as CLRs will be limited to a telemetered ramp rate of 20% per min. The actual ramping of these Loads will be managed by SCED.
All Large Loads that are not registered as CLRs will be subject to ramp rate restrictions, measured at the POI or Service Delivery Point:
  Lesser of 5% peak Demand or 20 MW per min when reducing consumption
  Lesser of 2% peak Demand or 8 MW per min when increasing consumption
These limits do not apply to NCLRs while appropriately responding to an ERCOT deployment.
Large Loads connected before the March 25, 2022 Market Notice will be grandfathered unless a material change to the Facility is made.
References – NPRR1191 6.5.7.12

## Slide 9: Path Forward
ERCOT has received a large amount of feedback on this package.
These issues will continue to be discussed at the LFLTF
  Next meeting is scheduled for 9/25

## Slide 10: Questions

## Slide 11: Appendix – Comparison of Load Types
 | Firm | RCL | NCLR | CLR
Must provide registration data to ERCOT |  |  |  | 
Is a Resource as defined in the Protocols |  |  |  | 
May be reduced to min Load in Planning studies for system capacity issues |  |  |  | 
May be dispatched like a Generation Resource in Planning studies |  |  |  | 
Required to have a QSE |  |  |  | 
May be curtailed by ERCOT at 3,100 MW PRC |  |  |  | 
May participate in Emergency Response Service (ERS) |  |  |  | 
May qualify to provide Ancillary Services |  |  |  | 
Can change Demand level outside of SCED |  |  |  | 
Rate at which Demand may change (ramp rate) will be restricted |  |  |  | 
Is dispatched by SCED at all times when consuming energy |  |  |  | *
Settled at Zonal prices |  |  |  | 
Settled at Nodal prices |  |  |  | *
* Pending approval of NPRR1188
Back to Directory