## Slide 1
2024 Ancillary Service Methodology Discussion
Balancing Operations Planning
ERCOT

## Slide 2: Discussion Scope for Today
This presentation will discuss the various approaches ERCOT is considering to determine Ancillary Service (A/S) quantities for 2024.
  ERCOT is not considering any changes in the methodologies used to compute Regulation Service and Non-Spinning Reserve Service requirements for 2024.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2024 assessment for ERCOT shows a decrease in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2024 will change to 1,185 MW.
  ERCOT is considering to remove the 2,800 MW RRS floor that is applied to summer peak hours for 2024. A Minimum 2,300 MW of RRS will apply to all hours.
  ERCOT is considering some changes in the methodology used to compute the frequency recovery portion of ECRS for 2024.
The Ancillary Service (A/S) quantities for 2024 contained in this presentation are based on the methodology that was approved in December 2022. The quantities for 2024 reflect moving forward the historic data on which these are based, unless otherwise noted.
ERCOT is seeking stakeholder feedback on these proposes changes for the 2024 A/S Methodology.

## Slide 3
Regulation Service

## Slide 4: Regulation Service Methodology
ERCOT is not considering any change to the methodology used to compute the minimum Regulation Service requirements in 2024.
The preliminary Regulation quantities for January 2024 through July 2024 in subsequent slides have been computed using current methodology (2022 and 2023 five-minute net load variability), updated Wind Adjustment tables and the updated Solar Adjustment tables.

## Slide 5: Overview – Dynamic PSRR Threshold in GTBD
Chart: Dynamic PSRR Threshold
 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 100 | 100 | 100 | 0 | 0 | 0
ERCOT started to apply a dynamic PSRR threshold in GTBD calculation on 6/12/2023
PSRR thresholds change with 4 pre-defined day periods - Night, Sunrise, Sunset and Other
ERCOT started with a threshold of 80MW/min for Sunrise and Sunset periods on 6/12 and subsequently increased it to 100MW/min on 6/15
ERCOT plans to update the thresholds and the definition of day periods seasonally* (4 times a year)
Night
* Seasons will be defined by shift in solar ramping patterns

## Slide 6: SCED Manual Offset and Reg Up Exhaustion

## Slide 7: Regulation Exhaustion
2023 Avg:1.6%
2022 Avg :2.0%
2023 Avg:3.8%
2022 Avg :5.1%

## Slide 8: Hourly Average Regulation Comparison

## Slide 9: Regulation Comparison February

## Slide 10: Regulation Comparison March

## Slide 11: Regulation Comparison June

## Slide 12: Other Ideas on Regulation Methodology
ERCOT has been exploring the idea of switching to an intra-hour netload forecast error based quantity computation methodology.
  This approach would essentially set regulation quantities based on the error in the net load forecast that GTBD/SCED uses.
  The changes in GTBD to use dynamic PSRR thresholds impact the net load forecast error value (in theory these should help lower the net load forecast error in GTBD when ramps can be correctly forecasted).
  Since these changes were implemented in June 2023, an approach that sets Regulation quantities based on intra-hour net load forecast error will be better considered after this change stabilizes.

## Slide 13
Responsive Reserve Service

## Slide 14: Responsive Reserve Service (RRS) Methodology
ERCOT is not considering one change in the methodology used to compute RRS requirements in 2024.
  ERCOT is considering to remove the 2,800 MW floor that is applied during summer peak hours. A minimum of 2,300 MW of RRS will continue to be procured in all hours. The additional 500 MW RRS during Summer peak helped in maintaining sufficient amount of Physical Responsive Capability (PRC) during these hours. The implementation of NPRR 989 that improved accounting of PRC from Energy Storage Resources (ESRs) and the recent implementation of ERCOT Contingency Reserve Service (ECRS) are helping in maintaining PRC.
NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2024 assessment for ERCOT shows a decrease in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2024 will change to 1,185 MW.
The preliminary RRS quantities for January 2024 through July 2024 in subsequent slides have been computed using 2022 and 2023 system inertia conditions and updated RRS table.
  The RRS table tracks RRS requirements for different inertia conditions. This table was updated in 2024 to use a minimum RRS-PFR limit of 1,185 MW.
Notes: OY2022 IFRO – 412 MW/0.1 Hz | Limit 1,240 MW
OY2023 IFRO – 463 MW/0.1 Hz | Limit 1,390 MW
OY2024 IFRO – 395 MW/0.1 Hz | Limit 1,185 MW

## Slide 15: Load Damping Ratio (New)
ERCOT has computed the effective load damping ratio for frequency events since Jan 1, 2017. Based on this analysis, 2% is a reasonable damping ratio for RRS studies.
For each frequency event, the load dampening ratio is calculated as the delta load percentage change/ delta frequency percentage change.
%
where : Event Start Time

## Slide 16: 2024 RRS Table
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS Curr IFRO (MW) | 3335 | 3287 | 3239 | 3195 | 3156 | 3079 | 3041 | 2991 | 2949 | 2871 | 2774 | 2705
**RRS Upd IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2960 | 2916 | 2880 | 2808 | 2716 | 2654
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290*** | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2651 | 2600 | 2562 | 2517 | 2466 | 2427 | 2381 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2606 | 2560 | 2529 | 2491 | 2444 | 2412 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,390 MW.
**RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,185 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. RRS requirement during these is based on the applicable floor.
Notes: RRS quantity for 2024 decrease between 2 MW (320 GW.s case) and 61 MW (150 GW.s case)

## Slide 17: Hourly Average RRS Comparison

## Slide 18: RRS Comparison February

## Slide 19: RRS Comparison March

## Slide 20: RRS Comparison July

## Slide 21
ERCOT Contingency Reserve Service

## Slide 22: ERCOT Contingency Reserve Service (ECRS) Methodology
ECRS requirements are computed as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support net load forecast errors during sustained net load ramps.
For 2024, ERCOT is considering to make minor tweaks to the frequency recovery portion of the calculation. Specifically, ERCOT is considering to use 2 years of historic information and cover 60% of historic net load and inertia conditions.
The preliminary ECRS quantities for January 2024 through July 2024 in subsequent slides have been computed using current methodology (2021, 2022 and 2023 Intra-Hour Net load and Net load Forecast, 2022 and 2023 system inertia conditions ) and updated Intra-hour Solar Over-Forecast Error Adjustment table.
  Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity

## Slide 23: Cold Start-up Time of OFFNS Resources in 2023 (Revised)
Cold Start time of units that were providing Non-Spin using OFFNS status was analyzed at 5-min resolution.
80th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
2 – Feb | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
3 – Mar | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
4 – Apr | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
5 – May | 18 min | 18 min | 18 min | 18 min | 24 min | 24 min
6 – Jun | 18 min | 18 min | 18 min | 30 min | 30 min | 30 min
7 – Jul | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
8 – Aug | 15 min | 18 min | 18 min | 30 min | 30 min | 18 min
Aug 17, 25, 30 | 18 min | 18 min | 30 min | 30 min | 30 min | 30 min
95th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
2 – Feb | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
3 – Mar | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
4 – Apr | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
5 – May | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
6 – Jun | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
7 – Jul | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
8 – Aug | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Aug 17, 25, 30 | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Notes: Decker Removed

## Slide 24: Hourly Average ECRS Comparison

## Slide 25: ECRS Comparison Jan

## Slide 26: ECRS Comparison Mar

## Slide 27: ECRS Comparison May

## Slide 28: ECRS Comparison July
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
2023 | 1571.8554 | 1517.6647 | 1556.4346 | 1431.2939 | 1407.9101 | 1417.1478 | 1612.2507 | 1790.9409 | 2464.7207 | 2181.4961 | 2484.8224 | 2525.6201 | 2509.5187 | 2339.0807 | 2127.7674 | 2451.3413 | 2574.7463 | 2447.7697 | 2497.9323 | 2393.2004 | 2076.1671 | 2046.2221 | 1834.5164 | 1717.8444
2024 ECRS | 1522 | 1500 | 1585 | 1413 | 1361 | 1389 | 1512 | 1878 | 1862 | 2080 | 2088 | 2220 | 2267 | 2508 | 2390 | 2656 | 2664 | 2567 | 2356 | 2011 | 2260 | 2273 | 2075 | 1871

## Slide 29
Non-Spin Reserve Service

## Slide 30: Non-Spinning Reserve Methodology
ERCOT is not considering any change to the methodology used to compute the minimum Non-Spin requirements in 2024. Non-Spin quantities in 2024 will be computed using 75th to 95th percentile of 6 Hours Ahead (HA) hourly average net load forecast error to compute Non-Spin quantities.
The preliminary Non-Spin quantities for January 2024 through July 2024 in subsequent slides have been computed using current methodology (2021, 2022 and 2023 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the updated Solar Over-Forecast Error Adjustment table.
  Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind and solar capacity, respectively.
  Note the Non-Spin quantities have been computed using the 2023 Intra-day Forced Outage table. ERCOT will update this in the next round of discussions in October.

## Slide 31: 2023 RUCs by Startup Time

## Slide 32: Adequacy of Non-Spin quantities in 2023
Between Jan 1, 2023 and Jul 31, 2023,
  ~5% of the time the 6 Hour Ahead (HA) net load forecast error based Non-Spin was not sufficient to cover the 6HA risk
  ~16% of the time the margin in the 6 Hour Ahead (HA) net load forecast error based Non-Spin to cover the 6HA risk was less than 1,430 MW.

## Slide 33: Hourly Average Non-Spin Comparison
*2024 NSRS quantities are calculated with 2023 outage table (to be updated).

## Slide 34: Non-Spin Comparison January
*2024 NSRS quantities are calculated with 2023 outage table (to be updated).

## Slide 35: Non-Spin Comparison May
*2024 NSRS quantities are calculated with 2023 outage table (to be updated).

## Slide 36: Non-Spin Comparison June
*2024 NSRS quantities are calculated with 2023 outage table (to be updated).

## Slide 37: Non-Spin Comparison July
*2024 NSRS quantities are calculated with 2023 outage table (to be updated).

## Slide 38: Summary (New)
Based on the analysis ERCOT has conducted thus far,
  ERCOT is not considering any changes in the methodologies used to compute Regulation Service and Non-Spinning Reserve Service requirements for 2024.
  ERCOT is considering changes in the methodologies used to compute Responsive Reserve Service and ERCOT Contingency Reserve Service requirements for 2024.
The proposed timeline for this review is included alongside.
Using feedback received from last year’s experience, to make the AS Methodology review process more efficient, this year, ERCOT plans to provide relevant details on the proposed methodology during the September/October working group discussions. Following these discussions ERCOT will present an abridged summary of the proposed changes during the November/December discussions.
2024 Methodology Review Timeline
September 20, 2023 – PDCWG
September 22, 2023 – WMWG
October 6, 2023 – WMWG (Proposed)
October 10, 2022 – PDCWG (Proposed)
October 19, 2023 – OWG (Proposed)
November 01, 2023 – WMS
November 02, 2023 – ROS
December 04, 2023 – TAC
December 19, 2023 – BoD
Interested Stakeholders are requested to attend September and October PDCWG and/or WMWG meetings to provide any feedback on the proposed 2024 AS Methodology.

## Slide 39
Suggestions?

## Slide 40: 2024 Solar Adjustment Tables
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
 | Min (MW) | Max (MW) | Average (MW)
Reg Up | 0 | 18 | 7.8
Reg Down | 0 | 20 | 7.7

## Slide 41: 2024 Wind Adjustment Tables
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Chart: Reg-Up Adjustment per 1000 MW increase in Wind Installed Capacity
| Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec.
2023 Reg-Up Adj. | 1.3798 | 1.5039 | 1.8328 | 1.806 | 1.6997 | 1.3779 | 1.1206 | 1.1201 | 1.303 | 1.2479 | 1.2649 | 1.3286
2024 Reg-Up Adj. | 1.1913 | 1.0376 | 1.6649 | 1.3893 | 1.4639 | 1.2949 | 1.309 | 1.0183 | 0.91327 | 0.88836 | 0.9438 | 0.83143
Chart: Reg-Down Adjustment per 1000 MW increase in Wind Installed Capacity
| Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec.
2023 Reg Down Adj. | 1.1056 | 1.3234 | 1.7668 | 1.679 | 1.3874 | 0.99909 | 0.84149 | 0.92914 | 1.0592 | 1.0554 | 1.0593 | 1.2217
2024 Reg Down Adj. | 1.1913 | 1.0376 | 1.6649 | 1.3893 | 1.4639 | 1.2949 | 1.309 | 1.0183 | 0.91327 | 0.88836 | 0.9438 | 0.83143
Notes: Avg Reg Up adjustment for wind is 1.2MW
Avg Reg Down adjustment for wind is 1.2 MW

## Slide 42: 2024 Intra-Hour Solar Adjustment Table
 | HE 1-2, 23-24 | HE 3-6 | HE 7-10 | HE 11-14 | HE 15-18 | HE 19-22
Jan | 0 | 0 | 0 | 21 | 20 | 0
Feb | 0 | 0 | 0 | 33 | 20 | 0
Mar | 0 | 0 | 0 | 33 | 73 | 0
Apr | 0 | 0 | 0 | 30 | 55 | 0
May | 0 | 0 | 0 | 59 | 96 | 26
Jun | 0 | 0 | 0 | 17 | 41 | 37
Jul | 0 | 0 | 0 | 23 | 23 | 8
Aug | 0 | 0 | 0 | 45 | 53 | 4
Sep | 0 | 0 | 0 | 64 | 56 | 0
Oct | 0 | 0 | 0 | 26 | 37 | 0
Nov | 0 | 0 | 0 | 1 | 4 | 0
Dec | 0 | 0 | 0 | 3 | 0 | 0

## Slide 43: Forecast Variability Process
ERCOT assess the netload forecast variability for Current Operation Day + 2 and may procure up to an additional 1,000 MW of Non-Spin for specific Operating Hours.
The approach for determining the additional increase will be updated such that the additional Non-Spin may be procured for Operating Hours that are
  identified as having an increased potential of high forecast variability,
  there is a risk that the actual net load during these Operating Hours could be higher than forecast (after making appropriate forecast model selection) AND
  the expected available capacity and expected reserves including the posted minimum Non-Spin requirements during these Operating Hours is not sufficient to cover the projected net load forecast uncertainty risk.
ERCOT procured additional Non-Spin for
  Jul 29, Aug 1, Aug 2, Aug 14, Aug 27, Aug 29, Aug 30, and Sep 3 and Sep 4 in 2021
  Jan. 2, Jan. 3, Jan. 20, Feb. 3, Feb. 4, May 22, May 23, May 24, June 1 in 2022.

## Slide 44: Non-Spinning Reserve Service (Non-Spin) Deployments in 2023-Q1
Chart: Non-Spin Responsibility
Between Jan 2023 and Mar 2023, there were 12 events that resulted in deployment of offline Non-Spin.
Note that, between Jun 2023 and Jul 2023, an average ~36 % of Non-Spin was provided using online capacity and by Quick Start Generation Resources. This type of Non-Spin is always available to SCED to dispatch (with an offer floor of $75) and no operator action is needed to deploy this capacity.
Deployment Start Time | Deployment End Time | Deployment Duration | Max Deployment (MW) | Reason
1/3/2023 17:21 | 1/3/2023 18:30 | 01:09:00 | 1134.8 | Available Headroom not sufficient for projected 30-minutes net load ramp
1/6/2023 16:53 | 1/6/2023 18:15 | 01:22:00 | 1214.5 | Projected Ramp Available
1/9/2023 17:26 | 1/9/2023 17:56 | 00:30:00 | 514 | Projected Ramp Available
1/17/2023 5:46 | 1/17/2023 7:25 | 01:39:00 | 468.4 | Projected Ramp Available
2/8/2023 18:07 | 2/8/2023 18:40 | 00:33:00 | 544 | 
3/21/2023 19:01 | 3/21/2023 19:50 | 00:49:00 | 544.6 | 
3/22/2023 19:01 | 3/22/2023 19:51 | 00:50:00 | 524.91 | 
3/24/2023 5:55 | 3/24/2023 7:19 | 01:24:00 | 1832 | 
3/24/2023 18:55 | 3/24/2023 19:33 | 00:38:00 | 976 | 
3/25/2023 18:44 | 3/25/2023 20:48 | 02:04:00 | 1828.7 | 
3/26/2023 18:35 | 3/26/2023 20:03 | 01:28:00 | 2241 | 
3/27/2023 18:32 | 3/27/2023 21:05 | 02:33:00 | 731 | 
Key Takeaway: All recent Non-Spin deployments have been to meet 30-minute ramping needs. Non-Spin performed well in all deployments.

## Slide 45: Non-Spinning Reserve Service (Non-Spin) Deployments in 2023-Q2
Chart: Non-Spin Responsibility
Between April 2023 and Jun 2023, there were 8 events that resulted in deployment of offline Non-Spin.
Note that, between Jun 2023 and Jul 2023, an average ~36 % of Non-Spin was provided using online capacity and by Quick Start Generation Resources. This type of Non-Spin is always available to SCED to dispatch (with an offer floor of $75) and no operator action is needed to deploy this capacity.
Deployment Start Time | Deployment End Time | Deployment Duration | Max Deployment (MW) | Reason
4/14/2023 19:15 | 4/14/2023 20:14 | 00:59:00 | 622.2 | Available Headroom not sufficient for projected 30-minutes net load ramp
4/21/2023 18:54 | 4/21/2023 20:56 | 02:02:00 | 690.4 | Projected Ramp Available
4/29/2023 19:39 | 4/29/2023 21:11 | 01:32:00 | 1182.5 | Projected Ramp Available
5/4/2023 19:50 | 5/4/2023 20:25 | 00:35:00 | 447 | Projected Ramp Available
5/11/2023 19:18 | 5/11/2023 21:18 | 02:00:00 | 1048.7 | 
6/10/2023 19:16 | 6/10/2023 20:32 | 01:16:00 | 328 | 
6/18/2023 19:36 | 6/18/2023 20:22 | 00:46:00 | 447.5 | 
6/20/2023 16:24 | 6/20/2023 21:09 | 04:45:00 | 378.7 | 
Key Takeaway: All recent Non-Spin deployments have been to meet 30-minute ramping needs. Non-Spin performed well in all deployments.

## Slide 46: Non-Spinning Reserve Service (Non-Spin) Deployments in 2023-Q3
Chart: Non-Spin Responsibility
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Jul-23
NSRS-Offline | 1553.8846 | 1621.9249 | 1762.7945 | 1782.4102 | 1823.1138 | 1855.9452 | 2405.2676 | 2385.802 | 2355.013 | 2351.9233 | 1932.9861 | 1959.539 | 1668.6809 | 1536.513 | 1432.1027 | 1354.7871 | 1288.6913 | 1243.3173 | 1121.0135 | 1101.4805 | 1158.0517 | 1216.3497 | 1595.5468 | 1693.453
NSRS-Online | 271.6289 | 255.8724 | 312.4973 | 298.4694 | 297.9607 | 284.808 | 395.8029 | 423.4334 | 448.8354 | 443.5995 | 354.6356 | 390.1498 | 642.1352 | 756.8418 | 869.2077 | 885.8493 | 936.69 | 973.4698 | 866.1968 | 879.2047 | 816.3629 | 868.9835 | 457.0845 | 320.2601
NSRS-QSGR | 475.1381 | 421.2155 | 575.7048 | 570.1364 | 530.0029 | 511.779 | 665.4426 | 657.7229 | 671.4032 | 668.461 | 599.6558 | 537.5339 | 460.3258 | 481.9194 | 525.9574 | 590.8087 | 604.7639 | 609.4529 | 601.1055 | 609.1019 | 618.4436 | 479.2261 | 574.4384 | 615.3287
Total NSRS Responsibility | 2300.3967 | 2299.0129 | 2650.9968 | 2651.0162 | 2651.0774 | 2652.5323 | 3466.5129 | 3466.5065 | 3467.0323 | 3463.8679 | 2885.7937 | 2886.0871 | 2771.1419 | 2768.4129 | 2827.2678 | 2831.4452 | 2829.6807 | 2822.6723 | 2588.3158 | 2581.2923 | 2587.0968 | 2563.2787 | 2626.9987 | 2629.042
Between Jun 2023 and Jul 2023, there were 4 events that resulted in deployment of offline Non-Spin.
Note that, between Jun 2023 and Jul 2023, an average ~36 % of Non-Spin was provided using online capacity and by Quick Start Generation Resources. This type of Non-Spin is always available to SCED to dispatch (with an offer floor of $75) and no operator action is needed to deploy this capacity.
Deployment Start Time | Deployment End Time | Deployment Duration | Max Deployment (MW) | Reason
7/10/2023 19:21 | 7/10/2023 20:23 | 01:02:00 | 1080.9 | Available Headroom not sufficient for projected 30-minutes net load ramp
Key Takeaway: All recent Non-Spin deployments have been to meet 30-minute ramping needs. Non-Spin performed well in all deployments.