## Summary
Release Date: September 19, 2023
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Fall 2023
SUMMARY
The ERCOT region is expected to have sufficient installed generating capacity to serve peak demands in the upcoming fall season, October – November 2023, under normal system conditions. Under a scenario with average fall weather conditions, ERCOT anticipates a fall 2023 peak demand of 69,654 MW, which includes the impacts of rooftop solar and Large Flexible Load additions.
ERCOT anticipates there will be 99,727 MW of resource capacity available during fall peak demand hours. This amount includes 3,992 MW of operational battery storage resources plus 20 MW of planned additions; 1,053 MW of the storage resources are assumed to be available to provide energy during the highest fall net load hours. (Net load is total load minus wind and solar generation.) This battery storage capacity estimate serves as a proxy for the amount expected during a tight reserve hour for the upcoming fall and is an interim availability assumption to be used until a formal capacity contribution method is adopted for future SARA reports.
Note that a gas-steam unit (292 MW fall rating) is expected to be indefinitely mothballed on 11/24/23. Since the mothball date is well after the forecasted peak demand, the unit's capacity is assumed to be available for this SARA report. Additionally, another gas-steam unit (568 MW fall rating) is expected to be available for the winter season after changing from a summer-only operations schedule to year-around operations.
In addition to a Base scenario assuming normal system conditions, this SARA report includes six risk scenarios reflecting alternative assumptions for peak demand, unplanned thermal outages, and renewable output. One of the three elevated risk scenarios (low renewable output) results in the need for rotating outages. Among the three extreme risk scenarios, the most severe one — defined with a combination of high peak load, high unplanned thermal outages, and extreme low wind output — also results in a high risk of rotating outages.
Also of note is that the Energy Emergency Alert (EEA) levels are expected be modified as a result of Nodal Protocol Revision Request 1176, Update to EEA Trigger Levels, which is currently pending Public Utility Commission of Texas approval. As a result, the SARA report does not reflecting the pending changes.

## Forecasted Capacity
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2023
Release Date: September 19, 2023
Installed and Fall Capacity Ratings, MW
| Resources, MW | Installed Capacity Rating 1/ | Expected Capacity for Fall Peak Demand
| Thermal Resources, Installed Fall-rated Capacity | 75099.1 | 67511 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
| Hydroelectric, Peak Average Capacity Contribution | 574.9 | 388.9602 | Based on 69% of installed capacity for hydro resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Switchable Capacity Total | 3840.12 | 3639 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
| Less Switchable Capacity Unavailable to ERCOT | -572 | -568 | Based on survey responses of Switchable Resource owners
| Available Mothballed Capacity | 126 | 118 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
| Capacity from Private Use Networks | 9592 | 2517 | Average grid injection during the top 20 fall peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocols Section 10.3.2.4.
| Coastal Wind, Peak Average Capacity Contribution | 5436.37 | 1683.362 | Based on 31% of installed capacity for coastal wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Panhandle Wind, Peak Average Capacity Contribution | 4410.43 | 1807.157 | Based on 41% of installed capacity for panhandle wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Other Wind, Peak Average Capacity Contribution | 27955.03 | 9194.988 | Based on 33% of installed capacity for other wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Solar Utility-Scale, Peak Average Capacity Contribution | 18375.47 | 11662.976 | Based on 64% of rated capacity for solar resources (fall season) per Nodal Protocols Section 3.2.6.2.2
| Storage, Peak Average Capacity Contribution | 3971.65 | 1047.7502 | Based on the amount of battery storage capability assumed to be available for dispatch prior to the highest fall net load hours. (Net load is total load minus wind and solar generation, and represents the demand that must be met with other available resources.) This is an interim availability assumption for use until a formal capacity contribution method is adopted for future reports
| RMR Capacity to be under Contract | 0 | 0
| Capacity Pending Retirement | 0 | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocols Section 3.14.1.2
| Non-Synchronous Ties, Capacity Contribution | 1220 | 719.8 | Based on net imports during winter 2020/2021 (Winter Storm Uri) Energy Emergency Alert (EEA) intervals
| Planned Thermal Resources with Signed IA, Air Permits and Adequate Water Supplies | 0 | 0 | Based on in-service dates provided by developers
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 31% fall capacity contribution for coastal wind resources
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 41% fall capacity contribution for panhandle wind resources
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 33% fall capacity contribution for other wind resources
| Planned Solar Utility-Scale, Peak Average Capacity Contribution | 0 | 0 | Based on in-service dates provided by developers and 64% fall capacity contribution for solar resources
| Planned Storage, Peak Average Capacity Contribution | 19.9 | 5.2498 | Based on the amount of battery storage capability assumed to be available for dispatch prior to the highest fall net load hours. This is an interim availability assumption for use until a formal capacity contribution method is adopted for future reports
[a] Total Resources, MW |  | 150048.97 | 99727.2432
1/ Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer.

## Base & Elevated Risk Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2023
Release Date: September 19, 2023
Base & Elevated Reserve Capacity Risk Scenarios, MW
|  | Average Weather Peak Load / Typical Unplanned Outages / Typical Renewable Output | High Peak Load / Typical Unplanned Outages / Typical Renewable Output | Average Weather Peak Load / High Unplanned Outages / Typical Renewable Output | Average Weather Peak Load / Typical Unplanned Outages / Low Renewable Output
Scenario Adjustments
| [a] Peak Load (Baseline) | 68666 | 68666 | 68666 | 68666
| [b] Rooftop PV Forecast Reduction, MW | -395 | -561 | -395 | -395
| [c] Large Flexible Load Adjustment, MW | 1383 | 1383 | 1383 | 1383
| [d] Adjusted Peak Load Forecast, [a+b+c] | 69654 | 69488 | 69654 | 69654
| [e] Total Resources (from Forecast Capacity tab) | 99727.2432 | 99727.2432 | 99727.2432 | 99727.2432
Uses of Reserve Capacity
| High Peak Load Adjustment | 0 | 4021 | 0 | 0
| Typical Planned Outages, Thermal | 4820 | 4820 | 4820 | 4820
| Typical Unplanned Outages, Thermal | 12006 | 12006 | 12006 | 12006
| High Unplanned Outage Adjustment, Thermal | 0 | 0 | 6041 | 0
| Low Wind Output Reduction | 0 | 0 | 0 | 8875.507
| Low Solar Output Reduction | 0 | 0 | 0 | 6814.976
[f] Total Uses of Reserve Capacity |  | 16826 | 20847 | 22867 | 32516.483
Capacity Available For Operating Reserves
[g] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d), MW |  | 13247.2432 | 9392.2432 | 7206.2432 | -2443.2398
Less than 2,300 MW indicates risk of EEA1
[h] Pre-EEA Resources available for ERCOT deployment (Emergency Response Service, distribution voltage reduction, LFL curtailment) |  | 0 | 0 | 0 | 3148
[i] EEA Resources available for ERCOT deployment |  | 0 | 0 | 0 | 1634
[j] Capacity Available for Operating Reserves, Emergency Conditions (e+f), MW |  | 13247.2432 | 9392.2432 | 7206.2432 | 2338.7602
Less than 1,000 MW indicates risk of EEA3 Load Shed

## Extreme Risk Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2023
Release Date: September 19, 2023
Extreme Reserve Capacity Risk Scenarios, MW (One or a combination of extreme risk assumptions resulting in low probability, high impact outcomes)
|  | Extreme Peak Load / Typical Unplanned Outages / Typical Renewable Output | Extreme Peak Load / Extreme Unplanned Outages / Typical Renewable Output | High Peak Load / High Unplanned Outages / Extreme Low Wind Output
Scenario Adjustments
| [a] Peak Load (Baseline) | 68666 | 68666 | 68666
| [b] Rooftop PV Forecast Reduction, MW | -561 | -561 | -561
| [c] Large Flexible Load Adjustment, MW | 1383 | 1383 | 1383
| [d] Adjusted Peak Load Forecast, [a+b+c] | 69488 | 69488 | 69488
| [e] Total Resources (from Forecast Capacity tab) | 99727.2432 | 99727.2432 | 99727.2432
Uses of Reserve Capacity
| High/Extreme Peak Load Adjustment | 6197 | 6197 | 4021
| Typical Planned Outages, Thermal | 4820 | 4820 | 4820
| Typical Unplanned Outages, Thermal | 12006 | 12006 | 12006
| High/Extreme Unplanned Outage Adjustment, Thermal | 0 | 9489 | 6041
| Extreme Low Wind Output Adjustment | 0 | 0 | 12503.507
[f] Total Uses of Reserve Capacity |  | 23023 | 32512 | 39391.507
Capacity Available For Operating Reserves
[g] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d), MW |  | 7216.2432 | -2272.7568 | -9152.2638
Less than 2,300 MW indicates risk of EEA1
[h] Pre-EEA Resources available for ERCOT deployment (Emergency Response Service, distribution voltage reduction, LFL curtailment) |  | 0 | 3148 | 3148
[i] EEA Resources available for ERCOT deployment |  | 0 | 1634 | 1634
[j] Capacity Available for Operating Reserves, Emergency Conditions (e+f), MW |  | 7216.2432 | 2509.2432 | -4370.2638
Less than 1,000 MW indicates risk of EEA3 Load Shed

## FallCapacities
Unit Megawatt Capacities - Fall
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | INSTALLED CAPACITY RATING (MW) | FALL CAPACITY (MW) | NEW PLANNED PROJECT ADDITIONS TO REPORT
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1269 | 1222
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1269 | 1209
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1365 | 1323.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1365 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 615 | 603
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 615 | 603
11 | FAYETTE POWER U2 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 460 | 444
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 922 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 893 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 956.8 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 893 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 893 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 893 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 916.8 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 916.8 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 430 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 1008 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 174.6 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 174.6 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 734.1 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 734.1 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 614.6 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 653.99 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 | 24INR0427 | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 164
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 195 | 164
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 222 | 190
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 21 | 19
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
35 | BARNEY M DAVIS STG 1 (ENTERING INDEFINITE MOTHBALL STATUS ON 11/24/23, RMR STUDY PENDING) |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 352.8 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 351 | 322
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 178
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 178
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 242 | 236
40 | BEACHWOOD POWER STATION U1 |  | BCH_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
41 | BEACHWOOD POWER STATION U2 |  | BCH_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
42 | BEACHWOOD POWER STATION U3 |  | BCH_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
43 | BEACHWOOD POWER STATION U4 |  | BCH_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
44 | BEACHWOOD POWER STATION U5 |  | BCH_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
45 | BEACHWOOD POWER STATION U6 |  | BCH_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
46 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 160.5
47 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 160.5
48 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 188.7 | 159.5
49 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 94.95 | 83.3
50 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 254.15 | 221.5
51 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 168
52 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 168
53 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 275.57 | 270
54 | BROTMAN POWER STATION U1 |  | BTM_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
55 | BROTMAN POWER STATION U2 |  | BTM_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
56 | BROTMAN POWER STATION U3 |  | BTM_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
57 | BROTMAN POWER STATION U4 |  | BTM_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
58 | BROTMAN POWER STATION U5 |  | BTM_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
59 | BROTMAN POWER STATION U6 |  | BTM_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
60 | BROTMAN POWER STATION U7 |  | BTM_UNIT7 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
61 | BROTMAN POWER STATION U8 |  | BTM_UNIT8 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
62 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-GT | WEST | 1987 | 75 | 75
63 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-GT | WEST | 1987 | 75 | 75
64 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 46.5
65 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 46.5
66 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 46.5
67 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 46.5
68 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 168
69 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 168
70 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 182
71 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 765 | 745
72 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 765 | 749
73 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 84
74 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 76.9
75 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 84.4
76 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 77.8
77 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 105 | 103.7
78 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 108.8 | 108
79 | COLORADO BEND II CTG 7 |  | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 332.5
80 | COLORADO BEND II CTG 8 |  | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 338.2
81 | COLORADO BEND II STG 9 |  | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 508.5 | 482.8
82 | COLORADO BEND ENERGY CENTER CTG 11 |  | CBEC_GT11 | WHARTON | GAS-GT | SOUTH | 2023 | 41.7 | 39
83 | COLORADO BEND ENERGY CENTER CTG 12 |  | CBEC_GT12 | WHARTON | GAS-GT | SOUTH | 2023 | 41.7 | 39
84 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 168
85 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 163
86 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 163
87 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2002 | 150 | 128
88 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 48 | 46.5
89 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 50 | 48.5
90 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 120 | 108.5
91 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 49
92 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 49
93 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 49
94 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 49
95 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 72
96 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 71
97 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 70
98 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 71
99 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 194 | 194
100 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 206 | 206
101 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 194 | 194
102 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 206 | 206
103 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 199 | 179
104 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 290 | 290
105 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
106 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
107 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
108 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.45 | 56.5
109 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 153.6
110 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 179.35 | 153.6
111 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 202 | 195
112 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 212
113 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 140 | 117
114 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 38
115 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 38
116 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 38
117 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 38.29 | 38
118 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 173
119 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 173
120 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 204 | 186
121 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 169
122 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 161
123 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 161
124 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 169
125 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 161
126 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 161
127 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 409
128 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 409
129 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 155.2
130 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 155.2
131 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 155.4
132 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 155.4
133 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 177.6
134 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 176.5
135 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 129 | 119
136 | FRONTERA ENERGY CENTER CTG 1 |  | FRONT_EC_CT1 | HIDALGO | GAS-CC | SOUTH | 2023 | 177 | 177
137 | FRONTERA ENERGY CENTER CTG 2 |  | FRONT_EC_CT2 | HIDALGO | GAS-CC | SOUTH | 2023 | 177 | 177
138 | FRONTERA ENERGY CENTER STG |  | FRONT_EC_ST | HIDALGO | GAS-CC | SOUTH | 2023 | 184.5 | 184.5
139 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 239 | 239
140 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 390 | 390
141 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 58
142 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 55
143 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 55
144 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 48
145 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 63
146 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 57
147 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
148 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
149 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
150 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 152
151 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 151
152 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 100 | 75
153 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
154 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
155 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
156 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
157 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 200
158 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 200
159 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395 | 375
160 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435 | 435
161 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435 | 435
162 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 214
163 | HAYS ENERGY FACILITY CSG 2 | 22INR0586 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 258 | 216
164 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 260 | 215
165 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 218
166 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 145
167 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 145
168 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 198.05 | 173
169 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150
170 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150
171 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 167
172 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 167
173 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 320.6 | 285
174 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 320.6 | 295
175 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 185 | 163
176 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 107 | 106
177 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 397 | 392
178 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 531 | 523
179 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 161
180 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153
181 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153
182 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 161
183 | LAMAR ENERGY CENTER STG 1 | 23INR0486 | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
184 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
185 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 93
186 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 90.2
187 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
188 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
189 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
190 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
191 | LIGNIN (CHAMON 2) U1 |  | LIG_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 42.5
192 | LIGNIN (CHAMON 2) U2 |  | LIG_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 42.5
193 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 178
194 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 172
195 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 204 | 188
196 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 212.5
197 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 212.5
198 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 258.4 | 254.9
199 | MIDLOTHIAN ENERGY FACILITY CTG 1 | 23INR0489 | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 233
200 | MIDLOTHIAN ENERGY FACILITY CTG 2 | 21INR0534 | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 231
201 | MIDLOTHIAN ENERGY FACILITY CTG 3 | 22INR0543 | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 230
202 | MIDLOTHIAN ENERGY FACILITY CTG 4 | 22INR0523 | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 247 | 233
203 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 245
204 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 247
205 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 68
206 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
207 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
208 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 68
209 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 69
210 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 69
211 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122 | 122
212 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118 | 118
213 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568 | 568
214 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
215 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
216 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 351 | 322
217 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 445 | 420
218 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 435 | 410
219 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 176 | 167.5
220 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 176 | 159
221 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 176 | 167.5
222 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 176 | 159
223 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 224 | 207.2
224 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 224 | 207.2
225 | OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 46.5
226 | OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 46.5
227 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 217
228 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 216
229 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1 | 307
230 | PANDA TEMPLE I POWER CTG 1 | 22INR0533 | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 232 | 219
231 | PANDA TEMPLE I POWER CTG 2 | 22INR0533 | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 232 | 206
232 | PANDA TEMPLE I POWER STG 1 | 22INR0533 | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1 | 323
233 | PANDA TEMPLE II POWER CTG 1 | 23INR0524 | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.5
234 | PANDA TEMPLE II POWER CTG 2 | 23INR0524 | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.5
235 | PANDA TEMPLE II POWER STG 1 | 23INR0524 | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1 | 353.1
236 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 86
237 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 86
238 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 90 | 79
239 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 168
240 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 168
241 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 195.5 | 168
242 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
243 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
244 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
245 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
246 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64
247 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 89.4 | 66
248 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 89.4 | 65
249 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 89.4 | 65
250 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 89.4 | 66
251 | PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
252 | PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
253 | PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
254 | PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
255 | PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
256 | PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
257 | PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
258 | PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
259 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 61
260 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 62
261 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 52
262 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 56
263 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 56
264 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 55
265 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 25 | 21.5
266 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 43.2 | 36
267 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 81
268 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 81
269 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 80
270 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 80
271 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98.1 | 98
272 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98.1 | 98
273 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 104
274 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 115.25 | 104
275 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 74.98 | 75
276 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 120 | 120
277 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 216.01 | 208
278 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 95 | 95
279 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 113.64 | 107
280 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 156.6 | 146
281 | RABBS POWER STATION U1 |  | RAB_UNIT1 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
282 | RABBS POWER STATION U2 |  | RAB_UNIT2 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
283 | RABBS POWER STATION U3 |  | RAB_UNIT3 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
284 | RABBS POWER STATION U4 |  | RAB_UNIT4 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
285 | RABBS POWER STATION U5 |  | RAB_UNIT5 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
286 | RABBS POWER STATION U6 |  | RAB_UNIT6 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
287 | RABBS POWER STATION U7 |  | RAB_UNIT7 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
288 | RABBS POWER STATION U8 |  | RAB_UNIT8 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
289 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
290 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
291 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
292 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
293 | RIO NOGALES POWER CTG 1 | 23INR0483 | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2023 | 190 | 164.8
294 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 164
295 | RIO NOGALES POWER CTG 3 | 24INR0602 | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 188.7 | 164
296 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 373.16 | 307
297 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
298 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 51
299 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
300 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 41.98 | 40
301 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 83
302 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 83
303 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
304 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
305 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
306 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
307 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 198.9 | 151
308 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47
309 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47
310 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 191 | 148
311 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 60.5 | 46
312 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 50 | 38
313 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 25 | 20
314 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 136 | 130
315 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 136 | 135
316 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 351 | 336
317 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 26.7 | 26.7
318 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 26.7 | 26.7
319 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 177 | 167
320 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 502 | 502
321 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 16.32 | 14
322 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 556 | 56
323 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 56 | 56
324 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 56 | 56
325 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 56 | 56
326 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 56 | 56
327 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 56 | 56
328 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 56
329 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 62 | 56
330 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
331 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
332 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
333 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
334 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
335 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
336 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110
337 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110
338 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 99.1
339 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 99.1
340 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 99.1
341 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 143.65 | 131.5
342 | TEXAS GULF SULPHUR CTG 1 | 24INR0605 | TGS_GT01 | WHARTON | GAS-GT | SOUTH | 1985 | 94 | 68.5
343 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 239 | 235
344 | TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
345 | TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
346 | TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
347 | TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
348 | TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
349 | TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
350 | TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
351 | TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
352 | TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
353 | TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
354 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
355 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
356 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
357 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 47
358 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 225 | 217
359 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 240 | 230
360 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 420 | 412
361 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 46.5
362 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 46.5
363 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 46.5
364 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 46.5
365 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 196.86 | 171
366 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 180.2 | 132
367 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 16.32 | 13
368 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
369 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
370 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 299.2 | 246
371 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 580.5 | 536
372 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
373 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
374 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20 | 20
375 | WICHITA FALLS STG 4 (ENTERING INDEFINITE MOTHBALL STATUS ON 11/1/23) |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 20 | 17
376 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
377 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
378 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
379 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
380 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 275 | 245.4
381 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 275 | 245.4
382 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 298 | 298
383 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 245.3
384 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 245.3
385 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 300 | 270
386 | WOLF HOLLOW 2 CTG 4 |  | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 360 | 330.8
387 | WOLF HOLLOW 2 CTG 5 |  | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 360 | 331.3
388 | WOLF HOLLOW 2 STG 6 |  | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 511.2 | 458.8
389 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 116.45 | 105
390 | BIOENERGY AUSTIN-WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8 | 9.8
391 | BIOENERGY TEXAS-COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6
392 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2
393 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4
394 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2
395 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4
396 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2
397 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4
398 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2
399 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8
400 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 75099.1 | 67511
401
402 | Operational Resources - Synchronized but not Approved for Commercial Operations (Thermal)
403 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 0 | 0
404
405 | Operational Capacity Thermal Unavailable due to Extended Outage or Derate |  | THERMAL_UNAVAIL |  |  |  |  | 0 | 0
406 | Operational Capacity Thermal Total |  | THERMAL_OPERATIONAL |  |  |  |  | 75099.1 | 67511
407
408 | Operational Resources (Hydro)
409 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9
410 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9
411 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 8
412 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9
413 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
414 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
415 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 18.3 | 17
416 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 50.8 | 49.5
417 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 50.8 | 49.5
418 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6 | 9.6
419 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
420 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
421 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
422 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29
423 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29
424 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6 | 6
425 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 15 | 14
426 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21 | 21
427 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 19.8 | 20
428 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
429 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
430 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
431 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22 | 22
432 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22 | 22
433 | Operational Capacity Total (Hydro) | [6 empty] | 567.7 | 557.4
434 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 567.7 | 384
435
436 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
437 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4 | 1.4
438 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7
439 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6
440 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2 | 2.2
441 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 14.9 | 14.9
442 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  |  |  |  | 14.9 | 10.2648
443
444 | Operational Capacity Hydroelectric Unavailable due to Extended Outage or Derate |  | HYDRO_UNAVAIL |  |  |  |  | -7.7 | -5.3046
445 | Operational Capacity Hydroelectric Total |  | HYDRO_OPERATIONAL |  |  |  |  | 574.9 | 388.9602
446
447 | Operational Resources (Switchable)
448 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
449 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
450 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
451 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 195
452 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 195
453 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
454 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
455 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
456 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400 | 400
457 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 179 | 162
458 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 179
459 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 179 | 178
460 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 389
461 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 154
462 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 151
463 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 312
464 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 149
465 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 150
466 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 318 | 317
467 | Switchable Capacity Total | [6 empty] | 3840.12 | 3639
468
469 | Switchable Capacity Unavailable to ERCOT
470 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56 | -56
471 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56 | -56
472 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56 | -56
473 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -202 | -200
474 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -202 | -200
475 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101_UNAVAIL | FANNIN | GAS-CC | NORTH | 2003 | 0 | 0
476 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -572 | -568
477
478 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 126 | 118
479
480 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  |  |  |  | 9592 | 2588
481 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST | [5 empty] | -71
482
483 | Operational Resources (Wind)
484 | WESTERN TRAIL WIND (AJAX WIND) U1 |  | AJAXWIND_UNIT1 | WILBARGER | WIND-O | WEST | 2022 | 225.6 | 225.6
485 | WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WILBARGER | WIND-O | WEST | 2022 | 141 | 141
486 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7 | 36.7
487 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8 | 35.8
488 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7 | 177.7
489 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.83 | 99.8
490 | AQUILLA LAKE WIND U1 |  | AQUILLA_U1_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 13.9 | 13.9
491 | AQUILLA LAKE WIND U2 |  | AQUILLA_U1_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 135.4 | 135.4
492 | AQUILLA LAKE 2 WIND U1 |  | AQUILLA_U2_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 7 | 7
493 | AQUILLA LAKE 2 WIND U2 |  | AQUILLA_U2_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 143.8 | 143.8
494 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.12 | 180.1
495 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.64 | 145.6
496 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.26 | 199.3
497 | BLACKJACK CREEK WIND U1 |  | BLACKJAK_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 120 | 120
498 | BLACKJACK CREEK WIND U2 |  | BLACKJAK_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 120 | 120
499 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100
500 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102
501 | BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | ANDREWS | WIND-O | WEST | 2021 | 90.2 | 90.2
502 | BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | ANDREWS | WIND-O | WEST | 2021 | 70.5 | 70.5
503 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120 | 120
504 | BLUE SUMMIT WIND 1 A | 22INR0550 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 132.84 | 132.8
505 | BLUE SUMMIT WIND 1 B | 22INR0550 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 6.96 | 6.9
506 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 6.9 | 6.9
507 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 92.5 | 92.5
508 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.7 | 13.4
509 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 186.5 | 182.4
510 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162 | 162
511 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.85 | 149.8
512 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120
513 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108
514 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9 | 44.9
515 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7 | 55.7
516 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6 | 120.6
517 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5 | 115.5
518 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117 | 117
519 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2 | 170.2
520 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 89 | 88
521 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 91 | 90
522 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2 | 115.2
523 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4 | 122.4
524 | CACTUS FLATS WIND U1 |  | CFLATS_U1 | CONCHO | WIND-O | WEST | 2022 | 148.4 | 148.4
525 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1 | 123.1
526 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165
527 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 134.42 | 130.5
528 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 123.6 | 120
529 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1 | 210.1
530 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7 | 231.7
531 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5 | 149.5
532 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9 | 200.9
533 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | STERLING | WIND-O | WEST | 2008 | 121.5 | 121.5
534 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75
535 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75 | 75
536 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.25 | 173.3
537 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5 | 126.5
538 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6
539 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4
540 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4 | 50.4
541 | CRANELL WIND |  | CRANELL_UNIT1 | REFUGIO | WIND-C | COASTAL | 2022 | 220 | 220
542 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
543 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
544 | DESERT SKY WIND 1 A | 17INR0070 | DSKYWND1_UNIT_1A | PECOS | WIND-O | WEST | 2022 | 65.79 | 53.1
545 | DESERT SKY WIND 1 B | 17INR0070 | DSKYWND2_UNIT_2A | PECOS | WIND-O | WEST | 2022 | 65.79 | 50.4
546 | DESERT SKY WIND 2 A | 17INR0070 | DSKYWND1_UNIT_1B | PECOS | WIND-O | WEST | 2022 | 23.93 | 18.7
547 | DESERT SKY WIND 2 B | 17INR0070 | DSKYWND2_UNIT_2B | PECOS | WIND-O | WEST | 2022 | 14.74 | 8
548 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
549 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
550 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 101.2 | 98
551 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 99 | 96
552 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 121.9 | 121.9
553 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2016 | 101.31 | 98.9
554 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2016 | 134.29 | 131.1
555 | EL ALGODON ALTO W U1 |  | ALGODON_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 171.6 | 171.6
556 | EL ALGODON ALTO W U2 |  | ALGODON_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 28.6 | 28.6
557 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2 | 25.2
558 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2 | 163.2
559 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200 | 200
560 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8 | 79.8
561 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6 | 75.6
562 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.48 | 186.5
563 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8 | 163.8
564 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2 | 124.2
565 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80 | 80
566 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6 | 69.6
567 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6 | 148.6
568 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82 | 82
569 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76 | 76
570 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4 | 107.4
571 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8 | 103.8
572 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 21INR0532 | BRAZ_WND_BRAZ_WND1 | SCURRY | WIND-O | WEST | 2023 | 120 | 120
573 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 21INR0532 | BRAZ_WND_BRAZ_WND2 | SCURRY | WIND-O | WEST | 2023 | 62.4 | 62.4
574 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
575 | GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 98.7 | 98.7
576 | GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 126.9 | 126.9
577 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
578 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
579 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.93 | 119.9
580 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 165.6 | 163.5
581 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2014 | 99.9 | 99.9
582 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2014 | 100 | 100
583 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5 | 152.5
584 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5 | 147.5
585 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52 | 52
586 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98 | 98
587 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100 | 100
588 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4 | 50.4
589 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46 | 46
590 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 51.9 | 52
591 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
592 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.4 | 122.5
593 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
594 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.5 | 127.6
595 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.5 | 101.6
596 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 134.81 | 131.1
597 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 101.69 | 98.9
598 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230 | 230
599 | HORSE HOLLOW WIND 2 | 17INR0053 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184 | 184
600 | HORSE HOLLOW WIND 3 | 17INR0053 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4 | 241.4
601 | HORSE HOLLOW WIND 4 | 17INR0053 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115 | 115
602 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95 | 95
603 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102 | 102
604 | INDIAN MESA WIND | 18INR0069 | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8 | 91.8
605 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.69 | 19.7
606 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230 | 230
607 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96 | 96
608 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74 | 74
609 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30 | 30
610 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.15 | 146.2
611 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.55 | 153.6
612 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
613 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
614 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.42 | 100.4
615 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2014 | 110 | 110
616 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
617 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
618 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5 | 40.5
619 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
620 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 159.96 | 160
621 | LAS MAJADAS WIND U1 |  | LMAJADAS_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 110 | 110
622 | LAS MAJADAS WIND U2 |  | LMAJADAS_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 24 | 24
623 | LAS MAJADAS WIND U3 |  | LMAJADAS_UNIT3 | WILLACY | WIND-C | COASTAL | 2023 | 138.6 | 138.6
624 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7 | 183.7
625 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.26 | 106.3
626 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.85 | 103.8
627 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194 | 194
628 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98 | 98
629 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100 | 100
630 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
631 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
632 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48 | 48
633 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51 | 51
634 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5 | 25.5
635 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24 | 24
636 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200 | 200
637 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200 | 200
638 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110 | 110
639 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1
640 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6
641 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.83 | 99.8
642 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.46 | 103.5
643 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
644 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
645 | MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | CONCHO | WIND-O | WEST | 2022 | 201.6 | 201.6
646 | MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | CONCHO | WIND-O | WEST | 2022 | 11.1 | 11.1
647 | MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | CONCHO | WIND-O | WEST | 2022 | 33.6 | 33.6
648 | MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | CONCHO | WIND-O | WEST | 2022 | 22.2 | 22.2
649 | MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | CONCHO | WIND-O | WEST | 2022 | 71.4 | 71.4
650 | MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | CONCHO | WIND-O | WEST | 2022 | 33.3 | 33.3
651 | MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | CONCHO | WIND-O | WEST | 2022 | 22 | 22
652 | MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | CONCHO | WIND-O | WEST | 2022 | 20 | 20
653 | MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | CONCHO | WIND-O | WEST | 2022 | 76.8 | 76.8
654 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150 | 150
655 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
656 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
657 | MIAMI WIND G1 |  | MIAM1_G1 | ROBERTS | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
658 | MIAMI WIND G2 |  | MIAM1_G2 | ROBERTS | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
659 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8 | 162.8
660 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2017 | 196.6 | 196.6
661 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.61 | 92.6
662 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60 | 60
663 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 54.6 | 54.6
664 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2 | 151.2
665 | OVEJA WIND U1 |  | OVEJA_G1 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
666 | OVEJA WIND U2 |  | OVEJA_G2 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
667 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9 | 144.9
668 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2
669 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2
670 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.19 | 94.2
671 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6 | 96.6
672 | PANTHER CREEK WIND 1 | 24INR0578 | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5 | 142.5
673 | PANTHER CREEK WIND 2 | 24INR0582 | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5 | 115.5
674 | PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | HOWARD | WIND-O | WEST | 2022 | 106.92 | 106.9
675 | PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | HOWARD | WIND-O | WEST | 2022 | 108.54 | 108.5
676 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.85 | 179.9
677 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.12 | 200.1
678 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7 | 91.7
679 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86 | 85.8
680 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8
681 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6
682 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8
683 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2 | 151.2
684 | PYRON WIND 1 | 23INR0525 | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5 | 121.5
685 | PYRON WIND 2 | 23INR0525 | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5 | 127.5
686 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
687 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
688 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 104.6
689 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 102.7
690 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6 | 89.6
691 | RELOJ DEL SOL WIND U1 |  | RELOJ_UNIT1 | ZAPATA | WIND-O | SOUTH | 2022 | 55.4 | 55.4
692 | RELOJ DEL SOL WIND U2 |  | RELOJ_UNIT2 | ZAPATA | WIND-O | SOUTH | 2022 | 48 | 48
693 | RELOJ DEL SOL WIND U3 |  | RELOJ_UNIT3 | ZAPATA | WIND-O | SOUTH | 2022 | 83.1 | 83.1
694 | RELOJ DEL SOL WIND U4 |  | RELOJ_UNIT4 | ZAPATA | WIND-O | SOUTH | 2022 | 22.8 | 22.8
695 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9 | 121.9
696 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.44 | 27.4
697 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114 | 114
698 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95 | 95
699 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150 | 150
700 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
701 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
702 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160 | 160
703 | SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
704 | SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
705 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64 | 64
706 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110 | 110
707 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2016 | 95.25 | 95.2
708 | SAND BLUFF WIND U1 | 20INR0296 | MCDLD_SB1_2 | GLASSCOCK | WIND-O | WEST | 2022 | 71.4 | 71.4
709 | SAND BLUFF WIND U2 |  | MCDLD_SB3_282 | GLASSCOCK | WIND-O | WEST | 2022 | 14.1 | 14.1
710 | SAND BLUFF WIND U3 |  | MCDLD_SB4_G87 | GLASSCOCK | WIND-O | WEST | 2022 | 4 | 4
711 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150 | 150
712 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78 | 78
713 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.24 | 30.2
714 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.05 | 226.1
715 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1 | 204.1
716 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132 | 132
717 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8 | 52.8
718 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102 | 102
719 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98 | 98
720 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5 | 148.5
721 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8 | 151.8
722 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 101.2 | 98.2
723 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 160.95 | 161
724 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98 | 98
725 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96 | 96
726 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 123.6 | 120
727 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201 | 201
728 | STEPHENS RANCH WIND 1 | 25INR0439 | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 211.2 | 211.2
729 | STEPHENS RANCH WIND 2 | 25INR0439 | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 164.7 | 164.7
730 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5 | 42.5
731 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8 | 16.8
732 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8 | 110.8
733 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 33.6 | 33.6
734 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 118.6 | 118.6
735 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125 | 125
736 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112 | 112
737 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 85 | 85
738 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150 | 150
739 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150 | 150
740 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.72 | 27.7
741 | TEXAS BIG SPRING WIND B (ENTERING INDEFINITE MOTHBALL STATUS ON 1/1/24) |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6 | 6.6
742 | TG EAST WIND U1 |  | TRUSGILL_UNIT1 | KNOX | WIND-O | WEST | 2022 | 42 | 42
743 | TG EAST WIND U2 |  | TRUSGILL_UNIT2 | KNOX | WIND-O | WEST | 2022 | 44.8 | 44.8
744 | TG EAST WIND U3 |  | TRUSGILL_UNIT3 | KNOX | WIND-O | WEST | 2022 | 42 | 42
745 | TG EAST WIND U4 |  | TRUSGILL_UNIT4 | KNOX | WIND-O | WEST | 2022 | 207.2 | 207.2
746 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150 | 150
747 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23 | 23
748 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5 | 127.5
749 | TRENT WIND 1 A | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 38.25 | 38.3
750 | TRENT WIND 1 B |  | TRENT_UNIT_1B | NOLAN | WIND-O | WEST | 2018 | 15.59 | 15.6
751 | TRENT WIND 2 |  | TRENT_UNIT_2 | NOLAN | WIND-O | WEST | 2018 | 50.49 | 50.5
752 | TRENT WIND 3 A |  | TRENT_UNIT_3A | NOLAN | WIND-O | WEST | 2018 | 38.25 | 38.3
753 | TRENT WIND 3 B |  | TRENT_UNIT_3B | NOLAN | WIND-O | WEST | 2018 | 13.79 | 13.8
754 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4 | 103.4
755 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6 | 94.6
756 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2 | 2
757 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 174.6 | 169.5
758 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2016 | 125.6 | 125.6
759 | VENADO WIND U1 |  | VENADO_UNIT1 | ZAPATA | WIND-O | SOUTH | 2021 | 105 | 105
760 | VENADO WIND U2 |  | VENADO_UNIT2 | ZAPATA | WIND-O | SOUTH | 2021 | 96.6 | 96.6
761 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12 | 12
762 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2 | 7.2
763 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
764 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22 | 22
765 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
766 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
767 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.91 | 114.9
768 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.35 | 142.3
769 | WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 116.6 | 116.6
770 | WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 123.2 | 123.2
771 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 59.8 | 57
772 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.34 | 92.3
773 | WHITE MESA WIND U1 |  | WHMESA_UNIT1 | CROCKETT | WIND-O | WEST | 2022 | 152.3 | 152.3
774 | WHITE MESA 2 WIND U1 |  | WHMESA_UNIT2_23 | CROCKETT | WIND-O | WEST | 2022 | 13.92 | 13.9
775 | WHITE MESA 2 WIND U2 |  | WHMESA_UNIT2_28 | CROCKETT | WIND-O | WEST | 2022 | 183.3 | 183.3
776 | WHITE MESA 2 WIND U3 |  | WHMESA_UNIT3_23 | CROCKETT | WIND-O | WEST | 2022 | 18.56 | 18.6
777 | WHITE MESA 2 WIND U4 |  | WHMESA_UNIT3_28 | CROCKETT | WIND-O | WEST | 2022 | 132.54 | 132.5
778 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
779 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
780 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5 | 199.5
781 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.62 | 67.6
782 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30 | 30
783 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5 | 112.5
784 | Operational Capacity Total (Wind) | [6 empty] | 32129.53 | 32029.7
785
786 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 5134.87 | 5128.7
787 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 100 | 31
788
789 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4410.43 | 4407.7
790 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 100 | 41
791
792 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 22584.23 | 22493.3
793 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 100 | 33
794
795 | Operational Resources (Wind) - Synchronized but not Approved for Commercial Operations
796 | AGUAYO WIND U1 | 20INR0250 | AGUAYO_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 193.5 | 192.9
797 | ANCHOR WIND U1 | 21INR0546 | ANCHOR_WIND1 | CALLAHAN | WIND-O | WEST | 2023 | 16 | 16
798 | ANCHOR WIND U2 | 21INR0387 | ANCHOR_WIND2 | CALLAHAN | WIND-O | WEST | 2023 | 98.9 | 98.9
799 | ANCHOR WIND U3 | 21INR0539 | ANCHOR_WIND3 | CALLAHAN | WIND-O | WEST | 2023 | 90 | 90
800 | ANCHOR WIND U4 | 21INR0539 | ANCHOR_WIND4 | CALLAHAN | WIND-O | WEST | 2023 | 38.7 | 38.7
801 | ANCHOR WIND U5 | 22INR0562 | ANCHOR_WIND5 | CALLAHAN | WIND-O | WEST | 2023 | 19.3 | 19.3
802 | APPALOOSA RUN WIND U1 | 20INR0249 | APPALOSA_UNIT1 | UPTON | WIND-O | WEST | 2023 | 157.9 | 157.9
803 | APPALOOSA RUN WIND U2 | 20INR0249 | APPALOSA_UNIT2 | UPTON | WIND-O | WEST | 2023 | 13.9 | 13.9
804 | APOGEE WIND U1 | 21INR0467 | APOGEE_UNIT1 | THROCKMORTON | WIND-O | WEST | 2023 | 25 | 25
805 | APOGEE WIND U2 | 21INR0467 | APOGEE_UNIT2 | THROCKMORTON | WIND-O | WEST | 2023 | 14 | 14
806 | APOGEE WIND U3 | 21INR0467 | APOGEE_UNIT3 | THROCKMORTON | WIND-O | WEST | 2023 | 30.2 | 30.2
807 | APOGEE WIND U4 | 21INR0467 | APOGEE_UNIT4 | THROCKMORTON | WIND-O | WEST | 2023 | 115 | 115
808 | APOGEE WIND U5 | 21INR0467 | APOGEE_UNIT5 | THROCKMORTON | WIND-O | WEST | 2023 | 110 | 110
809 | APOGEE WIND U6 | 21INR0467 | APOGEE_UNIT6 | THROCKMORTON | WIND-O | WEST | 2023 | 24 | 24
810 | APOGEE WIND U7 | 21INR0467 | APOGEE_UNIT7 | THROCKMORTON | WIND-O | WEST | 2023 | 75 | 75
811 | BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | CALLAHAN | WIND-O | WEST | 2023 | 195 | 195
812 | BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | CALLAHAN | WIND-O | WEST | 2023 | 145 | 145
813 | BOARD CREEK WP U1 | 21INR0324 | BOARDCRK_UNIT1 | NAVARRO | WIND-O | NORTH | 2023 | 108.8 | 108.8
814 | BOARD CREEK WP U2 | 21INR0324 | BOARDCRK_UNIT2 | NAVARRO | WIND-O | NORTH | 2023 | 190.4 | 190.4
815 | COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | SCURRY | WIND-O | WEST | 2023 | 90 | 90
816 | COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | SCURRY | WIND-O | WEST | 2023 | 26.6 | 26.6
817 | COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | SCURRY | WIND-O | WEST | 2023 | 126 | 126
818 | EL SUAZ RANCH U1 | 20INR0097 | ELSAUZ_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 153 | 153
819 | EL SUAZ RANCH U2 | 20INR0097 | ELSAUZ_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 148.5 | 148.5
820 | FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 130.2 | 130.2
821 | FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 84 | 84
822 | FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | BEE | WIND-O | SOUTH | 2023 | 54 | 54
823 | HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | GLASSCOCK | WIND-O | WEST | 2023 | 162.1 | 162.1
824 | INERTIA WIND U1 | 22INR0326 | INRT_W_UNIT1 | HASKELL | WIND-O | WEST | 2023 | 67.68 | 67.7
825 | INERTIA WIND U2 | 22INR0326 | INRT_W_UNIT2 | HASKELL | WIND-O | WEST | 2023 | 27.72 | 27.7
826 | INERTIA WIND U3 | 22INR0326 | INRT_W_UNIT3 | HASKELL | WIND-O | WEST | 2023 | 205.86 | 205.9
827 | LACY CREEK WIND U1 | 18INR0043 | LACY_CRK_UNIT1 | GLASSCOCK | WIND-O | WEST | 2023 | 135.4 | 135.4
828 | LACY CREEK WIND U2 | 18INR0043 | LACY_CRK_UNIT2 | GLASSCOCK | WIND-O | WEST | 2023 | 15.12 | 15.1
829 | LACY CREEK WIND U3 | 18INR0043 | LACY_CRK_UNIT3 | GLASSCOCK | WIND-O | WEST | 2023 | 138.2 | 138.2
830 | LACY CREEK WIND U4 | 18INR0043 | LACY_CRK_UNIT4 | GLASSCOCK | WIND-O | WEST | 2023 | 12.6 | 12.6
831 | MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | NOLAN | WIND-O | WEST | 2023 | 182.4 | 182.4
832 | MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | STARR | WIND-O | SOUTH | 2023 | 201.6 | 201.6
833 | PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | LIMESTONE | WIND-O | NORTH | 2023 | 153 | 153
834 | PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | LIMESTONE | WIND-O | NORTH | 2023 | 147 | 147
835 | PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 187.2 | 187.2
836 | PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | MILLS | WIND-O | NORTH | 2023 | 115.2 | 115.2
837 | VORTEX WIND U1 | 20INR0120 | VORTEX_WIND1 | THROCKMORTON | WIND-O | WEST | 2023 | 153.6 | 153.6
838 | VORTEX WIND U2 | 20INR0120 | VORTEX_WIND2 | THROCKMORTON | WIND-O | WEST | 2023 | 24.2 | 24.2
839 | VORTEX WIND U3 | 20INR0120 | VORTEX_WIND3 | THROCKMORTON | WIND-O | WEST | 2023 | 158.4 | 158.4
840 | VORTEX WIND U4 | 20INR0120 | VORTEX_WIND4 | THROCKMORTON | WIND-O | WEST | 2023 | 14 | 14
841 | WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | FISHER | WIND-O | WEST | 2023 | 209.4 | 209.4
842 | WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | FISHER | WIND-O | WEST | 2023 | 209.5 | 209.5
843 | WILDWIND U1 | 20INR0033 | WILDWIND_UNIT1 | COOKE | WIND-O | NORTH | 2023 | 18.38 | 18.4
844 | WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | COOKE | WIND-O | NORTH | 2023 | 48 | 48
845 | WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | COOKE | WIND-O | NORTH | 2023 | 6.3 | 6.3
846 | WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | COOKE | WIND-O | NORTH | 2023 | 54.6 | 54.6
847 | WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | COOKE | WIND-O | NORTH | 2023 | 52.8 | 52.8
848 | YOUNG WIND U1 | 21INR0401 | YNG_WND_UNIT1 | YOUNG | WIND-O | WEST | 2023 | 197.4 | 197.4
849 | YOUNG WIND U2 | 21INR0401 | YNG_WND_UNIT2 | YOUNG | WIND-O | WEST | 2023 | 152.28 | 152.3
850 | YOUNG WIND U3 | 21INR0401 | YNG_WND_UNIT3 | YOUNG | WIND-O | WEST | 2023 | 149.46 | 149.5
851 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 5672.3 | 5671.8
852
853 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Coastal Counties) |  | WIND_SYNCHRONIZED_C |  |  |  |  | 301.5 | 301.5
854 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_SYNC_PEAK_PCT_C | % |  |  |  | 100 | 31
855
856 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Panhandle Counties) |  | WIND_SYNCHRONIZED_P |  |  |  |  | 0 | 0
857 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_SYNC_PEAK_PCT_P | % |  |  |  | 100 | 41
858
859 | Operational Wind Capacity Synchronized but not Approved for Commercial Operations Sub-total (Other Counties) |  | WIND_SYNCHRONIZED_O |  |  |  |  | 5370.8 | 5370.3
860 | Wind Peak Average Capacity Percentage (Other) |  | WIND_SYNC_PEAK_PCT_O | % |  |  |  | 100 | 33
861
862 | Operational Resources (Solar)
863 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10
864 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10 | 10
865 | ANSON SOLAR U1 |  | ANSON1_UNIT1 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
866 | ANSON SOLAR U2 |  | ANSON1_UNIT2 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
867 | ARAGORN SOLAR |  | ARAGORN_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 188.2 | 185
868 | AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | HASKELL | SOLAR | WEST | 2021 | 74.9 | 74.9
869 | AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | HASKELL | SOLAR | WEST | 2021 | 153.5 | 153.5
870 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1 | 1
871 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 50 | 49.1
872 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6
873 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3
874 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30 | 30
875 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100 | 100
876 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15 | 15
877 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6
878 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50 | 50
879 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
880 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
881 | BPL FILES SOLAR |  | FILESSLR_PV1 | HILL | SOLAR | NORTH | 2023 | 146.09 | 145
882 | BRIGHTSIDE SOLAR |  | BRIGHTSD_UNIT1 | BEE | SOLAR | SOUTH | 2023 | 53.4 | 50
883 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
884 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
885 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
886 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
887 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180
888 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10 | 10
889 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10 | 10
890 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5 | 5
891 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7 | 125.7
892 | CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | WEBB | SOLAR | SOUTH | 2021 | 202.6 | 202.6
893 | DANCIGER SOLAR U1 |  | DAG_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100
894 | DANCIGER SOLAR U2 |  | DAG_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100
895 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144 | 144
896 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10 | 10
897 | ELARA SOLAR |  | ELARA_SL_UNIT1 | FRIO | SOLAR | SOUTH | 2022 | 132.4 | 132.4
898 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) |  | EGROVESL_UNIT1 | CRANE | SOLAR | WEST | 2023 | 109.5 | 108
899 | EUNICE SOLAR U1 |  | EUNICE_PV1 | ANDREWS | SOLAR | WEST | 2021 | 189.6 | 189.6
900 | EUNICE SOLAR U2 |  | EUNICE_PV2 | ANDREWS | SOLAR | WEST | 2021 | 237.1 | 237.1
901 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 6.8 | 6.8
902 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 152.5 | 150
903 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22
904 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 126 | 121.1
905 | GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | CONCHO | SOLAR | WEST | 2021 | 250 | 250
906 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 126.3 | 124.6
907 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 132.2 | 130.4
908 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5 | 5
909 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3 | 5.3
910 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6
911 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2 | 102.2
912 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3 | 102.3
913 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5 | 198.5
914 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1 | 162.1
915 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5 | 143.5
916 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8 | 59.8
917 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5 | 7.5
918 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7 | 100.7
919 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10 | 10
920 | LILY SOLAR |  | LILY_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2021 | 147.6 | 147.6
921 | LONGBOW SOLAR |  | LON_SOLAR1 | BRAZORIA | SOLAR | COASTAL | 2022 | 78.2 | 77
922 | LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | BORDEN | SOLAR | WEST | 2021 | 98.5 | 98.5
923 | LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | BORDEN | SOLAR | WEST | 2021 | 128.3 | 128.3
924 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3 | 5.3
925 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10 | 10
926 | MCLEAN (SHAKES) SOLAR |  | MCLNSLR_UNIT1 | DIMMIT | SOLAR | SOUTH | 2023 | 207.4 | 200
927 | MISAE SOLAR U1 |  | MISAE_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 121.4 | 121.4
928 | MISAE SOLAR U2 |  | MISAE_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 118.6 | 118.6
929 | NEBULA SOLAR (RAYOS DEL SOL) U1 |  | NEBULA_UNIT1 | CAMERON | SOLAR | COASTAL | 2022 | 137.5 | 137.5
930 | NOBLE SOLAR U1 |  | NOBLESLR_SOLAR1 | DENTON | SOLAR | NORTH | 2022 | 148.8 | 146.7
931 | NOBLE SOLAR U2 |  | NOBLESLR_SOLAR2 | DENTON | SOLAR | NORTH | 2022 | 130.2 | 128.3
932 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2 | 5.2
933 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180 | 180
934 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.18 | 39.2
935 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4
936 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5
937 | OCI ALAMO 4 SOLAR-BRACKETVILLE | 22INR0600 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.62 | 37.6
938 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100 | 100
939 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2016 | 110.2 | 110.2
940 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112 | 112
941 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.04 | 125.1
942 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 127.95 | 128.1
943 | PHOENIX SOLAR |  | PHOENIX_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 83.9 | 83.9
944 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6 | 2.6
945 | PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6 | 153.6
946 | PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150 | 150
947 | PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | ANDREWS | SOLAR | WEST | 2021 | 126.5 | 126.5
948 | PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | ANDREWS | SOLAR | WEST | 2021 | 126.4 | 126.4
949 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
950 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
951 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5 | 97.5
952 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5 | 107.5
953 | RADIAN SOLAR U1 |  | RADN_SLR_UNIT1 | BROWN | SOLAR | NORTH | 2023 | 161.41 | 158.9
954 | RADIAN SOLAR U2 |  | RADN_SLR_UNIT2 | BROWN | SOLAR | NORTH | 2023 | 166.02 | 162.9
955 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 211.19 | 200
956 | RATLIFF SOLAR (CONCHO VALLEY SOLAR) |  | RATLIFF_SOLAR1 | TOM GREEN | SOLAR | WEST | 2023 | 162.43 | 159.8
957 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8
958 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8
959 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PECOS | SOLAR | WEST | 2021 | 222 | 222
960 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PECOS | SOLAR | WEST | 2021 | 28 | 28
961 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2
962 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 155.44 | 150
963 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8 | 59.8
964 | ROWLAND SOLAR I |  | ROW_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 101.7 | 100
965 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50
966 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5
967 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10 | 10
968 | STRATEGIC SOLAR 1 |  | STRATEGC_UNIT1 | ELLIS | SOLAR | NORTH | 2022 | 135 | 127.1
969 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
970 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
971 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6
972 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5
973 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9 | 125.9
974 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9 | 128.9
975 | TAYGETE SOLAR 2 U1 |  | TAYGETE2_UNIT1 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9
976 | TAYGETE SOLAR 2 U2 |  | TAYGETE2_UNIT2 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9
977 | TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 136.8 | 136.8
978 | TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | CULBERSON | SOLAR | WEST | 2021 | 131.1 | 131.1
979 | TPE ERATH SOLAR |  | DG_ERATH_ERATH21 | ERATH | SOLAR | NORTH | 2021 | 10 | 10
980 | VANCOURT SOLAR |  | VANCOURT_UNIT1 | CAMERON | SOLAR | COASTAL | 2023 | 45.7 | 45.7
981 | VISION SOLAR 1 |  | VISION_UNIT1 | NAVARRO | SOLAR | NORTH | 2022 | 129.2 | 120.7
982 | WAGYU SOLAR |  | WGU_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2021 | 120 | 120
983 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10
984 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182 | 182
985 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7
986 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5 | 5
987 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100 | 100
988 | WESTORIA SOLAR U1 |  | WES_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6
989 | WESTORIA SOLAR U2 |  | WES_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6
990 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
991 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
992 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10 | 10
993 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10 | 10
994 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5 | 5
995 | Operational Capacity Total (Solar) | [6 empty] | 11138.77 | 11058.1
996 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 100 | 64
997
998 | Operational Resources (Solar) - Synchronized but not Approved for Commercial Operations
999 | ANDROMEDA SOLAR U1 | 22INR0412 | ANDMDSLR_UNIT1 | SCURRY | SOLAR | WEST | 2023 | 158.8 | 158
1000 | ANDROMEDA SOLAR U2 | 22INR0412 | ANDMDSLR_UNIT2 | SCURRY | SOLAR | WEST | 2023 | 162.4 | 162
1001 | BIG STAR SOLAR U1 | 21INR0413 | BIG_STAR_UNIT1 | BASTROP | SOLAR | SOUTH | 2023 | 132.27 | 130
1002 | BIG STAR SOLAR U2 | 21INR0413 | BIG_STAR_UNIT2 | BASTROP | SOLAR | SOUTH | 2023 | 70.83 | 70
1003 | BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | GRIMES | SOLAR | NORTH | 2023 | 69 | 69
1004 | BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | GRIMES | SOLAR | NORTH | 2023 | 141 | 141
1005 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 217.5 | 217.5
1006 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 221.3 | 221.3
1007 | CROWN SOLAR | 21INR0323 | CRWN_SLR_UNIT1 | FALLS | SOLAR | NORTH | 2023 | 101.3 | 100.3
1008 | DANISH FIELDS SOLAR U1 | 20INR0069 | DAN_UNIT1 | WHARTON | SOLAR | SOUTH | 2023 | 301.3 | 300
1009 | DANISH FIELDS SOLAR U2 | 20INR0069 | DAN_UNIT2 | WHARTON | SOLAR | SOUTH | 2023 | 151 | 150.2
1010 | DANISH FIELDS SOLAR U3 | 20INR0069 | DAN_UNIT3 | WHARTON | SOLAR | SOUTH | 2023 | 150.5 | 149.8
1011 | DILEO SOLAR | 22INR0359 | DILEOSLR_UNIT1 | BOSQUE | SOLAR | NORTH | 2023 | 71.4 | 71.4
1012 | EIFFEL SOLAR | 22INR0223 | EIFSLR_UNIT1 | LAMAR | SOLAR | NORTH | 2023 | 241 | 240
1013 | ELLIS SOLAR | 21INR0493 | ELLISSLR_UNIT1 | ELLIS | SOLAR | NORTH | 2023 | 81.3 | 80
1014 | FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 179.5 | 179.6
1015 | FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 171.8 | 171.9
1016 | FRYE SOLAR U1 | 20INR0080 | FRYE_SLR_UNIT1 | SWISHER | SOLAR | PANHANDLE | 2024 | 250.9 | 250
1017 | FRYE SOLAR U2 | 20INR0080 | FRYE_SLR_UNIT2 | SWISHER | SOLAR | PANHANDLE | 2024 | 251.1 | 250
1018 | GALLOWAY 2 SOLAR | 21INR0431 | GALLOWAY_SOLAR2 | CONCHO | SOLAR | WEST | 2023 | 111.1 | 110
1019 | GOLINDA SOLAR | 21INR0434 | GOLINDA_UNIT1 | FALLS | SOLAR | NORTH | 2023 | 101.1 | 100.3
1020 | GRIZZLY RIDGE SOLAR | 21INR0375 | GRIZZLY_SOLAR1 | HAMILTON | SOLAR | NORTH | 2023 | 101.7 | 100
1021 | HORIZON SOLAR | 21INR0261 | HRZN_SLR_UNIT1 | FRIO | SOLAR | SOUTH | 2023 | 203.5 | 200
1022 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b | HOVEY_UNIT2 | PECOS | SOLAR | WEST | 2023 | 7.41 | 7.4
1023 | JADE SOLAR U1 | 22INR0360 | JADE_SLR_UNIT1 | SCURRY | SOLAR | WEST | 2023 | 158.8 | 158
1024 | JADE SOLAR U2 | 22INR0360 | JADE_SLR_UNIT2 | SCURRY | SOLAR | WEST | 2023 | 162.4 | 162
1025 | MUSTANG CREEK SOLAR U1 | 18INR0050 | MUSTNGCK_SOLAR1 | JACKSON | SOLAR | SOUTH | 2023 | 60.2 | 60
1026 | MUSTANG CREEK SOLAR U2 | 18INR0050 | MUSTNGCK_SOLAR2 | JACKSON | SOLAR | SOUTH | 2023 | 90.3 | 90
1027 | MYRTLE SOLAR U1 | 19INR0041 | MYR_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 171.6 | 167.2
1028 | MYRTLE SOLAR U2 | 19INR0041 | MYR_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 149.6 | 145.8
1029 | PISGAH RIDGE SOLAR U1 | 22INR0254 | PISGAH_SOLAR1 | NAVARRO | SOLAR | NORTH | 2023 | 189.4 | 186.5
1030 | PISGAH RIDGE SOLAR U2 | 22INR0254 | PISGAH_SOLAR2 | NAVARRO | SOLAR | NORTH | 2023 | 64.4 | 63.5
1031 | PITTS DUDIK SOLAR U1 | 20INR0074 | PITTSDDK_UNIT1 | HILL | SOLAR | NORTH | 2023 | 49.6 | 49.6
1032 | PLAINVIEW SOLAR (RAMSEY SOLAR) U1 | 20INR0130 | PLN_UNIT1 | WHARTON | SOLAR | SOUTH | 2023 | 270 | 257
1033 | PLAINVIEW SOLAR (RAMSEY SOLAR) U2 | 20INR0130 | PLN_UNIT2 | WHARTON | SOLAR | SOUTH | 2023 | 270 | 257
1034 | ROSELAND SOLAR U1 | 20INR0205 | ROSELAND_SOLAR1 | FALLS | SOLAR | NORTH | 2023 | 254 | 250
1035 | ROSELAND SOLAR U2 | 20INR0205 | ROSELAND_SOLAR2 | FALLS | SOLAR | NORTH | 2023 | 167.9 | 165.3
1036 | ROSELAND SOLAR U3 | 22INR0506 | ROSELAND_SOLAR3 | FALLS | SOLAR | NORTH | 2023 | 86.1 | 84.7
1037 | TAVENER U1 (FORT BEND SOLAR) | 18INR0053 | TAV_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 143.61 | 143.6
1038 | TAVENER U2 (FORT BEND SOLAR) | 23INR0528 | TAV_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 98.04 | 96.4
1039 | TEXAS SOLAR NOVA U1 | 19INR0001 | NOVA1SLR_UNIT1 | KENT | SOLAR | WEST | 2023 | 126.81 | 126
1040 | TEXAS SOLAR NOVA U2 | 19INR0001 | NOVA1SLR_UNIT2 | KENT | SOLAR | WEST | 2023 | 126.7 | 126
1041 | TRES BAHIAS SOLAR | 20INR0266 | TREB_SLR_SOLAR1 | CALHOUN | SOLAR | COASTAL | 2023 | 196.29 | 195
1042 | SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | LAMAR | SOLAR | NORTH | 2023 | 125 | 125
1043 | SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | LAMAR | SOLAR | NORTH | 2023 | 125 | 125
1044 | SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | LAMAR | SOLAR | NORTH | 2023 | 125 | 125
1045 | SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | LAMAR | SOLAR | NORTH | 2023 | 125 | 125
1046 | SUN VALLEY U1 | 19INR0169 | SUNVASLR_UNIT1 | HILL | SOLAR | NORTH | 2023 | 165.75 | 165.8
1047 | SUN VALLEY U2 | 19INR0169 | SUNVASLR_UNIT2 | HILL | SOLAR | NORTH | 2023 | 86.19 | 86.2
1048 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Solar) | [6 empty] | 7236.7 | 7165.3
1049 | Solar Peak Average Capacity Percentage |  | SOLAR_SYNC_PEAK_PCT | % |  |  |  | 100 | 64
1050
1051 | Operational Resources (Storage)
1052 | AZURE SKY BESS |  | AZURE_BESS1 | HASKELL | STORAGE | WEST | 2022 | 77.6 | 77.6
1053 | BAT CAVE |  | BATCAVE_BES1 | MASON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
1054 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30
1055 | BELDING TNP (TRIPLE BUTTE BATTERY) (DGR) |  | BELD_BELU1 | PECOS | STORAGE | WEST | 2021 | 9.18 | 7.5
1056 | BLUE JAY BESS |  | BLUEJAY_BESS1 | GRIMES | STORAGE | NORTH | 2023 | 51.6 | 50
1057 | BRP ALVIN (DGR) |  | ALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10
1058 | BRP ANGELTON (DGR) |  | ANGLETON_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10
1059 | BRP BRAZORIA |  | BRAZORIA_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 10
1060 | BRP DICKINSON (DGR) |  | DICKNSON_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10
1061 | BRP HEIGHTS (DGR) |  | HEIGHTTN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 9.95 | 10
1062 | BRP LOOP 463 (DGR) |  | L_463S_UNIT1 | VICTORIA | STORAGE | SOUTH | 2021 | 9.95 | 10
1063 | BRP LOPENO (DGR) |  | BRP_LOP1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 9.95 | 10
1064 | BRP MAGNOLIA (DGR) |  | MAGNO_TN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10
1065 | BRP ODESSA SW (DGR) |  | ODESW_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 9.95 | 10
1066 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2021 | 9.95 | 10
1067 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2021 | 9.95 | 10
1068 | BRP RANCHTOWN (DGR) |  | BRP_RNC1_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 9.95 | 10
1069 | BRP SWEENY (DGR) |  | SWEENY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10
1070 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 9.95 | 10
1071 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 9.95 | 10
1072 | BYRD RANCH STORAGE |  | BYRDR_ES_BESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 50.6 | 50
1073 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2018 | 9.9 | 9.9
1074 | CATARINA BESS (DGR) |  | CATARINA_BESS | DIMMIT | STORAGE | SOUTH | 2022 | 9.95 | 9.9
1075 | CEDARVALE BESS (DGR) |  | CEDRVALE_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1076 | CHISHOLM GRID |  | CHISMGRD_BES1 | TARRANT | STORAGE | NORTH | 2021 | 101.7 | 100
1077 | COMMERCE ST ESS (DGR) |  | X4_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10 | 10
1078 | COYOTE SPRINGS BESS (DGR) |  | COYOTSPR_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1079 | CROSSETT POWER U1 |  | CROSSETT_BES1 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100
1080 | CROSSETT POWER U2 |  | CROSSETT_BES2 | CRANE | STORAGE | WEST | 2022 | 101.5 | 100
1081 | DECORDOVA BESS U1 |  | DCSES_BES1 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1082 | DECORDOVA BESS U2 |  | DCSES_BES2 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1083 | DECORDOVA BESS U3 |  | DCSES_BES3 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1084 | DECORDOVA BESS U4 |  | DCSES_BES4 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1085 | ENDURANCE PARK STORAGE |  | ENDPARKS_ESS1 | SCURRY | STORAGE | WEST | 2022 | 51.5 | 50
1086 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2021 | 40.3 | 40.3
1087 | FAULKNER BESS (DGR) |  | FAULKNER_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1088 | FLAT TOP BATTERY (DGR) |  | FLAT_TOP_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9 | 9.9
1089 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2021 | 9.9 | 9.9
1090 | FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | REEVES | STORAGE | WEST | 2022 | 101.5 | 100
1091 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 102.4 | 100
1092 | GEORGETOWN SOUTH (RABBIT HILL ESS) (DGR) |  | GEORSO_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2019 | 9.9 | 9.9
1093 | GOMEZ BESS (DGR) |  | GOMZ_BESS | REEVES | STORAGE | WEST | 2023 | 9.95 | 9.9
1094 | HIGH LONESOME BESS |  | HI_LONEB_BESS1 | CROCKETT | STORAGE | WEST | 2023 | 51.1 | 50
1095 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2020 | 2 | 2
1096 | HOLCOMB BESS (DGR) |  | HOLCOMB_BESS | LA SALLE | STORAGE | SOUTH | 2023 | 9.95 | 9.9
1097 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2017 | 9.9 | 9.9
1098 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.25 | 2.3
1099 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5 | 1.5
1100 | LILY STORAGE |  | LILY_BESS1 | KAUFMAN | STORAGE | NORTH | 2021 | 51.7 | 51.7
1101 | LONESTAR BESS (DGR) |  | LONESTAR_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9
1102 | MADERO GRID U1 |  | MADERO_UNIT1 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100
1103 | MADERO GRID U2 (IGNACIO GRID) |  | MADERO_UNIT2 | HIDALGO | STORAGE | SOUTH | 2023 | 100.79 | 100
1104 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5 | 1.5
1105 | NOBLE STORAGE U1 |  | NOBLESLR_BESS1 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5
1106 | NOBLE STORAGE U2 |  | NOBLESLR_BESS2 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5
1107 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 36 | 33.7
1108 | NORTH COLUMBIA (ROUGHNECK STORAGE) |  | NCO_ESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 51.75 | 50
1109 | NORTH FORK |  | NF_BRP_BES1 | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
1110 | OLNEY BESS (DGR) |  | OLNEYTN_BESS | YOUNG | STORAGE | WEST | 2023 | 9.95 | 9.9
1111 | PORT LAVACA BATTERY (DGR) |  | PRTLAVS_BESS1 | CALHOUN | STORAGE | COASTAL | 2019 | 9.9 | 9.9
1112 | PYRON ESS |  | PYR_ESS | NOLAN | STORAGE | WEST | 2017 | 9.9 | 9.9
1113 | PYRON BESS 2A |  | PYR_ESS2A | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1
1114 | PYRON BESS 2B |  | PYR_ESS2B | NOLAN | STORAGE | WEST | 2023 | 15.1 | 15.1
1115 | PYOTE TNP (SWOOSE BATTERY) (DGR) |  | PYOTE_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9 | 9.9
1116 | QUEEN BESS |  | QUEEN_BA_BESS1 | UPTON | STORAGE | WEST | 2023 | 51.1 | 50
1117 | RATTLESNAKE BESS (DGR) |  | RTLSNAKE_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9
1118 | REPUBLIC ROAD STORAGE |  | RPUBRDS_ESS1 | ROBERTSON | STORAGE | NORTH | 2022 | 51.75 | 50
1119 | RIVER VALLEY STORAGE U1 |  | RVRVLYS_ESS1 | WILLIAMSON | STORAGE | SOUTH | 2023 | 51.5 | 50
1120 | RIVER VALLEY STORAGE U2 |  | RVRVLYS_ESS2 | WILLIAMSON | STORAGE | SOUTH | 2023 | 51.5 | 50
1121 | ROSELAND STORAGE |  | ROSELAND_BESS1 | FALLS | STORAGE | NORTH | 2023 | 51.6 | 50
1122 | SADDLEBACK BESS (DGR) |  | SADLBACK_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1123 | SARAGOSA BESS (DGR) |  | SGSA_BESS1 | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1124 | SCREWBEAN BESS (DGR) |  | SBEAN_BESS | CULBERSON | STORAGE | WEST | 2023 | 9.95 | 9.9
1125 | SILICON HILL STORAGE U1 |  | SLCNHLS_ESS1 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50
1126 | SILICON HILL STORAGE U2 |  | SLCNHLS_ESS2 | TRAVIS | STORAGE | SOUTH | 2023 | 51.8 | 50
1127 | SNYDER (DGR) |  | SNY_BESS_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 9.95 | 10
1128 | SWEETWATER BESS (DGR) |  | SWTWR_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.95 | 9.9
1129 | SP TX-12B BESS |  | SPTX12B_BES1 | UPTON | STORAGE | WEST | 2023 | 25.1 | 22.7
1130 | SWOOSE II |  | SWOOSEII_BESS1 | WARD | STORAGE | WEST | 2022 | 101.5 | 100
1131 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | HOWARD | STORAGE | WEST | 2017 | 2 | 2
1132 | TOYAH POWER STATION (DGR) |  | TOYAH_BESS | REEVES | STORAGE | WEST | 2021 | 9.95 | 9.9
1133 | TURQUOISE STORAGE |  | TURQBESS_BESS1 | HUNT | STORAGE | NORTH | 2023 | 196.2 | 190
1134 | WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 9.95 | 10
1135 | WEST COLUMBIA (PROSPECT STORAGE) (DGR) |  | WCOLLOCL_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2019 | 9.9 | 9.9
1136 | WOLF TANK STORAGE |  | WFTANK_ESS1 | WEBB | STORAGE | SOUTH | 2023 | 150.4 | 150
1137 | WORSHAM BATTERY (DGR) |  | WORSHAM_BESS1 | REEVES | STORAGE | WEST | 2019 | 9.9 | 9.9
1138 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2 | 2
1139 | Operational Capacity Total (Storage) | [6 empty] | 3095.66 | 3048.6
1140 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 100 | 0
1141
1142 | Operational Resources (Storage) - Synchronized but not Approved for Commercial Operations
1143 | ANCHOR BESS U1 | 21INR0474 | ANCHOR_BESS1 | CALLAHAN | STORAGE | WEST | 2023 | 35.2 | 35.2
1144 | ANCHOR BESS U2 | 21INR0474 | ANCHOR_BESS2 | CALLAHAN | STORAGE | WEST | 2023 | 36.3 | 36.3
1145 | BAY CITY BESS (DGR) | 23INR0507 | BAY_CITY_BESS | MATAGORDA | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1146 | JUNCTION BESS (DGR) | 23INR0521 | JUNCTION_BESS | KIMBLE | STORAGE | SOUTH | 2023 | 9.95 | 9.9
1147 | MUSTANG CREEK STORAGE | 21INR0484 | MUSTNGCK_BES1 | JACKSON | STORAGE | SOUTH | 2023 | 70.5 | 70
1148 | NORTH ALAMO BESS (DGR) | 23INR0477 | N_ALAMO_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.99
1149 | NORTH MERCEDES BESS (DGR) | 23INR0514 | N_MERCED_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.9 | 9.9 | Yes
1150 | RODEO RANCH ENERGY STORAGE U1 | 23INR0371 | RRANCHES_UNIT1 | REEVES | STORAGE | WEST | 2023 | 150.32 | 145
1151 | RODEO RANCH ENERGY STORAGE U2 | 23INR0371 | RRANCHES_UNIT2 | REEVES | STORAGE | WEST | 2023 | 150.32 | 145
1152 | SMT SANTA ROSA (DGR) | 23INR0515 | S_SNROSA_BESS | CAMERON | STORAGE | COASTAL | 2023 | 9.99 | 9.99
1153 | SUN VALLEY BESS U1 | 22INR0429 | SUNVASLR_BESS1 | HILL | STORAGE | NORTH | 2023 | 54.08 | 53.3
1154 | SUN VALLEY BESS U2 | 22INR0429 | SUNVASLR_BESS2 | HILL | STORAGE | NORTH | 2023 | 47.32 | 46.7
1155 | TIMBERWOLF BESS | 22INR0495 | TBWF_ESS_BES1 | CRANE | STORAGE | WEST | 2023 | 150.34 | 150
1156 | VORTEX BESS | 21INR0473 | VORTEX_BESS1 | THROCKMORTON | STORAGE | WEST | 2023 | 121.8 | 121.8
1157 | WEST HARLINGEN BESS (DGR) | 23INR0512 | W_HARLIN_BESS | CAMERON | STORAGE | COASTAL | 2023 | 9.99 | 9.99
1158 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Storage) | [6 empty] | 875.99 | 862.97
1159 | Storage Peak Average Capacity Percentage |  | STORAGE_SYNC_PEAK_PCT | % |  |  |  | 0 | 0
1160
1161 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0 | 0
1162
1163 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0
1164
1165 | Non-Synchronous Tie Resources
1166 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600 | 600
1167 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220 | 220
1168 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100 | 100
1169 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300 | 300
1170 | Non-Synchronous Ties Total | [6 empty] | 1220 | 1220
1171 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 100 | 59
1172
1173 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
1174 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2023 | 0 | 0
1175 | BEACHWOOD II POWER STATION (U7-U8) | 23INR0506 |  | BRAZORIA | GAS-GT | COASTAL | 2024 | 0 | 0
1176 | REMY JADE POWER STATION | 23INR0339 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 0 | 0
1177 | REMY JADE II POWER STATION | 24INR0382 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 0 | 0
1178 | SKY SEALY | 21INR0500 |  | AUSTIN | GAS-IC | SOUTH | 2025 | 0 | 0
1179 | TECO GTG2 | 23INR0408 |  | HARRIS | GAS-GT | HOUSTON | 2024 | 0 | 0
1180 | Planned Thermal Resources Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 0 | 0
1181
1182 | Planned Wind Resources with Executed SGIA
1183 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2025 | 0 | 0
1184 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2023 | 0 | 0
1185 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2024 | 0 | 0
1186 | CRAWFISH | 19INR0177 |  | WHARTON | WIND-O | SOUTH | 2023 | 0 | 0
1187 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2024 | 0 | 0
1188 | GOODNIGHT WIND II | 23INR0637 |  | ARMSTRONG | WIND-P | PANHANDLE | 2023 | 0 | 0 | Yes
1189 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2025 | 0 | 0
1190 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2025 | 0 | 0
1191 | MONTE ALTO 2 WIND | 19INR0023 |  | WILLACY | WIND-C | COASTAL | 2024 | 0 | 0
1192 | MONTE ALTO I WIND | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2024 | 0 | 0
1193 | MONTE CRISTO 1 WIND | 19INR0054 |  | HIDALGO | WIND-O | SOUTH | 2024 | 0 | 0 | Yes
1194 | MONTGOMERY RANCH WIND | 20INR0040 |  | FOARD | WIND-O | WEST | 2024 | 0 | 0
1195 | PIONEER DJ WIND | 23INR0387 |  | MIDLAND | WIND-O | WEST | 2024 | 0 | 0
1196 | RAY GULF WIND | 22INR0517 |  | WHARTON | WIND-O | SOUTH | 2025 | 0 | 0
1197 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2023 | 0 | 0
1198 | ROADRUNNER CROSSING WIND II | 21INR0515 |  | EASTLAND | WIND-O | NORTH | 2023 | 0 | 0 | Yes
1199 | SHAMROCK | 22INR0502 |  | CROCKETT | WIND-O | WEST | 2024 | 0 | 0
1200 | SHEEP CREEK WIND | 21INR0325 |  | CALLAHAN | WIND-O | WEST | 2023 | 0 | 0
1201 | SIETE | 20INR0047 |  | WEBB | WIND-O | SOUTH | 2024 | 0 | 0
1202 | Planned Capacity Total (Wind) | [6 empty] | 0 | 0
1203
1204 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 0 | 0
1205 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 100 | 31
1206
1207 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0 | 0
1208 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 100 | 41
1209
1210 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 0 | 0
1211 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 100 | 33
1212
1213 | Planned Solar Resources with Executed SGIA
1214 | 7V SOLAR | 21INR0351 |  | FAYETTE | SOLAR | SOUTH | 2024 | 0 | 0
1215 | ADAMSTOWN SOLAR | 21INR0210 |  | WICHITA | SOLAR | WEST | 2025 | 0 | 0
1216 | ALILA SOLAR | 23INR0093 |  | SAN PATRICIO | SOLAR | COASTAL | 2026 | 0 | 0
1217 | AMSTERDAM SOLAR | 21INR0256 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1218 | ANGELO SOLAR | 19INR0203 |  | TOM GREEN | SOLAR | WEST | 2024 | 0 | 0
1219 | ANGUS SOLAR | 20INR0035 |  | BOSQUE | SOLAR | NORTH | 2025 | 0 | 0
1220 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2024 | 0 | 0
1221 | ARROYO SOLAR | 20INR0086 |  | CAMERON | SOLAR | COASTAL | 2024 | 0 | 0
1222 | ASH CREEK SOLAR | 21INR0379 |  | HILL | SOLAR | NORTH | 2024 | 0 | 0
1223 | AUREOLA SOLAR | 21INR0302 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0 | Yes
1224 | BAKER BRANCH SOLAR | 23INR0026 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1225 | BIG ELM SOLAR | 21INR0353 |  | BELL | SOLAR | NORTH | 2024 | 0 | 0
1226 | BLEVINS SOLAR | 23INR0118 |  | FALLS | SOLAR | NORTH | 2025 | 0 | 0 | Yes
1227 | BLUE SKY SOL | 22INR0455 |  | CROCKETT | SOLAR | WEST | 2024 | 0 | 0
1228 | BRASS FORK SOLAR | 22INR0270 |  | HASKELL | SOLAR | WEST | 2025 | 0 | 0
1229 | BRIGHT ARROW SOLAR | 22INR0242 |  | HOPKINS | SOLAR | NORTH | 2024 | 0 | 0
1230 | CACHENA SOLAR | 23INR0027 |  | WILSON | SOLAR | SOUTH | 2025 | 0 | 0
1231 | CAMP CREEK SOLAR SLF | 23INR0385 |  | ROBERTSON | SOLAR | NORTH | 2024 | 0 | 0 | Yes
1232 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2025 | 0 | 0
1233 | CASCADE SOLAR | 23INR0091 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0 | Yes
1234 | CASTRO SOLAR | 20INR0050 |  | CASTRO | SOLAR | PANHANDLE | 2025 | 0 | 0
1235 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2025 | 0 | 0
1236 | CHILLINGHAM SOLAR | 23INR0070 |  | BELL | SOLAR | NORTH | 2024 | 0 | 0
1237 | CLUTCH CITY SOLAR | 22INR0279 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1238 | COMPADRE SOLAR | 24INR0023 |  | HILL | SOLAR | NORTH | 2024 | 0 | 0
1239 | CORAL SOLAR | 22INR0295 |  | FALLS | SOLAR | NORTH | 2023 | 0 | 0
1240 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2025 | 0 | 0
1241 | COTTONWOOD BAYOU SOLAR I | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1242 | CRADLE SOLAR | 23INR0150 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1243 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2025 | 0 | 0
1244 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2025 | 0 | 0
1245 | CUCHILLAS SOLAR | 24INR0059 |  | WEBB | SOLAR | SOUTH | 2024 | 0 | 0 | Yes
1246 | DEVILLE SOLAR | 22INR0262 |  | CALLAHAN | SOLAR | WEST | 2025 | 0 | 0 | Yes
1247 | RENEGADE PROJECT (DAWN SOLAR) | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2024 | 0 | 0
1248 | DELILAH SOLAR 1 | 22INR0202 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1249 | DELILAH SOLAR 2 | 22INR0203 |  | LAMAR | SOLAR | NORTH | 2025 | 0 | 0
1250 | DESERT VINE SOLAR | 22INR0307 |  | ZAPATA | SOLAR | SOUTH | 2024 | 0 | 0
1251 | DONEGAL SOLAR | 23INR0089 |  | DICKENS | SOLAR | PANHANDLE | 2024 | 0 | 0
1252 | DORADO SOLAR | 22INR0261 |  | CALLAHAN | SOLAR | WEST | 2025 | 0 | 0 | Yes
1253 | DORI BQ SOLAR | 23INR0040 |  | HARRIS | SOLAR | HOUSTON | 2024 | 0 | 0
1254 | DUFFY SOLAR | 23INR0057 |  | MATAGORDA | SOLAR | COASTAL | 2025 | 0 | 0 | Yes
1255 | DR SOLAR | 22INR0454 |  | CULBERSON | SOLAR | WEST | 2024 | 0 | 0
1256 | EASTBELL MILAM SOLAR | 21INR0203 |  | MILAM | SOLAR | SOUTH | 2023 | 0 | 0
1257 | ELIZA SOLAR | 21INR0368 |  | KAUFMAN | SOLAR | NORTH | 2024 | 0 | 0
1258 | EQUINOX SOLAR 1 | 21INR0226 |  | STARR | SOLAR | SOUTH | 2026 | 0 | 0
1259 | ERATH COUNTY SOLAR | 23INR0202 |  | ERATH | SOLAR | NORTH | 2025 | 0 | 0 | Yes
1260 | ERIN SOLAR | 23INR0058 |  | WHARTON | SOLAR | SOUTH | 2025 | 0 | 0 | Yes
1261 | ESTONIAN SOLAR FARM | 22INR0335 |  | DELTA | SOLAR | NORTH | 2024 | 0 | 0
1262 | FAGUS SOLAR PARK (MISAE SOLAR II) | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2025 | 0 | 0
1263 | FENCE POST SOLAR | 22INR0404 |  | NAVARRO | SOLAR | NORTH | 2024 | 0 | 0
1264 | FEWELL SOLAR | 23INR0367 |  | LIMESTONE | SOLAR | NORTH | 2025 | 0 | 0 | Yes
1265 | FIVE WELLS SOLAR | 24INR0015 |  | BELL | SOLAR | NORTH | 2023 | 0 | 0
1266 | GALACTIC SOLAR | 23INR0144 |  | GRAYSON | SOLAR | NORTH | 2024 | 0 | 0
1267 | GARCITAS CREEK SOLAR | 23INR0223 |  | JACKSON | SOLAR | SOUTH | 2025 | 0 | 0
1268 | GP SOLAR | 23INR0045 |  | VAN ZANDT | SOLAR | NORTH | 2025 | 0 | 0
1269 | GRANDSLAM SOLAR | 21INR0391 |  | ATASCOSA | SOLAR | SOUTH | 2025 | 0 | 0
1270 | GRANSOLAR TEXAS ONE | 22INR0511 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0
1271 | GREATER BRYANT G SOLAR | 23INR0300 |  | MIDLAND | SOLAR | WEST | 2024 | 0 | 0
1272 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2024 | 0 | 0
1273 | GREYHOUND SOLAR | 21INR0268 |  | ECTOR | SOLAR | WEST | 2025 | 0 | 0
1274 | GRIMES COUNTY SOLAR | 23INR0160 |  | GRIMES | SOLAR | NORTH | 2025 | 0 | 0
1275 | GULF STAR SOLAR SLF (G-STAR SOLAR) | 23INR0111 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1276 | HALO SOLAR | 21INR0304 |  | BELL | SOLAR | NORTH | 2024 | 0 | 0
1277 | HAYHURST TEXAS SOLAR | 22INR0363 |  | CULBERSON | SOLAR | WEST | 2024 | 0 | 0
1278 | HONEYCOMB SOLAR | 22INR0559 |  | BEE | SOLAR | SOUTH | 2025 | 0 | 0 | Yes
1279 | HOPKINS SOLAR | 20INR0210 |  | HOPKINS | SOLAR | NORTH | 2023 | 0 | 0
1280 | HORNET SOLAR | 23INR0021 |  | SWISHER | SOLAR | PANHANDLE | 2024 | 0 | 0
1281 | HOYTE SOLAR | 23INR0235 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0
1282 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2024 | 0 | 0
1283 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2025 | 0 | 0
1284 | JACKALOPE SOLAR | 23INR0180 |  | SAN PATRICIO | SOLAR | COASTAL | 2024 | 0 | 0
1285 | JUNGMANN SOLAR | 22INR0356 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0
1286 | LANGER SOLAR | 23INR0030 |  | BOSQUE | SOLAR | NORTH | 2025 | 0 | 0 | Yes
1287 | LAVACA BAY SOLAR | 23INR0084 |  | MATAGORDA | SOLAR | COASTAL | 2024 | 0 | 0
1288 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1289 | LUNIS CREEK SOLAR 1 | 21INR0344 |  | JACKSON | SOLAR | SOUTH | 2024 | 0 | 0
1290 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1291 | MANDORLA SOLAR | 21INR0303 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0 | Yes
1292 | MARKUM SOLAR | 20INR0230 |  | MCLENNAN | SOLAR | NORTH | 2024 | 0 | 0
1293 | MATAGORDA SOLAR | 22INR0342 |  | MATAGORDA | SOLAR | COASTAL | 2023 | 0 | 0
1294 | MERCURY I SOLAR | 21INR0257 |  | HILL | SOLAR | NORTH | 2024 | 0 | 0
1295 | MERCURY II SOLAR | 23INR0153 |  | HILL | SOLAR | NORTH | 2024 | 0 | 0
1296 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2024 | 0 | 0
1297 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2025 | 0 | 0
1298 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2025 | 0 | 0
1299 | NEPTUNE SOLAR | 21INR0499 |  | JACKSON | SOLAR | SOUTH | 2023 | 0 | 0
1300 | NORIA SOLAR DCC | 23INR0061 |  | NUECES | SOLAR | COASTAL | 2025 | 0 | 0
1301 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2025 | 0 | 0
1302 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2025 | 0 | 0
1303 | ORIANA SOLAR | 24INR0093 |  | VICTORIA | SOLAR | SOUTH | 2025 | 0 | 0
1304 | OUTPOST SOLAR | 23INR0007 |  | WEBB | SOLAR | SOUTH | 2024 | 0 | 0
1305 | OYSTERCATCHER SOLAR | 21INR0362 |  | ELLIS | SOLAR | NORTH | 2025 | 0 | 0
1306 | PARLIAMENT SOLAR | 23INR0044 |  | WALLER | SOLAR | HOUSTON | 2024 | 0 | 0
1307 | PEREGRINE SOLAR | 22INR0283 |  | GOLIAD | SOLAR | SOUTH | 2024 | 0 | 0
1308 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2025 | 0 | 0
1309 | PINK SOLAR | 22INR0281 |  | HUNT | SOLAR | NORTH | 2023 | 0 | 0
1310 | PORTER SOLAR | 21INR0458 |  | DENTON | SOLAR | NORTH | 2024 | 0 | 0
1311 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2024 | 0 | 0
1312 | REDONDA SOLAR | 23INR0162 |  | ZAPATA | SOLAR | SOUTH | 2024 | 0 | 0
1313 | HOLLYWOOD SOLAR (RED-TAILED HAWK SOLAR) | 21INR0389 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1314 | ROCINANTE SOLAR | 23INR0231 |  | GONZALES | SOLAR | SOUTH | 2024 | 0 | 0
1315 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2025 | 0 | 0
1316 | ROWLAND SOLAR II | 22INR0482 |  | FORT BEND | SOLAR | HOUSTON | 2024 | 0 | 0
1317 | SAMSON SOLAR 2 | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1318 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1319 | SCHOOLHOUSE SOLAR | 22INR0211 |  | LEE | SOLAR | SOUTH | 2025 | 0 | 0
1320 | SECOND DIVISION SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2024 | 0 | 0
1321 | SHAULA I SOLAR | 22INR0251 |  | DEWITT | SOLAR | SOUTH | 2025 | 0 | 0
1322 | SHAULA II SOLAR | 22INR0267 |  | DEWITT | SOLAR | SOUTH | 2026 | 0 | 0
1323 | SIGNAL SOLAR | 20INR0208 |  | HUNT | SOLAR | NORTH | 2025 | 0 | 0
1324 | SP JAGUAR SOLAR | 24INR0038 |  | MCLENNAN | SOLAR | NORTH | 2025 | 0 | 0
1325 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2025 | 0 | 0
1326 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2023 | 0 | 0
1327 | STAMPEDE SOLAR | 22INR0409 |  | HOPKINS | SOLAR | NORTH | 2024 | 0 | 0
1328 | STARLING SOLAR | 23INR0035 |  | GONZALES | SOLAR | SOUTH | 2025 | 0 | 0
1329 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2024 | 0 | 0
1330 | STILLHOUSE SOLAR | 24INR0166 |  | BELL | SOLAR | NORTH | 2025 | 0 | 0 | Yes
1331 | STONERIDGE SOLAR | 24INR0031 |  | MILAM | SOLAR | SOUTH | 2024 | 0 | 0 | Yes
1332 | SUNRAY | 21INR0395 |  | UVALDE | SOLAR | SOUTH | 2024 | 0 | 0
1333 | TALITHA SOLAR | 21INR0393 |  | JIM WELLS | SOLAR | SOUTH | 2024 | 0 | 0
1334 | TANGLEWOOD SOLAR | 23INR0054 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1335 | TEXANA SOLAR | 18INR0058 |  | WHARTON | SOLAR | SOUTH | 2024 | 0 | 0
1336 | TEXAS BLUEBONNET SOLAR | 24INR0580 |  | MCLENNAN | SOLAR | NORTH | 2024 | 0 | 0 | Yes
1337 | TEXAS SOLAR NOVA 2 | 20INR0269 |  | KENT | SOLAR | WEST | 2023 | 0 | 0
1338 | THREE W SOLAR | 25INR0055 |  | HILL | SOLAR | NORTH | 2025 | 0 | 0 | Yes
1339 | TIERRA BONITA SOLAR | 21INR0424 |  | PECOS | SOLAR | WEST | 2024 | 0 | 0
1340 | TROJAN SOLAR | 23INR0296 |  | COOKE | SOLAR | NORTH | 2026 | 0 | 0
1341 | TRUE NORTH SOLAR | 23INR0114 |  | FALLS | SOLAR | NORTH | 2024 | 0 | 0 | Yes
1342 | TULSITA SOLAR | 21INR0223 |  | GOLIAD | SOLAR | SOUTH | 2024 | 0 | 0
1343 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2024 | 0 | 0
1344 | ULYSSES SOLAR | 21INR0253 |  | COKE | SOLAR | WEST | 2024 | 0 | 0
1345 | UMBRA (STOCKYARD) SOLAR | 23INR0155 |  | FRANKLIN | SOLAR | NORTH | 2025 | 0 | 0
1346 | XE MURAT SOLAR | 22INR0354 |  | HARRIS | SOLAR | HOUSTON | 2024 | 0 | 0
1347 | ZIER SOLAR | 21INR0019 |  | KINNEY | SOLAR | SOUTH | 2024 | 0 | 0
1348 | Planned Capacity Total (Solar) | [6 empty] | 0 | 0
1349 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 100 | 64
1350
1351 | Planned Storage Resources with Executed SGIA
1352 | ADAMSTOWN STORAGE | 21INR0209 |  | WICHITA | STORAGE | WEST | 2025 | 0 | 0
1353 | AE-TELVIEW ESS (DGR) | 23INR0541 |  | FORT BEND | STORAGE | HOUSTON | 2024 | 0 | 0 | Yes
1354 | AL PASTOR BESS | 24INR0273 |  | DAWSON | STORAGE | WEST | 2024 | 0 | 0
1355 | AMSTERDAM STORAGE | 22INR0417 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1356 | ANEMOI ENERGY STORAGE | 23INR0369 |  | HIDALGO | STORAGE | SOUTH | 2023 | 0 | 0
1357 | ANGELO STORAGE | 23INR0418 |  | TOM GREEN | STORAGE | WEST | 2024 | 0 | 0 | Yes
1358 | ANOLE BESS | 23INR0299 |  | DALLAS | STORAGE | NORTH | 2024 | 0 | 0 | Yes
1359 | ARROYO STORAGE SLF | 24INR0306 |  | CAMERON | STORAGE | COASTAL | 2024 | 0 | 0
1360 | BIG STAR STORAGE | 21INR0469 |  | BASTROP | STORAGE | SOUTH | 2023 | 0 | 0
1361 | BLEVINS STORAGE | 23INR0119 |  | FALLS | STORAGE | NORTH | 2025 | 0 | 0 | Yes
1362 | BOCO BESS | 23INR0470 |  | BORDEN | STORAGE | WEST | 2024 | 0 | 0
1363 | BORDERTOWN BESS | 23INR0354 |  | STARR | STORAGE | SOUTH | 2025 | 0 | 0
1364 | BRAZOS BEND BESS | 23INR0363 |  | FORT BEND | STORAGE | HOUSTON | 2024 | 0 | 0
1365 | BRIGHT ARROW STORAGE | 22INR0302 |  | HOPKINS | STORAGE | NORTH | 2023 | 0 | 0
1366 | BRP ANTLIA BESS | 22INR0349 |  | VAL VERDE | STORAGE | WEST | 2024 | 0 | 0
1367 | BRP AVILA BESS | 23INR0287 |  | PECOS | STORAGE | WEST | 2024 | 0 | 0
1368 | BRP CACHI BESS | 22INR0388 |  | GUADALUPE | STORAGE | SOUTH | 2024 | 0 | 0
1369 | BRP CARINA BESS | 22INR0353 |  | NUECES | STORAGE | COASTAL | 2024 | 0 | 0
1370 | BRP DICKENS BESS | 22INR0325 |  | DICKENS | STORAGE | PANHANDLE | 2024 | 0 | 0
1371 | BRP HYDRA BESS | 22INR0372 |  | PECOS | STORAGE | WEST | 2023 | 0 | 0
1372 | BRP LIBRA BESS | 22INR0366 |  | GUADALUPE | STORAGE | SOUTH | 2023 | 0 | 0
1373 | BRP PALEO BESS | 22INR0322 |  | HALE | STORAGE | PANHANDLE | 2023 | 0 | 0
1374 | BRP PAVO BESS | 22INR0384 |  | PECOS | STORAGE | WEST | 2024 | 0 | 0
1375 | BRP TORTOLAS BESS | 23INR0072 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 0 | 0
1376 | BRP ZEYA BESS | 23INR0290 |  | GALVESTON | STORAGE | HOUSTON | 2024 | 0 | 0
1377 | CALLISTO I ENERGY CENTER | 22INR0490 |  | HARRIS | STORAGE | HOUSTON | 2024 | 0 | 0
1378 | CAMP CREEK STORAGE SLF | 23INR0423 |  | ROBERTSON | STORAGE | NORTH | 2024 | 0 | 0 | Yes
1379 | CHILLINGHAM STORAGE | 23INR0079 |  | BELL | STORAGE | NORTH | 2024 | 0 | 0
1380 | CISCO BESS (DGR) | 24INR0588 |  | EASTLAND | STORAGE | NORTH | 2024 | 0 | 0 | Yes
1381 | CITADEL BESS | 24INR0147 |  | HARRIS | STORAGE | HOUSTON | 2024 | 0 | 0
1382 | CONNOLLY STORAGE | 23INR0403 |  | WISE | STORAGE | NORTH | 2024 | 0 | 0
1383 | CONTINENTAL BESS | 23INR0543 |  | STARR | STORAGE | SOUTH | 2023 | 0 | 0 | Yes
1384 | CONTINENTAL BESS (DGR) | 23INR0543 |  | STARR | STORAGE | SOUTH | 2023 | 0 | 0 | Yes
1385 | CORAL STORAGE | 23INR0124 |  | FALLS | STORAGE | NORTH | 2024 | 0 | 0
1386 | COTTONWOOD BAYOU STORAGE | 21INR0443 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 0 | 0
1387 | DAMON STORAGE | 23INR0523 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 0 | 0
1388 | DANISH FIELDS STORAGE | 21INR0450 |  | WHARTON | STORAGE | SOUTH | 2024 | 0 | 0
1389 | DESERT WILLOW BESS | 23INR0195 |  | ELLIS | STORAGE | NORTH | 2024 | 0 | 0 | Yes
1390 | DIBOLL BESS (DGR) | 23INR0522 |  | ANGELINA | STORAGE | NORTH | 2024 | 0 | 0
1391 | DOGFISH BESS | 23INR0219 |  | PECOS | STORAGE | WEST | 2024 | 0 | 0 | Yes
1392 | BURKSOL BESS (DONEGAL BESS) | 23INR0103 |  | DICKENS | STORAGE | PANHANDLE | 2024 | 0 | 0
1393 | DORI BQ BESS | 24INR0196 |  | HARRIS | STORAGE | HOUSTON | 2024 | 0 | 0 | Yes
1394 | EBONY ENERGY STORAGE | 23INR0154 |  | COMAL | STORAGE | SOUTH | 2024 | 0 | 0
1395 | ELIZA STORAGE | 22INR0260 |  | KAUFMAN | STORAGE | NORTH | 2024 | 0 | 0
1396 | ESTONIAN ENERGY STORAGE | 22INR0336 |  | DELTA | STORAGE | NORTH | 2024 | 0 | 0
1397 | EVAL STORAGE | 22INR0401 |  | CAMERON | STORAGE | COASTAL | 2024 | 0 | 0
1398 | FALFURRIAS BESS (DGR) | 23INR0620 |  | BROOKS | STORAGE | SOUTH | 2024 | 0 | 0 | Yes
1399 | FARMERSVILLE BESS (DGR) | 23INR0555 |  | COLLIN | STORAGE | NORTH | 2024 | 0 | 0 | Yes
1400 | FENCE POST BESS | 22INR0405 |  | NAVARRO | STORAGE | NORTH | 2024 | 0 | 0
1401 | FERDINAND GRID BESS | 22INR0422 |  | BEXAR | STORAGE | SOUTH | 2025 | 0 | 0
1402 | FIVE WELLS STORAGE | 23INR0159 |  | BELL | STORAGE | NORTH | 2023 | 0 | 0
1403 | FORT DUNCAN BESS | 23INR0350 |  | MAVERICK | STORAGE | SOUTH | 2025 | 0 | 0
1404 | GARDEN CITY EAST BESS (DGR) | 23INR0565 |  | GLASSCOCK | STORAGE | WEST | 2024 | 0 | 0 | Yes
1405 | GIGA TEXAS ENERGY STORAGE | 23INR0239 |  | TRAVIS | STORAGE | SOUTH | 2023 | 0 | 0
1406 | GREAT KISKADEE STORAGE | 23INR0166 |  | HIDALGO | STORAGE | SOUTH | 2024 | 0 | 0
1407 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2024 | 0 | 0
1408 | GRIZZLY RIDGE BESS (DGR) | 22INR0596 |  | HAMILTON | STORAGE | NORTH | 2023 | 9.9 | 9.9
1409 | GUAJILLO ENERGY STORAGE | 23INR0343 |  | WEBB | STORAGE | SOUTH | 2024 | 0 | 0
1410 | GULF STAR STORAGE SLF | 23INR0460 |  | WHARTON | STORAGE | SOUTH | 2024 | 0 | 0 | Yes
1411 | HAMILTON BESS (DGR) | 23INR0554 |  | VAL VERDE | STORAGE | WEST | 2024 | 0 | 0 | Yes
1412 | HONEYCOMB STORAGE SLF | 23INR0392 |  | BEE | STORAGE | SOUTH | 2025 | 0 | 0 | Yes
1413 | HOUSE MOUNTAIN 2 BATT | 22INR0485 |  | BREWSTER | STORAGE | WEST | 2023 | 0 | 0
1414 | HUMMINGBIRD STORAGE | 22INR0327 |  | DENTON | STORAGE | NORTH | 2024 | 0 | 0
1415 | IEP ORCHARD BESS | 23INR0556 |  | FORT BEND | STORAGE | HOUSTON | 2024 | 0 | 0 | Yes
1416 | INERTIA BESS | 22INR0328 |  | HASKELL | STORAGE | WEST | 2023 | 0 | 0
1417 | INERTIA BESS 2 | 22INR0375 |  | HASKELL | STORAGE | WEST | 2025 | 0 | 0
1418 | IRON BELT ENERGY STORAGE | 25INR0208 |  | BORDEN | STORAGE | WEST | 2025 | 0 | 0
1419 | JUDKINS BESS (DGR) | 24INR0586 |  | ECTOR | STORAGE | WEST | 2024 | 0 | 0 | Yes
1420 | LARKSPUR ENERGY STORAGE | 23INR0340 |  | UPTON | STORAGE | WEST | 2025 | 0 | 0
1421 | LIMOUSIN OAK STORAGE | 22INR0338 |  | GRIMES | STORAGE | NORTH | 2024 | 0 | 0
1422 | LONG POINT STORAGE | 21INR0444 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0 | Yes
1423 | LONGBOW BESS | 25INR0328 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 0 | 0 | Yes
1424 | LOWER RIO BESS | 22INR0468 |  | HIDALGO | STORAGE | SOUTH | 2023 | 0 | 0 | Yes
1425 | LUFKIN SOUTH BESS (DGR) | 24INR0587 |  | ANGELINA | STORAGE | NORTH | 2024 | 0 | 0 | Yes
1426 | MIDWAY BESS | 23INR0688 |  | ECTOR | STORAGE | WEST | 2024 | 0 | 0 | Yes
1427 | MINERAL WELLS EAST BESS (DGR) | 23INR0570 |  | PALO PINTO | STORAGE | NORTH | 2023 | 0 | 0 | Yes
1428 | MYRTLE STORAGE | 21INR0442 |  | BRAZORIA | STORAGE | COASTAL | 2023 | 0 | 0
1429 | NORIA STORAGE | 23INR0062 |  | NUECES | STORAGE | COASTAL | 2025 | 0 | 0
1430 | ORIANA BESS | 24INR0109 |  | VICTORIA | STORAGE | SOUTH | 2025 | 0 | 0
1431 | PADUA GRID BESS | 22INR0368 |  | BEXAR | STORAGE | SOUTH | 2024 | 0 | 0
1432 | PAULINE BESS (DGR) | 24INR0585 |  | HENDERSON | STORAGE | NORTH | 2024 | 0 | 0 | Yes
1433 | PINTAIL PASS BESS | 24INR0302 |  | SAN PATRICIO | STORAGE | COASTAL | 2025 | 0 | 0 | Yes
1434 | PLATINUM STORAGE | 22INR0554 |  | FANNIN | STORAGE | NORTH | 2025 | 0 | 0
1435 | RAMSEY STORAGE | 21INR0505 |  | WHARTON | STORAGE | SOUTH | 2024 | 0 | 0
1436 | RED EGRET BESS | 24INR0281 |  | GALVESTON | STORAGE | HOUSTON | 2025 | 0 | 0 | Yes
1437 | RED HOLLY STORAGE | 21INR0033 |  | DAWSON | STORAGE | WEST | 2024 | 0 | 0
1438 | REGIS GREGORY | 23INR0539 |  | SAN PATRICIO | STORAGE | COASTAL | 2024 | 0 | 0 | Yes
1439 | REGIS MOORE FIELD BESS | 23INR0498 |  | HIDALGO | STORAGE | SOUTH | 2024 | 0 | 0 | Yes
1440 | ROCINANTE BESS | 23INR0232 |  | GONZALES | STORAGE | SOUTH | 2024 | 0 | 0
1441 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2024 | 0 | 0
1442 | SABAL STORAGE | 22INR0398 |  | CAMERON | STORAGE | COASTAL | 2023 | 0 | 0
1443 | SEVEN FLAGS BESS | 23INR0351 |  | WEBB | STORAGE | SOUTH | 2024 | 0 | 0 | Yes
1444 | SMT ELSA (DGR) | 23INR0513 |  | HIDALGO | STORAGE | SOUTH | 2023 | 0 | 0 | Yes
1445 | SMT GARCENO BESS (DGR) | 23INR0509 |  | STARR | STORAGE | SOUTH | 2023 | 0 | 0
1446 | SMT HARLINGEN II (DGR) | 23INR0512 |  | CAMERON | STORAGE | COASTAL | 2023 | 0 | 0 | Yes
1447 | SMT IRONMAN BESS | 24INR0265 |  | BRAZORIA | STORAGE | COASTAL | 2024 | 0 | 0 | Yes
1448 | SMT LOS FRESNOS (DGR) | 23INR0508 |  | CAMERON | STORAGE | COASTAL | 2023 | 0 | 0
1449 | SMT MAYBERRY BESS (DGR) | 23INR0511 |  | CAMERON | STORAGE | COASTAL | 2023 | 0 | 0
1450 | SMT MCALLEN II | 24INR0436 |  | HIDALGO | STORAGE | SOUTH | 2024 | 0 | 0 | Yes
1451 | SMT MERCEDES (DGR) | 23INR0514 |  | HIDALGO | STORAGE | SOUTH | 2023 | 10 | 10 | Yes
1452 | SMT RIO GRANDE CITY BESS (DGR) | 23INR0510 |  | STARR | STORAGE | SOUTH | 2023 | 0 | 0
1453 | SOHO BESS | 23INR0419 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1454 | SOHO II BESS | 25INR0162 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0 | Yes
1455 | SOPORTAR ESS | 23INR0381 |  | BEXAR | STORAGE | SOUTH | 2025 | 0 | 0 | Yes
1456 | SOWERS STORAGE | 22INR0552 |  | KAUFMAN | STORAGE | NORTH | 2024 | 0 | 0
1457 | SP JAGUAR BESS | 24INR0039 |  | MCLENNAN | STORAGE | NORTH | 2025 | 0 | 0
1458 | ST. GALL I ENERGY STORAGE | 22INR0524 |  | PECOS | STORAGE | WEST | 2023 | 0 | 0
1459 | STAMPEDE BESS | 22INR0410 |  | HOPKINS | STORAGE | NORTH | 2024 | 0 | 0
1460 | STOCKYARD GRID BATT | 21INR0492 |  | TARRANT | STORAGE | NORTH | 2024 | 0 | 0
1461 | TALITHA BESS | 23INR0331 |  | JIM WELLS | STORAGE | SOUTH | 2024 | 0 | 0
1462 | TANZANITE STORAGE | 22INR0549 |  | HENDERSON | STORAGE | NORTH | 2024 | 0 | 0
1463 | THIRD COAST BESS | 23INR0361 |  | JACKSON | STORAGE | SOUTH | 2024 | 0 | 0 | Yes
1464 | TIDWELL PRAIRIE STORAGE 1 | 21INR0517 |  | ROBERTSON | STORAGE | NORTH | 2026 | 0 | 0
1465 | TIERRA SECA BESS | 23INR0364 |  | VAL VERDE | STORAGE | WEST | 2024 | 0 | 0 | Yes
1466 | UMBRA (STOCKYARD) BESS | 23INR0156 |  | FRANKLIN | STORAGE | NORTH | 2025 | 0 | 0
1467 | WALSTROM BESS | 22INR0540 |  | AUSTIN | STORAGE | SOUTH | 2024 | 0 | 0 | Yes
1468 | WEIL TRACT BESS | 23INR0569 |  | NUECES | STORAGE | COASTAL | 2023 | 0 | 0 | Yes
1469 | ZIER STORAGE | 21INR0027 |  | KINNEY | STORAGE | SOUTH | 2024 | 0 | 0
1470 | SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * | [6 empty] | 0 | 0
1471 | Planned Capacity Total (Storage) | [6 empty] | 19.9 | 19.9
1472 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 100 | 0
1473
1474 | Inactive Planned Resources
1475 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60 | 60
1476 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2026 | 0 | 0
1477 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1
1478 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 250.1 | 250.1
1479 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5 | 152.5
1480 | MIRAGE CTG 1 | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2023 | 0 | 0
1481 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150 | 150
1482 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2025 | 0 | 0
1483 | SODA LAKE SOLAR 1 SLF | 20INR0143 |  | CRANE | SOLAR | WEST | 2024 | 0 | 0
1484 | SODA LAKE SOLAR 2 SLF | 23INR0080 |  | CRANE | SOLAR | WEST | 2023 | 0 | 0
1485 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2024 | 0 | 0
1486 | Inactive Planned Capacity Total | [6 empty] | 862.7 | 862.7
1487
1488 | Seasonal Mothballed Resources
1489 | POWERLANE PLANT STG 1 (AS OF 10/1/2022, AVAILABLE 5/26 THROUGH 9/30) |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 18.75 | 17.5
1490 | SPENCER STG U4 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 61 | 57
1491 | SPENCER STG U5 (AS OF 10/24/2022, AVAILABLE 4/2 THROUGH 11/30) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 65 | 61
1492 | Total Seasonal Mothballed Capacity | [6 empty] | 356586.97 | 328729.0603
1493
1494 | Mothballed Resources
1495 | BRANDON (LP&L) (DGR) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | BRANDON_UNIT1 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 25 | 20
1496 | CALENERGY-FALCON SEABOARD STG 3 (AS OF 7/8/22, DUE TO FORCED OUTAGE) |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 62 | 62
1497 | R MASSENGALE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G6 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
1498 | R MASSENGALE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G7 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
1499 | R MASSENGALE STG (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G8 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 58.9 | 38
1500 | RAY OLINGER STG 1 (AS OF 4/5/22) |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78 | 78
1501 | TY COOKE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT2 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 18.7 | 14
1502 | TY COOKE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT3 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 26.6 | 17
1503 | Total Mothballed Capacity | [6 empty] | 309.2 | 265
1504
1505 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
1506 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP (NOT EXPECTED TO BE REPAIRED AFTER SPILL GATE FAILURE) |  | DG_LKWDTP_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8 | 4.8
1507 | Total Retiring Capacity | [6 empty] | 4.8 | 4.8
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide Ancillary Services rather than sustained capacity available to meet system peak loads.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Reources Services (RIOO-RS) system.
Note on J444: Extended outage: MacQueeny unit was placed on an extended outage on March 2023 and is expected to end in Summer 2025.

## Planning Reserve Margin
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2023
Release Date: September 19, 2023
Planning Reserve Margins
Fall
| Peak Demand Forecast, MW | 68666
| Rooftop PV Forecast Reduction, MW | -395
| Large Flexible Load Adjustment, MW | 1383
| Adjusted Peak Load Forecast, MW | 69654
| Total Resources, MW | 99727.2432
| Emergency Resources Deployed by ERCOT, MW 1 | 4782
| Planning Reserve Margin 2 | 53.73%
Formula: PRM% = 100 x ((Total Resources / (Adjusted Peak Demand - Emergency Resources)) - 1)
1 The derivation of the emergency resource amount is described in the Scenario Assumptions Details tab.
2 The Planning Reserve Margin (PRM) is the forecasted capacity reserve that can cover higher-than-expected peak demand and lower-than-expected resource availability when looking at months or longer in the future. This is in contrast to operating reserve measures that focus on actual available capacity during real-time and hour-ahead operating periods. Consequently, the PRM is not an appropriate measure of capacity reserves when operations timeframes are being considered.

## Scenario Assumption Details
| Base & Moderate Risk Scenarios | Extreme Risk Scenarios
Adjusted Peak Load Forecast | Based on average weather conditions at the time of fall peak using weather from 2008-2021 (used 2008’s weather to approximate the 15 year average weather conditions) These baseline forecasts are adjusted downwards to account for peak load reductions from rooftop solar installations that are not already accounted for in the baseline forecasts. The rooftop solar load reductions for the forecasted fall peak load hour is 395 MW.
Load Adjustments | Weather conditions at the time of peak are based on 2015’s weather to approximate 90th percentile weather These baseline forecasts are adjusted downwards to account for peak load reductions from rooftop solar installations that are not already accounted for in the baseline forecasts. The rooftop solar load reductions for the forecasted fall peak load hour is 561 MW. | Weather conditions at the time of peak are based on 2015’s weather to approximate 95th percentile weather These baseline forecasts are adjusted downwards to account for peak load reductions from rooftop solar installations that are not already accounted for in the baseline forecasts. The rooftop solar load reductions for the forecasted fall peak load hour is 561 MW.
Typical Planned Outages, Thermal | Based on historical average of Planned outages for October through November weekdays, hours ending 3 pm - 8 pm, for the last three years (2020 - 2022). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
Typical Unplanned Outages, Thermal | Based on historical average of Unplanned outages for October through November weekdays, hours ending 3 pm - 8 pm, for the last three years (2020 - 2022). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
Unplanned Outage Adjustments, Thermal | The High Unplanned Outage Adjustment is based on the 90th percentile of historical forced outages for October through November weekdays, hours ending 3 pm - 8 pm, for the last five fall seasons (2018 -2022); the adjustment is the 95th percentile value, 18,047 MW, less the typical forced outage amount of 12,006 MW. The outages for the High Unplanned Outage Adjustment include an incremental amount from Private Use Network (PUN) generators; specifically, the 90th percentile amount less the 50th percentile amount. See the Background tab for more information on the treatment of PUN capacity. Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators. | Based on the maximum historical forced outage level for October through November weekdays, hours ending 3 pm - 8 pm, for the last five fall seasons (2018 -2022); the adjustment is 21,495 MW, less the typical forced outage amount of 12,006 MW. The outages for the High Unplanned Outage Adjustment include an incremental amount from Private Use Network (PUN) generators; specifically, the 90th percentile amount less the 50th percentile amount. See the Background tab for more information on the treatment of PUN capacity. Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
Wind Output Adjustments | The adjustment is based on the 10th percentile of hourly wind capacity for the daily period hour-ending 16 through 17 (4 pm through 5 pm) for the months of October and November. The capacity values are derived from annual hourly simulated wind output profiles for the period 1980 - 2021 inclusive. The profiles reflect hourly weather conditions for each of the 42 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the 2022 Fall SARA. This low wind output level is 3,810 MW. The adjustment is the fall Peak Average Capacity Contribution, 12,686 MW, less 3,810 MW. The latest posted methodology report for profile development is available at: https://www.ercot.com/files/docs/2021/12/07/Report_ERCOT_1980-2020_WindSolarDGPVGenProfiles.pdf | The adjustments are based on the minimum hourly wind capacity value for the daily period hour-ending 16 through 17 (4 pm through 5 pm) for the months of October and November. The capacity values are derived from annual hourly simulated wind output profiles for the period 1980 - 2021 inclusive. The profiles reflect hourly weather conditions for each of the 42 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the 2022 Fall SARA. This extreme low wind output level is 182 MW. The adjustment is the fall Peak Average Capacity Contribution, 12,686 MW less 182 MW. Note that a scenario with a combined extreme peak load and extreme-low renewables output is not provided because an extreme peak load is associated with high solar output due to minimal cloud cover serving as a driver for both system conditions.
Solar Output Adjustments | The adjustment is based on the 10th percentile of hourly solar capacity for the daily period hour-ending 16 through 17 (4 pm through 5 pm) for the months of October and November. The capacity values are derived from annual hourly simulated wind output profiles for the period 1980 - 2021 inclusive. The profiles reflect hourly weather conditions for each of the 42 simulated weather years. A profile is developed for each current operational wind site as well as each planned wind site included in the 2022 Fall SARA. This low solar output level is 4,848 MW. The adjustment is the fall Peak Average Capacity Contribution, 11,663 MW, less 4,848 MW. The latest posted methodology report for profile development is available at: https://www.ercot.com/files/docs/2021/12/07/Report_ERCOT_1980-2020_WindSolarDGPVGenProfiles.pdf | No adjustment for solar is provided. A scenario with a combined extreme peak load and extreme-low renewables output (both wind and solar) is not provided because an extreme peak load is associated with high solar output due to minimal cloud cover serving as a driver for both system conditions.
Emergency Resources Deployed by ERCOT prior to EEA Declaration | An amount is only shown if Capacity Available for Operating Reserves, line item [g], is below 3,000 MW. Consists of the sum of (1) expected Emergency Response Service (1,103 MW) and (2) TDSP Distribution Voltage Reduction (562 MW), and (3) the expected peak consumption by operational LFLs at co-located and standalone sites (1,483 MW), which is assumed to be available for curtailment based on ERCOT requests to address an imminent capacity reserve shortage. The ERS and Distribution Voltage Reduction amounts reflect a 2% gross-up to account for avoided transmission losses. Other resources that may be available include voluntary customer Demand Response (including customer installation of backup generators), switchable generation resources currently serving the Eastern Interconnection, and additional DC tie imports subject to availability.
Emergency Resources Deployed by ERCOT | Amounts are shown when Capacity Available for Operating Reserves (CAFOR), line item [g], is below 2,300 MW. Expected resources available when an EEA is declared comprise the sum of Load Resources Available for Responsive Reserves (1,410 MW), Load Resources Available for Non-Spinning Reserve Service (77 MW), and Load Resources providing ERCOT Contingency Reserve Service (ECRS) (147 MW). Each of these amounts reflect a 2% gross-up to account for avoided transmission losses. Other resources that may be available include voluntary customer Demand Response (including customer installation of backup generators), switchable generation resources currently serving the Eastern Interconnection, and additional DC tie imports subject to availability. The voltage reduction amount comes from a presentation made at the ERCOT Operations Working Group meeting on March 24th, available at https://www.ercot.com/files/docs/2022/03/23/Distributed%20Voltage%20Reduction%20Survey%20Summary%20(2022%20March%20OWG).pptx.

## Background
Release Date: September 19, 2023
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (for example, an anticipated common-mode event such as a system-wide heat wave) which can be used to consider the range of resource adequacy outcomes in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses operating reserve thresholds of 2,300 and 1,000 MW, respectively, to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) and Level 3 (EEA3) may be triggered during the time of the forecasted seasonal peak load. These threshold levels are intended to be roughly analogous to the 2,300 and 1,000 MW Physical Responsive Capability (PRC) thresholds for EEA1 and EEA3 with controlled outages ordered by ERCOT, respectively. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 and 1,000 MW reserve capacity thresholds are reasonable indicators for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variations in these parameters are based on historic ranges of the parameter values, known changes expected in the near-term, or reasonable assumptions regarding potential future events.
Thermal Outage Accounting
Directly comparing SARA thermal unplanned (previously "forced") outage scenario capacity with outage amounts listed in ERCOT outage reports — such as the Unplanned Resource Outages Report — will yield misleading results. The reason is that the SARA report consists of multiple resource availability line items, and thermal outages for certain resource types are reflected elsewhere in the SARA reports rather than the thermal outage scenario line items. As a result, the SARA thermal outage scenario amounts will always be less than what is typically shown in other outage reports. The main differences include the following:
• Outages for Private Use Network (PUN) generators are incorporated in the line item called “Capacity from Private Use Networks.” This is an aggregate estimate of the amount of capacity available for the ERCOT grid during the highest 20 seasonal hourly demands for the last three years and incorporates average generator outage amounts over those hourly intervals. Additionally, the aggregate estimate reflects PUN owner decisions to supply power to their industrial loads versus export to the grid. PUN outages are thus already reflected in the SARA available resource capacity estimate.
• Extended outages are reported in the SARA Capacities tab in a line item called “Operational Capacity Unavailable due to Extended Outage or Derate.” Extended Outages are those forced outages that are expected to last a minimum of 180 days as reported by the resource owner via submission of a Notice of Suspension of Operations (NSO) form. These outages are thus already reflected in the SARA available resource capacity estimate.
• The capacity of Switchable Generation Resources (SWGRs) that are assumed to serve a neighboring grid for the season is deducted from available resource capacity, so outages associated with these SWGRs are not reflected anywhere in the SARA report.
To more closely align the SARA with other outage reports based on ERCOT Outage Scheduler data, a modification was made to the treatment of outages classified as Unavoidable Extensions, or UEs. UEs are defined as "a Planned or Maintenance Outage that is not completed within the ERCOT-approved timeframe and extended." For past SARA reports, if the original outage was classified as Planned in the Outage Scheduler, then the entire outage (including the UE portion) was classified as Planned. If the original outage was classified as Forced, then the entire outage (including UE portion) was classified as Forced. In contrast, for other ERCOT outage reports, UE outages are all classified as Forced (Unplanned). SARA reports now treat all UEs as Unplanned, as well as the orginial outage type if it is Planned. While this category change does not impact the total base outage amount, it does increase the high and extreme unplanned thermal adjustments used in several risk scenarios.
Accounting for Large Flexible Loads
Due to a new influx of Large Flexible Loads (LFLs), an interim solution was implemented to better account for the peak consumption of these loads. The new interim methodology utilizes the 20 hours over each of the past three years with the lowest average Physical Responsive Capability. The methodology compares historical load zone prices to an ERCOT determined (and industry backed) estimate of the bitcoin mining breakeven cost. This breakeven cost was estimated at $87/MWh and is based on the average economics of an Antminer S19 bitcoin mining rig from July 15th, 2023 through August 14th, 2023. If the historical load zone price for the LFL's respective load zone was below the breakeven threshold then the load's peak summer consumption was estimated to be the maximum observed consumption at the site according to internal tracking of LFL projects. If the historical load zone price was greater than the breakeven threshold then the LFL was assumed to be fully curtailed and consuming only 3% of the load's maximum capability. The 3% assumption accounts for the idle power draw of ASIC miners and necessary auxiliary cooling on site. The estimated consumption for each LFL, including both co-located and stand-alone loads, was summed for each of the 60 hours analyzed and then averaged to calculate the total estimated average consumption. This value was calculated to be 917 MW for stand-alone LFLs and 566 MW for co-located LFLs. This is reflected in item [c] as an adjustment to the baseline peak load forecast on the Base, Moderate & Extreme Risk Scenario tabs. The reported adjustment of 1,383 MW is the result of subtracting the 100 MW already allocated for peak LFL consumption in the baseline peak load forecast from the newly calculated average expected peak LFL consumption of 1,483 MW (917 MW + 566 MW). This adjustment reflects ERCOT's continuous effort to better understand and forecast the operations of Large Flexible Loads.