## Slide 1
Data Analyses on Large Loads
Evan Neel
Large Load Integration
ERCOT
Large Flexible Load Task Force
September 25, 2023
ERCOT Public

## Slide 2: Contents
Large Flexible Load Ramping Behavior
Large Flexible Load Price Responsiveness
Large Flexible Load September 6th EEA Behavior

## Slide 3: ERCOT Analysis Large Flexible Load Ramping Behavior

## Slide 4: Large Flexible Load Ramping Analysis – Background
Objective – Identify the number of SCED intervals in 2023 (through end of August) where LFL ramping exceeded procured Regulation.
Methodology
Change in LFL consumption was calculated as 5-min system wide deltas between the start of SCED intervals.
Those 5-min ramps were compared to the amount of regulation up/down (respective to ramp direction) that was procured for that interval (Month & HE).
If the LFL ramp exceeded the amount of procured regulation for that interval, it was counted. (See Appendix)

## Slide 5: Large Flexible Load Ramping Analysis – Background
Methodology (continued)
The analysis was then extended to project the potential impact of load growth identified through the interim interconnection queue.
In each case, 5-min ramps were multiplied by a scalar that was calculated by dividing the hypothetical load total by the rolling 24-hour max consumption.
  Projected to 2023 total Approved to Energize (3,077 MW)
  Projected to 2023 total Approved – Planning Studies Approved + Approved to Energize (9,734 MW)
The next few slides take a focused look at two months of interest – August & January.
Note that these stats are not indicating regulation exhaustion, but rather insufficient regulation to match LFL ramps 1-to-1. Any additional future procurement would account for other factors (like net-load ramp), as well.

## Slide 6: LFL Ramping Analysis – August (Historical Data)
Chart: Regulation Down (MW) Procurement vs. 5-min LFL Ramp - August
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Down Procured | 387 | 304 | 265 | 247 | 195 | 152 | 196 | 237 | 262 | 262 | 486 | 202 | 246 | 267 | 292 | 273 | 371 | 408 | 447 | 283 | 434 | 505 | 554 | 479
Max LFL Ramp | 197.996 | 85.2239 | 110.5099 | 109.9255 | 212.0172 | 176.4999 | 157.3179 | 171.4476 | 30.5439 | 241.4179 | 152.4855 | 204.6786 | 261.0788 | 461.4526 | 462.7966 | 303.7385 | 440.9936 | 369.0271 | 362.6165 | 407.2345 | 316.193 | 82.4774 | 271.8607 | 67.5685
Low | 0.0067444 | 0.0021973 | 0.0057678 | 0.038452 | 0.0030518 | 0.0073242 | 0.0098877 | 0.12012 | 0.035339 | 0.016968 | 0.00015259 | 0.05188 | 0.0065002 | 0.056488 | 0.089905 | 0.028742 | 0.045227 | 0.0065613 | 0.0012207 | 0.083282 | 0.1778 | 0.33203 | 0.019897 | 0.068939
Average LFL Ramp | 63.4732 | 50.4831 | 68.1333 | 52.9982 | 83.5799 | 62.896 | 71.6696 | 71.6234 | 30.5439 | 66.3644 | 69.0527 | 81.5125 | 70.1041 | 98.0494 | 114.214 | 92.3809 | 94.2638 | 97.51 | 92.7313 | 93.5924 | 79.5845 | 73.3872 | 94.1363 | 50.8881
Chart: Regulation Up (MW) Procurement vs. 5-min LFL Ramp - August
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Up Procured | 198 | 124 | 148 | 195 | 236 | 332 | 427 | 289 | 329 | 556 | 641 | 690 | 654 | 623 | 589 | 537 | 552 | 574 | 510 | 485 | 335 | 67 | 115 | 121
Max LFL Ramp | 94.6248 | 143.5826 | 72.4038 | 150.3384 | 95.1119 | 87.3564 | 88.8392 | 130.5234 | 113.9588 | 91.2163 | 57.3686 | 155.8209 | 100.1045 | 176.3213 | 139.7766 | 119.1763 | 132.6572 | 135.3586 | 263.047 | 144.526 | 207.0928 | 348.4976 | 224.8896 | 193.2516
Low | 0.0039062 | 0.019287 | 0.0042725 | 0.05481 | 0.0076294 | 0.051727 | 0.030029 | 0.013916 | 0.0028076 | 0.0071716 | 0.053467 | 0.099487 | 0.00085449 | 0.048828 | 0.1615 | 0.026408 | 0.040894 | 0.0091553 | 0.0095215 | 0.005127 | 0.032776 | 0.055054 | 0.075012 | 0.016479
Average LFL Ramp | 63.9831 | 62.757 | 48.004 | 61.7876 | 57.6013 | 63.2266 | 54.0089 | 62.2771 | 50.8937 | 64.8009 | 50.3881 | 62.0444 | 55.9474 | 60.7405 | 71.6938 | 62.0567 | 49.2724 | 69.2193 | 76.7926 | 54.8994 | 84.277 | 91.1188 | 67.3055 | 54.4977
LFL up-ramp in the late evening already exceeds current regulation-up procurement.
HE 22 has seen up-ramps 4x greater than currently procured reg-up.
Early afternoon (HE 12 – 17) has seen down-ramps in excess of available reg-down.
Current operations could potentially exacerbate the need to procure additional regulation services at a higher expense to the system.

## Slide 7: LFL Ramping Analysis – August (Projected to Approved to Energize)
Projecting to the total approved to energize in 2023 (a very sensible projection) exacerbates already existing regulation shortages.
With this amount of load, average LFL up-ramp for HE 22 is projected to exceed procured reg-up by a considerable margin.
The majority of hours could potentially see down ramps that are not covered 1-to-1 by current regulation procurements.
Chart: Regulation Up (MW) Procurement vs. 5-min LFL Ramp - August
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Up Procured | 198 | 124 | 148 | 195 | 236 | 332 | 427 | 289 | 329 | 556 | 641 | 690 | 654 | 623 | 589 | 537 | 552 | 574 | 510 | 485 | 335 | 67 | 115 | 121
Max LFL Ramp | 150.0241 | 224.9707 | 114.327 | 237.3211 | 150.1417 | 135.1308 | 139.1967 | 204.5091 | 176.2817 | 143.8686 | 90.586 | 245.9755 | 155.7503 | 278.4146 | 216.4502 | 188.1292 | 209.4099 | 213.754 | 410.8961 | 224.6635 | 316.9445 | 557.4681 | 355.1049 | 298.939
Low | 0.006121 | 0.029835 | 0.0067479 | 0.086899 | 0.011814 | 0.080409 | 0.046452 | 0.021632 | 0.0043477 | 0.011269 | 0.083519 | 0.15713 | 0.0013484 | 0.076468 | 0.25605 | 0.041252 | 0.063258 | 0.014162 | 0.014744 | 0.0081286 | 0.05095 | 0.085162 | 0.11661 | 0.026021
Average LFL Ramp | 100.5275 | 98.2282 | 75.2243 | 96.9201 | 90.1032 | 98.5512 | 84.2203 | 97.5848 | 79.4579 | 101.8739 | 79.3148 | 97.5102 | 87.4677 | 95.2183 | 112.374 | 97.3377 | 77.0837 | 108.6772 | 120.4656 | 86.1478 | 131.845 | 142.6255 | 105.3432 | 85.286
Chart: Regulation Down (MW) Procurement vs. 5-min LFL Ramp - August
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Down Procured | 387 | 304 | 265 | 247 | 195 | 152 | 196 | 237 | 262 | 262 | 486 | 202 | 246 | 267 | 292 | 273 | 371 | 408 | 447 | 283 | 434 | 505 | 554 | 479
Max LFL Ramp | 312.5523 | 134.5327 | 174.4972 | 173.5261 | 329.5777 | 278.6966 | 248.2552 | 266.0061 | 48.2408 | 378.2629 | 240.7774 | 323.1014 | 412.2483 | 731.6159 | 725.1277 | 475.6734 | 682.8979 | 582.3427 | 566.43 | 638.1245 | 494.3617 | 129.2287 | 426.6653 | 106.6919
Low | 0.010484 | 0.0034091 | 0.0089691 | 0.060814 | 0.0048133 | 0.011429 | 0.015574 | 0.18763 | 0.055344 | 0.026331 | 0.00023908 | 0.080252 | 0.010154 | 0.08956 | 0.14187 | 0.045976 | 0.070981 | 0.01015 | 0.0018883 | 0.13136 | 0.28081 | 0.51912 | 0.031383 | 0.10769
Average LFL Ramp | 100.0312 | 79.0101 | 106.8728 | 83.1093 | 130.2104 | 98.5911 | 112.0465 | 111.3443 | 48.2408 | 103.9444 | 108.7271 | 128.1383 | 109.8563 | 153.2847 | 178.5039 | 144.9281 | 147.3277 | 152.8839 | 145.4248 | 146.9162 | 125.1217 | 115.4781 | 147.3709 | 80.3472

## Slide 8: LFL Ramping Analysis – August (Projected to All Approved)
Extension – If the ~9.7 GW of LFLs with approved planning studies were to connect and exhibit similar ramping behavior, it would present a significant reliability risk in August.
Considerable increases in regulation procurement could potentially be needed for many hours.
This could potentially require reserving hundreds of MW behind HASL – increasing procurement costs and reducing available MW dispatchable by SCED.
Chart: Regulation Up (MW) Procurement vs. 5-min LFL Ramp - August
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Up Procured | 198 | 124 | 148 | 195 | 236 | 332 | 427 | 289 | 329 | 556 | 641 | 690 | 654 | 623 | 589 | 537 | 552 | 574 | 510 | 485 | 335 | 67 | 115 | 121
Max LFL Ramp | 455.0941 | 682.4428 | 346.8079 | 719.9073 | 455.451 | 409.9158 | 422.2497 | 620.3731 | 534.746 | 436.4217 | 274.7904 | 746.1604 | 472.4644 | 844.5635 | 656.5962 | 570.6851 | 635.2396 | 648.4171 | 1246.4426 | 681.5111 | 961.443 | 1691.065 | 1077.2015 | 906.8238
Low | 0.018568 | 0.090504 | 0.02047 | 0.2636 | 0.035839 | 0.24392 | 0.14091 | 0.065621 | 0.013189 | 0.034184 | 0.25335 | 0.47665 | 0.0040904 | 0.23196 | 0.77672 | 0.12514 | 0.19189 | 0.042961 | 0.044727 | 0.024658 | 0.15455 | 0.25834 | 0.35372 | 0.078935
Average LFL Ramp | 304.9475 | 297.9727 | 228.1909 | 294.0046 | 273.3257 | 298.9525 | 255.4802 | 296.0211 | 241.0334 | 309.0319 | 240.5995 | 295.7948 | 265.3312 | 288.8424 | 340.8836 | 295.2713 | 233.8314 | 329.6694 | 365.4292 | 261.3271 | 399.9484 | 432.6508 | 319.556 | 258.7128
Chart: Regulation Down (MW) Procurement vs. 5-min LFL Ramp - August
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Down Procured | 387 | 304 | 265 | 247 | 195 | 152 | 196 | 237 | 262 | 262 | 486 | 202 | 246 | 267 | 292 | 273 | 371 | 408 | 447 | 283 | 434 | 505 | 554 | 479
Max LFL Ramp | 948.1193 | 408.1014 | 529.3328 | 526.3869 | 999.7653 | 845.4189 | 753.0758 | 806.9225 | 146.3373 | 1147.4507 | 730.392 | 980.1197 | 1250.5445 | 2219.338 | 2199.6561 | 1442.9431 | 2071.553 | 1766.5215 | 1718.2508 | 1935.7342 | 1499.6334 | 392.012 | 1294.2783 | 323.6471
Low | 0.031803 | 0.010341 | 0.027208 | 0.18448 | 0.014601 | 0.034669 | 0.047242 | 0.56917 | 0.16788 | 0.079874 | 0.00072524 | 0.24344 | 0.030801 | 0.27168 | 0.43037 | 0.13947 | 0.21532 | 0.030788 | 0.0057281 | 0.39846 | 0.85183 | 1.5748 | 0.095199 | 0.32667
Average LFL Ramp | 303.4421 | 239.675 | 324.1959 | 252.1099 | 394.9897 | 299.0736 | 339.89 | 337.7599 | 146.3373 | 315.3126 | 329.8209 | 388.7043 | 333.2463 | 464.9851 | 541.4869 | 439.6358 | 446.9148 | 463.7694 | 441.1422 | 445.6666 | 379.5533 | 350.2998 | 447.0457 | 243.7311

## Slide 9: LFL Ramping Analysis – January (Historical Data)
Winter months are also seeing considerable LFL ramps.
A total of 6 hours had ramps that exceeded the total procured regulation.
Most of these exceedances occurred during down ramps across several hours spread throughout the month.
Chart: Regulation Up (MW) Procurement vs. 5-min LFL Ramp - January
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Up Procured | 241 | 197 | 255 | 266 | 351 | 535 | 644 | 393 | 311 | 399 | 412 | 353 | 378 | 330 | 371 | 448 | 724 | 850 | 390 | 238 | 245 | 186 | 209 | 212
Max LFL Ramp | 186.665 | 88.1726 | 129.9863 | 219.8475 | 146.702 | 163.4325 | 183.5127 | 132.0316 | 247.764 | 231.0391 | 119.7898 | 75.4149 | 82.331 | 187.6572 | 124.5182 | 69.1802 | 127.981 | 152.2503 | 133.1149 | 289.0052 | 218.183 | 145.7491 | 172.5106 | 165.183
Low | 0.0045471 | 0.00038147 | 0.012329 | 0.005127 | 0.0015564 | 0.015472 | 0.028198 | 0.011292 | 0.042847 | 0.022858 | 0.014648 | 0.0036621 | 0.0068359 | 0.00018311 | 0.041504 | 0.0054932 | 0.014771 | 0.010437 | 0.018768 | 0.0027924 | 0.0025177 | 0.0034485 | 0.041168 | 0.018829
Average LFL Ramp | 69.6883 | 58.3424 | 64.4614 | 69.803 | 56.508 | 66.9636 | 59.5294 | 66.325 | 66.3386 | 72.6107 | 63.2895 | 51.7887 | 54.8562 | 68.3381 | 60.3646 | 43.3272 | 65.7681 | 66.3396 | 57.5174 | 70.6612 | 81.0929 | 68.3813 | 64.2193 | 65.1595
Chart: Regulation Down (MW) Procurement vs. 5-min LFL Ramp - January
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Down Procured | 276 | 223 | 217 | 245 | 204 | 294 | 247 | 219 | 747 | 549 | 490 | 454 | 414 | 386 | 442 | 388 | 299 | 224 | 303 | 267 | 284 | 305 | 389 | 337
Max LFL Ramp | 194.9564 | 91.5554 | 244.8377 | 168.7982 | 288.5305 | 182.108 | 234.4211 | 251.3026 | 166.8558 | 262.2639 | 204.6184 | 156.9208 | 212.3128 | 118.7648 | 186.611 | 127.1355 | 249.2185 | 233.7185 | 248.2019 | 319.3653 | 154.5243 | 228.561 | 220.1002 | 282.9335
Low | 0.012695 | 0.010376 | 0.00076294 | 7.6294e-05 | 0.011047 | 0.0061035 | 0.025879 | 0.016235 | 0.036224 | 0.00024414 | 0.0062256 | 0.011444 | 0.016602 | 0.0383 | 0.0038452 | 0.02832 | 0.035126 | 0.0090332 | 0.050415 | 0.034332 | 0.0063782 | 0.0016174 | 0.0056763 | 0.0029297
Average LFL Ramp | 94.1709 | 56.1301 | 81.6051 | 78.2679 | 86.6508 | 102.1408 | 152.6411 | 120.9375 | 95.1756 | 112.1463 | 104.956 | 95.2772 | 95.9414 | 87.3226 | 87.0353 | 66.3754 | 95.8517 | 111.2328 | 116.1228 | 98.8645 | 87.768 | 103.6674 | 88.5157 | 97.1083

## Slide 10: LFL Ramping Analysis – January (Projected to Approved to Energize)
Projecting to the total approved to energize to date, shows LFLs could utilize the majority of currently procured regulation in winter months.
In several case, the average ramp exceeds the amount of reg down procured.
Behavior demonstrates a pattern of ramping load up/down around system solar ramps. This will need to be accounted for in the future.
Chart: Regulation Up (MW) Procurement vs. 5-min LFL Ramp - January
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Up Procured | 241 | 197 | 255 | 266 | 351 | 535 | 644 | 393 | 311 | 399 | 412 | 353 | 378 | 330 | 371 | 448 | 724 | 850 | 390 | 238 | 245 | 186 | 209 | 212
Max LFL Ramp | 402.8133 | 189.3449 | 246.6907 | 474.4194 | 324.7807 | 361.82 | 394.0815 | 244.6829 | 470.2117 | 498.5703 | 249.9343 | 161.9487 | 179.8081 | 404.9545 | 269.1872 | 151.0871 | 276.1762 | 298.9091 | 278.8373 | 632.3519 | 486.0506 | 285.0408 | 355.285 | 357.0975
Low | 0.0094873 | 0.00083312 | 0.024071 | 0.0099175 | 0.0033647 | 0.030492 | 0.058074 | 0.024998 | 0.09201 | 0.046304 | 0.0278 | 0.0078641 | 0.013223 | 0.00036122 | 0.085477 | 0.012008 | 0.029138 | 0.021495 | 0.039159 | 0.0059964 | 0.0054081 | 0.0069858 | 0.083396 | 0.036467
Average LFL Ramp | 149.1714 | 123.5908 | 130.2915 | 150.7236 | 117.6157 | 137.3218 | 121.556 | 131.0926 | 136.9284 | 155.6857 | 133.9394 | 107.1411 | 109.5129 | 147.0578 | 130.6013 | 93.309 | 140.7799 | 138.2097 | 119.1154 | 147.2333 | 170.2684 | 139.3331 | 136.6366 | 139.4531
Chart: Regulation Down (MW) Procurement vs. 5-min LFL Ramp - January
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Down Procured | 276 | 223 | 217 | 245 | 204 | 294 | 247 | 219 | 747 | 549 | 490 | 454 | 414 | 386 | 442 | 388 | 299 | 224 | 303 | 267 | 284 | 305 | 389 | 337
Max LFL Ramp | 431.61 | 191.0249 | 464.658 | 373.699 | 547.5791 | 375.0509 | 503.404 | 461.7187 | 306.5646 | 547.1981 | 439.4046 | 288.3109 | 415.9776 | 256.2882 | 403.4211 | 274.3517 | 537.8006 | 510.433 | 486.2939 | 625.7221 | 303.3736 | 493.2227 | 453.2956 | 610.5556
Low | 0.028106 | 0.021369 | 0.0015456 | 0.00016662 | 0.021645 | 0.011983 | 0.048363 | 0.032522 | 0.07926 | 0.00046334 | 0.012042 | 0.022576 | 0.034634 | 0.080657 | 0.0075074 | 0.052033 | 0.07543 | 0.017565 | 0.097822 | 0.076008 | 0.012453 | 0.0034966 | 0.012189 | 0.0054293
Average LFL Ramp | 204.6149 | 115.9503 | 171.4234 | 165.5948 | 177.8964 | 208.5659 | 307.8657 | 243.4907 | 193.6466 | 236.9784 | 223.2289 | 185.0092 | 203.0089 | 188.6259 | 188.2943 | 136.274 | 206.2025 | 234.2717 | 233.7181 | 203.4749 | 187.9353 | 217.3668 | 185.2931 | 206.2881

## Slide 11: LFL Ramping Analysis – January (Projected to All Approved)
Extension – If the ~9.7 GW of LFLs with approved planning studies were to connect and exhibit similar ramping behavior, it would present a significant reliability risk in January.
Additional regulation procurement to match LFL ramps 1-to-1 on this scale is infeasible.
Load in SCED (CLR) would help mitigate this impact.
Chart: Regulation Up (MW) Procurement vs. 5-min LFL Ramp - January
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Up Procured | 241 | 197 | 255 | 266 | 351 | 535 | 644 | 393 | 311 | 399 | 412 | 353 | 378 | 330 | 371 | 448 | 724 | 850 | 390 | 238 | 245 | 186 | 209 | 212
Max LFL Ramp | 1221.9236 | 574.3728 | 748.3299 | 1439.1391 | 985.2138 | 1097.5716 | 1195.436 | 742.2394 | 1426.375 | 1512.4003 | 758.1692 | 491.2671 | 545.4431 | 1228.4191 | 816.5723 | 458.3187 | 837.7735 | 906.733 | 845.8457 | 1918.2231 | 1474.4219 | 864.6638 | 1077.7477 | 1083.2459
Low | 0.028779 | 0.0025272 | 0.07302 | 0.030085 | 0.010207 | 0.092497 | 0.17617 | 0.075831 | 0.27911 | 0.14046 | 0.084331 | 0.023856 | 0.04011 | 0.0010958 | 0.25929 | 0.036427 | 0.088391 | 0.065204 | 0.11879 | 0.01819 | 0.016405 | 0.021191 | 0.25298 | 0.11062
Average LFL Ramp | 452.5076 | 374.9096 | 395.2359 | 457.2162 | 356.7842 | 416.5622 | 368.7369 | 397.666 | 415.3689 | 472.2685 | 406.3016 | 325.0099 | 332.2047 | 446.0959 | 396.1756 | 283.0505 | 427.0522 | 419.2556 | 361.3336 | 446.6283 | 516.5049 | 422.6635 | 414.4836 | 423.0275
Chart: Regulation Down (MW) Procurement vs. 5-min LFL Ramp - January
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Reg Down Procured | 276 | 223 | 217 | 245 | 204 | 294 | 247 | 219 | 747 | 549 | 490 | 454 | 414 | 386 | 442 | 388 | 299 | 224 | 303 | 267 | 284 | 305 | 389 | 337
Max LFL Ramp | 1309.2779 | 579.4692 | 1409.5281 | 1133.6062 | 1661.0672 | 1137.7071 | 1527.0632 | 1400.6118 | 929.9557 | 1659.9112 | 1332.9225 | 874.5835 | 1261.8572 | 777.4436 | 1223.7675 | 832.2388 | 1631.4042 | 1548.3854 | 1475.16 | 1898.1118 | 920.2759 | 1496.1783 | 1375.0606 | 1852.1048
Low | 0.085259 | 0.064823 | 0.0046884 | 0.00050545 | 0.065659 | 0.03635 | 0.14671 | 0.098656 | 0.24043 | 0.0014055 | 0.036529 | 0.068485 | 0.10506 | 0.24467 | 0.022774 | 0.15784 | 0.22882 | 0.053283 | 0.29674 | 0.23057 | 0.037775 | 0.010607 | 0.036976 | 0.01647
Average LFL Ramp | 620.6939 | 351.7323 | 520.0083 | 502.3275 | 539.6442 | 632.6793 | 933.9027 | 738.6226 | 587.4221 | 718.8679 | 677.1592 | 561.2207 | 615.8223 | 572.1918 | 571.186 | 413.3837 | 625.51 | 710.6573 | 708.9779 | 617.236 | 570.0969 | 659.3766 | 562.0819 | 625.7698

## Slide 12: ERCOT Analysis Large Flexible Load Price Responsiveness

## Slide 13: Analysis of Price Responsive Behavior – Background
Objective – Determine the amount of price responsive behavior exhibited by large loads tracked via the interim process once in operation.
Methodology
For every 5 min interval from Oct-22 through Aug-23 the theoretical strike price for an S19 XP was calculated and compared to respective LZ settlement prices.
  If the settlement price exceeded the theoretical strike price, it was assumed that the load should curtail for that interval.
The loads were considered to have curtailed if their consumption at the end of the interval was less than 20% of their rolling 24-hour average consumption (MW).
Ancillary service obligations were subtracted from the calculation as to not skew the data. A load with AS obligations greater than 75% if its max consumption was considered “not to have curtailed”.
Percentages of intervals where the load curtailed when expected to (based on S19 XP) were calculated for all loads.

## Slide 14: Analysis of Price Responsive Behavior – Background
Input from the Loads
Part of this analysis included outreach to owners and operators of data center and cryptomining loads. While all loads indicated they were flexible in response to prices, many loads cited various limitations to the simple strike price/spot price strategy:
  Risk adjustments to strike prices due to 15-minute settlement intervals.
  Unique operational nuances associated with long term power purchase agreements.
  Third-party hosting agreements/contracts with uptime requirements that result in either a limitation of flexibility, or additional hedges that get factored into the overall strike price.
All of these factors are traditionally unknown to ERCOT and make passive price response forecasting incredibly difficult.

## Slide 15: Analysis of Price Responsive Behavior – ERCOT Observations
 | Non 4CP | All | 4CP
LFL 1 | 12% | 37% | 54%
LFL 2 | 28% | 52% | 59%
LFL 3 | 22% | 58% | 81%
LFL 4 | 35% | 52% | 75%
LFL 5 | 40% | 66% | 81%
LFL 6 | 46% | 72% | 74%
LFL 7 | 48% | 64% | 89%
LFL 8 | 57% | 70% | 89%
LFL 9 | 58% | 70% | 89%
LFL 10 | 71% | 77% | 86%
LFL 11 | 79% | 81% | 86%
LFL 12 | 75% | 84% | 89%
LFL 13 | 75% | 82% | 93%
LFL 14 | 85% | 87% | 90%
LFL 15 | 97% | 88% | 84%
LFL 16 | 92% | 95% | 99%
LFL 17 | 94% | 96% | 99%
LFL 18 | 96% | 97% | 99%
AVG | 62% | 74% | 84%
AVG (Weighted) | 48% | 66% | 79%
Chart: Percentage of 5-min Intervals where LFLs Curtailed for High Prices (OCT-22 through AUG-23)
| LFL 1 | LFL 2 | LFL 3 | LFL 4 | LFL 5 | LFL 6 | LFL 7 | LFL 8 | LFL 9 | LFL 10 | LFL 11 | LFL 12 | LFL 13 | LFL 14 | LFL 15 | LFL 16 | LFL 17 | LFL 18
4CP Months | 0.5407 | 0.59185 | 0.81288 | 0.74808 | 0.81274 | 0.73569 | 0.89499 | 0.89086 | 0.89322 | 0.86313 | 0.85605 | 0.88714 | 0.92979 | 0.90088 | 0.83544 | 0.99469 | 0.98761 | 0.9882
Non 4CP Months | 0.11974 | 0.28458 | 0.21983 | 0.35323 | 0.39663 | 0.45968 | 0.48073 | 0.57431 | 0.57908 | 0.71119 | 0.78789 | 0.74607 | 0.74972 | 0.85138 | 0.96676 | 0.91706 | 0.94212 | 0.95986
All Months | 0.37495 | 0.51785 | 0.57937 | 0.52383 | 0.66317 | 0.71688 | 0.63959 | 0.6957 | 0.69955 | 0.76946 | 0.81403 | 0.83643 | 0.81878 | 0.87036 | 0.87767 | 0.94683 | 0.96409 | 0.97107
Price responsive capabilities vary greatly between loads. The data suggests that many LFLs are primarily responding to 4CP intervals rather than high-price intervals.
The degree to which loads are 4CP vs Price sensitive is demonstrated by their spread. A larger spread indicates a load is primarily responding to 4CP, or their economic curtailment strategy has greatly improved in recent months.
As indicated by the load weighted averages, larger loads are worse at responding to high prices on average.

## Slide 16: Analysis of Price Responsive Behavior – ERCOT Observations
Chart: Percentage of 5-min Intervals where LFLs Curtailed for High Prices (OCT-22 through AUG-23)
| LFL 1 | LFL 2 | LFL 3 | LFL 4 | LFL 5 | LFL 6 | LFL 7 | LFL 8 | LFL 9 | LFL 10 | LFL 11 | LFL 12 | LFL 13 | LFL 14 | LFL 15 | LFL 16 | LFL 17 | LFL 18
4CP Months | 0.5407 | 0.59185 | 0.81288 | 0.74808 | 0.81274 | 0.73569 | 0.89499 | 0.89086 | 0.89322 | 0.86313 | 0.85605 | 0.88714 | 0.92979 | 0.90088 | 0.83544 | 0.99469 | 0.98761 | 0.9882
Non 4CP Months | 0.11974 | 0.28458 | 0.21983 | 0.35323 | 0.39663 | 0.45968 | 0.48073 | 0.57431 | 0.57908 | 0.71119 | 0.78789 | 0.74607 | 0.74972 | 0.85138 | 0.96676 | 0.91706 | 0.94212 | 0.95986
All Months | 0.37495 | 0.51785 | 0.57937 | 0.52383 | 0.66317 | 0.71688 | 0.63959 | 0.6957 | 0.69955 | 0.76946 | 0.81403 | 0.83643 | 0.81878 | 0.87036 | 0.87767 | 0.94683 | 0.96409 | 0.97107
This has significant impacts for load forecasting
  Highly price sensitive loads can be forecasted since their behavior is consistent. (Green)
  Primarily 4CP Only-responsive loads can be forecasted to some extent. (Yellow)
  Other loads are not easily forecasted without additional information. (Red)

## Slide 17: Price Responsiveness of LFLs – By the Hour
Chart: Count of 5-min Intervals where LFLs did not Curtail During High Prices
Non 4CP Months | 381 | 389 | 465 | 540 | 464 | 532 | 546 | 651 | 275 | 136 | 110 | 67 | 47 | 147 | 197 | 254 | 508 | 1223 | 1020 | 925 | 982 | 447 | 283 | 453
4CP Months | 122 | 112 | 43 | 10 | 9 | 55 | 96 | 27 | 0 | 0 | 26 | 106 | 55 | 328 | 417 | 368 | 353 | 292 | 445 | 950 | 584 | 391 | 133 | 67
Overall pattern indicates a correlation to net-load and respective price action.
Failure to curtail during 4CP months is most prominent from HE 14 to HE 22.
  No 4CP risk and no economic curtailment
  Loads returning from 4CP curtailment while prices are still high (and conditions are potentially tight)

## Slide 18: ERCOT Analysis Large Flexible Load September 6th EEA Behavior

## Slide 19: September 6th Large Load Behavior – Price
Chart: September 6th Large Flexible Load Behavior
LFL curtailment begins around 11:30 am when system prices begin to touch the breakeven cost. This is likely combined with typical 4CP behavior.
$85/MWh
The orange line indicates an approximate strike price estimate for LFLs participating in bitcoin mining. This was calculated based on an S19 j Pro and network metrics from the afternoon of 9/6.
LFL load ramped up at ~6:30 pm to meet a RRS & ECRS obligation at 7 pm.
LFLs returned in mass once prices stabilized under the strike price threshold (9 - 11 pm).
Max 5 min Up Ramp: 242 MW
Max 5 min Down Ramp: 391 MW

## Slide 20: September 6th Large Load Behavior – PRC
Chart: September 6th Large Flexible Load Behavior - PRC
Early LFL ramp up for AS obligations helped contribute to falling PRC (~150 MW).
ECRS was deployed nearly instantaneously upon ramping up for obligation.
PRC drop stabilized shortly after RRS was deployed.
PRC was above 5,000 MW before the majority of LFLs began ramping up their consumption later in the evening.
The Large Flexible Load Task Force may want to explore solutions on how to efficiently prevent loads ramping up just to meet AS obligations that will be immediately deployed in emergency conditions.

## Slide 21: Questions?
email: evan.neel@ercot.com

## Slide 22: Appendix

## Slide 23: LFL Ramping Analysis – 100% Reg Exceedance (Historical)

## Slide 24: LFL Ramping Analysis – 50% Reg Exceedance (Historical)

## Slide 25: LFL Ramping Analysis – 100% Reg Exceedance (Approved to Energize)

## Slide 26: LFL Ramping Analysis – 100% Reg Exceedance (All Approved)