## Slide 1
ERCOT 2023 UFLS Survey Results
ERCOT Compliance

## Slide 2: Background on the ERCOT UFLS Survey and Requirements
ERCOT coordinated and conducted the 2023 survey with ERCOT Transmission Operators (TOs.) The survey serves to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event.
The table below is taken from the ERCOT Nodal Operating Guides, Section 2.6.1 (1), Requirements for Under-Frequency Load Shedding, and lists the required load shed amounts:
Frequency Threshold | Load Relief
59.3 Hz | At least 5% of the TO Load
58.9 Hz | A total of at least 15% of the TO Load
58.5 Hz | A total of at least 25% of the TO Load
ERCOT Nodal Operating Guides, Section 2.6.1 (2)
  ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC). For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.

## Slide 3: 2023 UFLS Survey Activity Timeline
Below is the timeline reflecting the survey dates and activities:
Date | Activity
March 16 | Announcement of survey timeline to OWG
March 30 | Market Notice sent to Authorized TO Representatives
May 11 @ 11:00 AM | Date and time of survey
July 14 | Survey results due to ERCOT
August 17 | Results reported to OWG
September 7 | Results reported to ROS
September 26 | Results reported to TAC

## Slide 4: Survey Results
The overall results of the 2023 UFLS survey are reflected in the table below:
TOs successfully met the UFLS requirements for all three thresholds.
The ERCOT load at the time of the survey was 51,290 MW. In comparison, the 2022 survey overall result was 32.62% at 52,825 MW of load.
Frequency Threshold | Minimum Requirement | Survey Measurement
59.3 Hz | At least 5% of the TO Load | 7.06%
58.9 Hz | A total of at least 15% of the TO Load | 18.93%
58.5 Hz | A total of at least 25% of the TO Load | 30.95%

## Slide 5: Optional Supplemental Anti-Stall UFLS Stages
ERCOT Nodal Operating Guides 2.6.1 (3)
A TO may meet the Load relief requirements of the Supplemental anti-stall UFLS stages by utilizing Load that would otherwise be utilized to meet the 58.9 Hz and 58.5 Hz standard UFLS stages. In this circumstance, the TO’s Load relief responsibility at the 58.9 and 58.5 Hz standard UFLS stages is reduced by the amount of Load already shed in the supplemental anti-stall UFLS stages. A TO may not meet the Load relief requirements of the supplemental anti-stall UFLS stages by utilizing Load that the TO needs to meet the 59.3 Hz standard UFLS stage.
Reference: ERCOT Nodal Operating Guides Section 2: System Operations and Control Requirements
Frequency Threshold | Minimum Requirement | Delay to Trip
59.5 Hz | At least 1.5% of the TO Load | 90 seconds
59.5 Hz | A total of at least 3.0% of the TO Load | 120 seconds
59.5 Hz | A total of at least 4.5% of the TO Load | 150 seconds

## Slide 6: Conclusion
ERCOT Compliance appreciates all entities participation in the 2023 UFLS Survey.
Questions or Comments?