## 2023 RRS Table
| Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
(MW)
*RRS Curr IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3088 | 3015 | 2982 | 2936 | 2898 | 2825 | 2732 | 2668
**RRS Upd IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3088 | 3015 | 2982 | 2936 | 2898 | 2825 | 2732 | 2668
| Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:01 | 1:01 | 1:01 | 1:01 | 1:01
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2618 | 2571 | 2538 | 2498 | 2450 | 2416 | 2375 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2618 | 2571 | 2538 | 2498 | 2450 | 2416 | 2375 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068

## 2023_RRS
2023 RRS (Floor = 2800 MW for peak hours ¦ Floor = 2300 MW for remaining hours, new minimum RRS-PFR limit =1390 MW)
HE | Jan | Feb | Mar | Apr | May | Jun | July | Aug | Sep | Oct | Nov | Dec
1 | 3041 | 3079 | 3335 | 3195 | 3041 | 2651 | 2517 | 2466 | 2705 | 3079 | 3195 | 3156
2 | 3041 | 3079 | 3335 | 3195 | 3041 | 2651 | 2517 | 2466 | 2705 | 3079 | 3195 | 3156
3 | 2991 | 3041 | 3335 | 3239 | 3041 | 2774 | 2562 | 2562 | 2774 | 3156 | 3195 | 3195
4 | 2991 | 3041 | 3335 | 3239 | 3041 | 2774 | 2562 | 2562 | 2774 | 3156 | 3195 | 3195
5 | 2991 | 3041 | 3335 | 3239 | 3041 | 2774 | 2562 | 2562 | 2774 | 3156 | 3195 | 3195
6 | 2991 | 3041 | 3335 | 3239 | 3041 | 2774 | 2562 | 2562 | 2774 | 3156 | 3195 | 3195
7 | 2871 | 2991 | 3239 | 3156 | 2949 | 2651 | 2517 | 2466 | 2651 | 2991 | 3041 | 3079
8 | 2871 | 2991 | 3239 | 3156 | 2949 | 2651 | 2517 | 2466 | 2651 | 2991 | 3041 | 3079
9 | 2871 | 2991 | 3239 | 3156 | 2949 | 2651 | 2517 | 2466 | 2651 | 2991 | 3041 | 3079
10 | 2871 | 2991 | 3239 | 3156 | 2949 | 2651 | 2517 | 2466 | 2651 | 2991 | 3041 | 3079
11 | 2949 | 3041 | 3239 | 3041 | 2774 | 2381 | 2300 | 2300 | 2427 | 2871 | 3041 | 2991
12 | 2949 | 3041 | 3239 | 3041 | 2774 | 2381 | 2300 | 2300 | 2427 | 2871 | 3041 | 2991
13 | 2949 | 3041 | 3239 | 3041 | 2774 | 2381 | 2300 | 2300 | 2427 | 2871 | 3041 | 2991
14 | 2949 | 3041 | 3239 | 3041 | 2774 | 2381 | 2300 | 2300 | 2427 | 2871 | 3041 | 2991
15 | 2991 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2949
16 | 2991 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2949
17 | 2991 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2949
18 | 2991 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2949
19 | 2949 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2949
20 | 2949 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2949
21 | 2949 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2949
22 | 2949 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2949
23 | 3041 | 3079 | 3335 | 3195 | 3041 | 2651 | 2517 | 2466 | 2705 | 3079 | 3195 | 3156
24 | 3041 | 3079 | 3335 | 3195 | 3041 | 2651 | 2517 | 2466 | 2705 | 3079 | 3195 | 3156
Total | 71168 | 72536 | 78152 | 74452 | 69620 | 64228 | 61984 | 61576 | 64628 | 70788 | 73816 | 73276
These preliminary 2023 quantities above are based on the 2023 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1390 MW and a floor of 2300 MW across all hours. Note that, NERC’s preliminary 2024 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows an increase in ERCOT’s IFRO. As a result of this ERCOT expects that the minimum RRS-PFR limit for 2023 will change to align with ERCOT's new IFRO.

## 2023_RRS_Details
2023-01-01 | [5 empty] | 2023-02-01 | [5 empty] | 2023-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 1 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 1 | 3335 | 1390 | 1945 | 2.35 | 58.32%
2 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 2 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 2 | 3335 | 1390 | 1945 | 2.35 | 58.32%
3 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 3 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 3 | 3335 | 1390 | 1945 | 2.35 | 58.32%
4 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 4 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 4 | 3335 | 1390 | 1945 | 2.35 | 58.32%
5 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 5 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 5 | 3335 | 1390 | 1945 | 2.35 | 58.32%
6 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 6 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 6 | 3335 | 1390 | 1945 | 2.35 | 58.32%
7 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 7 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 7 | 3239 | 1390 | 1849 | 2.06 | 57.09%
8 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 8 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 8 | 3239 | 1390 | 1849 | 2.06 | 57.09%
9 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 9 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 9 | 3239 | 1390 | 1849 | 2.06 | 57.09%
10 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 10 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 10 | 3239 | 1390 | 1849 | 2.06 | 57.09%
11 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 11 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 11 | 3239 | 1390 | 1849 | 2.06 | 57.09%
12 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 12 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 12 | 3239 | 1390 | 1849 | 2.06 | 57.09%
13 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 13 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 13 | 3239 | 1390 | 1849 | 2.06 | 57.09%
14 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 14 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 14 | 3239 | 1390 | 1849 | 2.06 | 57.09%
15 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 15 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 15 | 3195 | 1390 | 1805 | 1.94 | 56.49%
16 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 16 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 16 | 3195 | 1390 | 1805 | 1.94 | 56.49%
17 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 17 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 17 | 3195 | 1390 | 1805 | 1.94 | 56.49%
18 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 18 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 18 | 3195 | 1390 | 1805 | 1.94 | 56.49%
19 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 19 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 19 | 3195 | 1390 | 1805 | 1.94 | 56.49%
20 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 20 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 20 | 3195 | 1390 | 1805 | 1.94 | 56.49%
21 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 21 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 21 | 3195 | 1390 | 1805 | 1.94 | 56.49%
22 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 22 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 22 | 3195 | 1390 | 1805 | 1.94 | 56.49%
23 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 23 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 23 | 3335 | 1390 | 1945 | 2.35 | 58.32%
24 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 24 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 24 | 3335 | 1390 | 1945 | 2.35 | 58.32%
2023-04-01 | [5 empty] | 2023-05-01 | [5 empty] | 2023-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 1 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 1 | 2651 | 1390 | 1261 | 1.28 | 47.57%
2 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 2 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 2 | 2651 | 1390 | 1261 | 1.28 | 47.57%
3 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 3 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 3 | 2774 | 1390 | 1384 | 1.39 | 49.89%
4 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 4 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 4 | 2774 | 1390 | 1384 | 1.39 | 49.89%
5 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 5 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 5 | 2774 | 1390 | 1384 | 1.39 | 49.89%
6 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 6 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 6 | 2774 | 1390 | 1384 | 1.39 | 49.89%
7 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 7 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 7 | 2651 | 1390 | 1261 | 1.28 | 47.57%
8 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 8 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 8 | 2651 | 1390 | 1261 | 1.28 | 47.57%
9 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 9 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 9 | 2651 | 1390 | 1261 | 1.28 | 47.57%
10 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 10 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 10 | 2651 | 1390 | 1261 | 1.28 | 47.57%
11 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 11 | 2774 | 1390 | 1384 | 1.39 | 49.89% | 11 | 2381 | 1390 | 991 | 1.04 | 41.62%
12 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 12 | 2774 | 1390 | 1384 | 1.39 | 49.89% | 12 | 2381 | 1390 | 991 | 1.04 | 41.62%
13 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 13 | 2774 | 1390 | 1384 | 1.39 | 49.89% | 13 | 2381 | 1390 | 991 | 1.04 | 41.62%
14 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 14 | 2774 | 1390 | 1384 | 1.39 | 49.89% | 14 | 2381 | 1390 | 991 | 1.04 | 41.62%
15 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 15 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 15 | 2800 | 1390 | 1410 | 1.33 | 50.36%
16 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 16 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 16 | 2800 | 1390 | 1410 | 1.33 | 50.36%
17 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 17 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 17 | 2800 | 1390 | 1410 | 1.33 | 50.36%
18 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 18 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 18 | 2800 | 1390 | 1410 | 1.33 | 50.36%
19 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 19 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 19 | 2800 | 1390 | 1410 | 1.33 | 50.36%
20 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 20 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 20 | 2800 | 1390 | 1410 | 1.33 | 50.36%
21 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 21 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 21 | 2800 | 1390 | 1410 | 1.33 | 50.36%
22 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 22 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 22 | 2800 | 1390 | 1410 | 1.33 | 50.36%
23 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 23 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 23 | 2651 | 1390 | 1261 | 1.28 | 47.57%
24 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 24 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 24 | 2651 | 1390 | 1261 | 1.28 | 47.57%
2023-07-01 | [5 empty] | 2023-08-01 | [5 empty] | 2023-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 1 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 1 | 2705 | 1390 | 1315 | 1.33 | 48.61%
2 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 2 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 2 | 2705 | 1390 | 1315 | 1.33 | 48.61%
3 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 3 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 3 | 2774 | 1390 | 1384 | 1.39 | 49.89%
4 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 4 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 4 | 2774 | 1390 | 1384 | 1.39 | 49.89%
5 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 5 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 5 | 2774 | 1390 | 1384 | 1.39 | 49.89%
6 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 6 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 6 | 2774 | 1390 | 1384 | 1.39 | 49.89%
7 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 7 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 7 | 2651 | 1390 | 1261 | 1.28 | 47.57%
8 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 8 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 8 | 2651 | 1390 | 1261 | 1.28 | 47.57%
9 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 9 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 9 | 2651 | 1390 | 1261 | 1.28 | 47.57%
10 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 10 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 10 | 2651 | 1390 | 1261 | 1.28 | 47.57%
11 | 2300 | 1390 | 910 | 1 | 39.57% | 11 | 2300 | 1390 | 910 | 1 | 39.57% | 11 | 2427 | 1390 | 1037 | 1.08 | 42.73%
12 | 2300 | 1390 | 910 | 1 | 39.57% | 12 | 2300 | 1390 | 910 | 1 | 39.57% | 12 | 2427 | 1390 | 1037 | 1.08 | 42.73%
13 | 2300 | 1390 | 910 | 1 | 39.57% | 13 | 2300 | 1390 | 910 | 1 | 39.57% | 13 | 2427 | 1390 | 1037 | 1.08 | 42.73%
14 | 2300 | 1390 | 910 | 1 | 39.57% | 14 | 2300 | 1390 | 910 | 1 | 39.57% | 14 | 2427 | 1390 | 1037 | 1.08 | 42.73%
15 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 15 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 15 | 2800 | 1390 | 1410 | 1.33 | 50.36%
16 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 16 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 16 | 2800 | 1390 | 1410 | 1.33 | 50.36%
17 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 17 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 17 | 2800 | 1390 | 1410 | 1.33 | 50.36%
18 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 18 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 18 | 2800 | 1390 | 1410 | 1.33 | 50.36%
19 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 19 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 19 | 2800 | 1390 | 1410 | 1.33 | 50.36%
20 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 20 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 20 | 2800 | 1390 | 1410 | 1.33 | 50.36%
21 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 21 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 21 | 2800 | 1390 | 1410 | 1.33 | 50.36%
22 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 22 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 22 | 2800 | 1390 | 1410 | 1.33 | 50.36%
23 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 23 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 23 | 2705 | 1390 | 1315 | 1.33 | 48.61%
24 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 24 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 24 | 2705 | 1390 | 1315 | 1.33 | 48.61%
2023-10-01 | [5 empty] | 2023-11-01 | [5 empty] | 2023-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 1 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 1 | 3156 | 1390 | 1766 | 1.83 | 55.96%
2 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 2 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 2 | 3156 | 1390 | 1766 | 1.83 | 55.96%
3 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 3 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 3 | 3195 | 1390 | 1805 | 1.94 | 56.49%
4 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 4 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 4 | 3195 | 1390 | 1805 | 1.94 | 56.49%
5 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 5 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 5 | 3195 | 1390 | 1805 | 1.94 | 56.49%
6 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 6 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 6 | 3195 | 1390 | 1805 | 1.94 | 56.49%
7 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 7 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 7 | 3079 | 1390 | 1689 | 1.74 | 54.86%
8 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 8 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 8 | 3079 | 1390 | 1689 | 1.74 | 54.86%
9 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 9 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 9 | 3079 | 1390 | 1689 | 1.74 | 54.86%
10 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 10 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 10 | 3079 | 1390 | 1689 | 1.74 | 54.86%
11 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 11 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 11 | 2991 | 1390 | 1601 | 1.58 | 53.53%
12 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 12 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 12 | 2991 | 1390 | 1601 | 1.58 | 53.53%
13 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 13 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 13 | 2991 | 1390 | 1601 | 1.58 | 53.53%
14 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 14 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 14 | 2991 | 1390 | 1601 | 1.58 | 53.53%
15 | 2800 | 1390 | 1410 | 1.39 | 50.36% | 15 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 15 | 2949 | 1390 | 1559 | 1.51 | 52.87%
16 | 2800 | 1390 | 1410 | 1.39 | 50.36% | 16 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 16 | 2949 | 1390 | 1559 | 1.51 | 52.87%
17 | 2800 | 1390 | 1410 | 1.39 | 50.36% | 17 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 17 | 2949 | 1390 | 1559 | 1.51 | 52.87%
18 | 2800 | 1390 | 1410 | 1.39 | 50.36% | 18 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 18 | 2949 | 1390 | 1559 | 1.51 | 52.87%
19 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 19 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 19 | 2949 | 1390 | 1559 | 1.51 | 52.87%
20 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 20 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 20 | 2949 | 1390 | 1559 | 1.51 | 52.87%
21 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 21 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 21 | 2949 | 1390 | 1559 | 1.51 | 52.87%
22 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 22 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 22 | 2949 | 1390 | 1559 | 1.51 | 52.87%
23 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 23 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 23 | 3156 | 1390 | 1766 | 1.83 | 55.96%
24 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 24 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 24 | 3156 | 1390 | 1766 | 1.83 | 55.96%

## 2024 RRS Table
| Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
(MW)
*RRS Curr IFRO (MW) | 3335 | 3287 | 3239 | 3195 | 3156 | 3079 | 3041 | 2991 | 2949 | 2871 | 2774 | 2705
**RRS Upd IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2960 | 2916 | 2880 | 2808 | 2716 | 2654
| Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:01 | 1:01 | 1:01 | 1:01 | 1:01
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2651 | 2600 | 2562 | 2517 | 2466 | 2427 | 2381 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2606 | 2560 | 2529 | 2491 | 2444 | 2412 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068

## 2024_RRS
2024 RRS (Floor = 2300 MW for all hours, new minimum RRS-PFR limit =1185 MW)
HE | Jan | Feb | Mar | Apr | May | Jun | July | Aug | Sep | Oct | Nov | Dec
1 | 2998 | 2998 | 3178 | 3086 | 2808 | 2491 | 2412 | 2342
2 | 2998 | 2998 | 3178 | 3086 | 2808 | 2491 | 2412 | 2342
3 | 2998 | 2998 | 3178 | 3128 | 2916 | 2560 | 2491 | 2373
4 | 2998 | 2998 | 3178 | 3128 | 2916 | 2560 | 2491 | 2373
5 | 2998 | 2998 | 3178 | 3128 | 2916 | 2560 | 2491 | 2373
6 | 2998 | 2998 | 3178 | 3128 | 2916 | 2560 | 2491 | 2373
7 | 2916 | 2916 | 3128 | 3086 | 2716 | 2529 | 2444 | 2342
8 | 2916 | 2916 | 3128 | 3086 | 2716 | 2529 | 2444 | 2342
9 | 2916 | 2916 | 3128 | 3086 | 2716 | 2529 | 2444 | 2342
10 | 2916 | 2916 | 3128 | 3086 | 2716 | 2529 | 2444 | 2342
11 | 2960 | 2960 | 3086 | 2960 | 2560 | 2342 | 2300 | 2300
12 | 2960 | 2960 | 3086 | 2960 | 2560 | 2342 | 2300 | 2300
13 | 2960 | 2960 | 3086 | 2960 | 2560 | 2342 | 2300 | 2300
14 | 2960 | 2960 | 3086 | 2960 | 2560 | 2342 | 2300 | 2300
15 | 2916 | 2916 | 2998 | 2880 | 2491 | 2300 | 2300 | 2300
16 | 2916 | 2916 | 2998 | 2880 | 2491 | 2300 | 2300 | 2300
17 | 2916 | 2916 | 2998 | 2880 | 2491 | 2300 | 2300 | 2300
18 | 2916 | 2916 | 2998 | 2880 | 2491 | 2300 | 2300 | 2300
19 | 2916 | 2916 | 2960 | 2880 | 2491 | 2300 | 2300 | 2300
20 | 2916 | 2916 | 2960 | 2880 | 2491 | 2300 | 2300 | 2300
21 | 2916 | 2916 | 2960 | 2880 | 2491 | 2300 | 2300 | 2300
22 | 2916 | 2916 | 2960 | 2880 | 2491 | 2300 | 2300 | 2300
23 | 2998 | 2998 | 3178 | 3086 | 2808 | 2491 | 2412 | 2342
24 | 2998 | 2998 | 3178 | 3086 | 2808 | 2491 | 2412 | 2342
Total | 70816 | 70816 | 74112 | 72080 | 63928 | 58088 | 56988 | 55828 | 0 | 0 | 0 | 0
These preliminary 2024 quantities above are based on the 2024 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1185 MW and a floor of 2300 MW across all hours. Note that, NERC’s preliminary 2024 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows an increase in ERCOT’s IFRO. As a result of this ERCOT expects that the minimum RRS-PFR limit for 2023 will change to align with ERCOT's new IFRO.

## 2024_RRS_Details
2024-01-01 | [5 empty] | 2024-02-01 | [5 empty] | 2024-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 1 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 1 | 3178 | 1271 | 1907 | 2.06 | 60.01%
2 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 2 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 2 | 3178 | 1271 | 1907 | 2.06 | 60.01%
3 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 3 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 3 | 3178 | 1271 | 1907 | 2.06 | 60.01%
4 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4 | 3178 | 1271 | 1907 | 2.06 | 60.01%
5 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 5 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 5 | 3178 | 1271 | 1907 | 2.06 | 60.01%
6 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 6 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 6 | 3178 | 1271 | 1907 | 2.06 | 60.01%
7 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 7 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 7 | 3128 | 1251 | 1877 | 1.94 | 60.01%
8 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 8 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 8 | 3128 | 1251 | 1877 | 1.94 | 60.01%
9 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 9 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 9 | 3128 | 1251 | 1877 | 1.94 | 60.01%
10 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 10 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 10 | 3128 | 1251 | 1877 | 1.94 | 60.01%
11 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 11 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 11 | 3086 | 1234 | 1852 | 1.83 | 60.01%
12 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 12 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 12 | 3086 | 1234 | 1852 | 1.83 | 60.01%
13 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 13 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 13 | 3086 | 1234 | 1852 | 1.83 | 60.01%
14 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 14 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 14 | 3086 | 1234 | 1852 | 1.83 | 60.01%
15 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 15 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 15 | 2998 | 1199 | 1799 | 1.74 | 60.01%
16 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 16 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 16 | 2998 | 1199 | 1799 | 1.74 | 60.01%
17 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 17 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 17 | 2998 | 1199 | 1799 | 1.74 | 60.01%
18 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 18 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 18 | 2998 | 1199 | 1799 | 1.74 | 60.01%
19 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 19 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 19 | 2960 | 1185 | 1775 | 1.65 | 59.97%
20 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 20 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 20 | 2960 | 1185 | 1775 | 1.65 | 59.97%
21 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 21 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 21 | 2960 | 1185 | 1775 | 1.65 | 59.97%
22 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 22 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 22 | 2960 | 1185 | 1775 | 1.65 | 59.97%
23 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 23 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 23 | 3178 | 1271 | 1907 | 2.06 | 60.01%
24 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 24 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 24 | 3178 | 1271 | 1907 | 2.06 | 60.01%
2024-04-01 | [5 empty] | 2024-05-01 | [5 empty] | 2024-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 1 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 1 | 2491 | 1185 | 1306 | 1.15 | 52.43%
2 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 2 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 2 | 2491 | 1185 | 1306 | 1.15 | 52.43%
3 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 3 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 3 | 2560 | 1185 | 1375 | 1.24 | 53.71%
4 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 4 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 4 | 2560 | 1185 | 1375 | 1.24 | 53.71%
5 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 5 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 5 | 2560 | 1185 | 1375 | 1.24 | 53.71%
6 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 6 | 2916 | 1185 | 1731 | 1.58 | 59.36% | 6 | 2560 | 1185 | 1375 | 1.24 | 53.71%
7 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 7 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 7 | 2529 | 1185 | 1344 | 1.19 | 53.14%
8 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 8 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 8 | 2529 | 1185 | 1344 | 1.19 | 53.14%
9 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 9 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 9 | 2529 | 1185 | 1344 | 1.19 | 53.14%
10 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 10 | 2716 | 1185 | 1531 | 1.39 | 56.37% | 10 | 2529 | 1185 | 1344 | 1.19 | 53.14%
11 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 11 | 2560 | 1185 | 1375 | 1.24 | 53.71% | 11 | 2342 | 1185 | 1157 | 1.01 | 49.4%
12 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 12 | 2560 | 1185 | 1375 | 1.24 | 53.71% | 12 | 2342 | 1185 | 1157 | 1.01 | 49.4%
13 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 13 | 2560 | 1185 | 1375 | 1.24 | 53.71% | 13 | 2342 | 1185 | 1157 | 1.01 | 49.4%
14 | 2960 | 1185 | 1775 | 1.65 | 59.97% | 14 | 2560 | 1185 | 1375 | 1.24 | 53.71% | 14 | 2342 | 1185 | 1157 | 1.01 | 49.4%
15 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 15 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 15 | 2300 | 1185 | 1115 | 1 | 48.48%
16 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 16 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 16 | 2300 | 1185 | 1115 | 1 | 48.48%
17 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 17 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 17 | 2300 | 1185 | 1115 | 1 | 48.48%
18 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 18 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 18 | 2300 | 1185 | 1115 | 1 | 48.48%
19 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 19 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 19 | 2300 | 1185 | 1115 | 1 | 48.48%
20 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 20 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 20 | 2300 | 1185 | 1115 | 1 | 48.48%
21 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 21 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 21 | 2300 | 1185 | 1115 | 1 | 48.48%
22 | 2880 | 1185 | 1695 | 1.51 | 58.85% | 22 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 22 | 2300 | 1185 | 1115 | 1 | 48.48%
23 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 23 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 23 | 2491 | 1185 | 1306 | 1.15 | 52.43%
24 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 24 | 2808 | 1185 | 1623 | 1.44 | 57.8% | 24 | 2491 | 1185 | 1306 | 1.15 | 52.43%
2024-07-01 | [5 empty] | 2024-08-01 | [5 empty] | 2024-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2412 | 1185 | 1227 | 1.08 | 50.87% | 1 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 1
2 | 2412 | 1185 | 1227 | 1.08 | 50.87% | 2 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 2
3 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 3 | 2373 | 1185 | 1188 | 1.04 | 50.06% | 3
4 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 4 | 2373 | 1185 | 1188 | 1.04 | 50.06% | 4
5 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 5 | 2373 | 1185 | 1188 | 1.04 | 50.06% | 5
6 | 2491 | 1185 | 1306 | 1.15 | 52.43% | 6 | 2373 | 1185 | 1188 | 1.04 | 50.06% | 6
7 | 2444 | 1185 | 1259 | 1.12 | 51.51% | 7 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 7
8 | 2444 | 1185 | 1259 | 1.12 | 51.51% | 8 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 8
9 | 2444 | 1185 | 1259 | 1.12 | 51.51% | 9 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 9
10 | 2444 | 1185 | 1259 | 1.12 | 51.51% | 10 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 10
11 | 2300 | 1185 | 1115 | 1 | 48.48% | 11 | 2300 | 1185 | 1115 | 1 | 48.48% | 11
12 | 2300 | 1185 | 1115 | 1 | 48.48% | 12 | 2300 | 1185 | 1115 | 1 | 48.48% | 12
13 | 2300 | 1185 | 1115 | 1 | 48.48% | 13 | 2300 | 1185 | 1115 | 1 | 48.48% | 13
14 | 2300 | 1185 | 1115 | 1 | 48.48% | 14 | 2300 | 1185 | 1115 | 1 | 48.48% | 14
15 | 2300 | 1185 | 1115 | 1 | 48.48% | 15 | 2300 | 1185 | 1115 | 1 | 48.48% | 15
16 | 2300 | 1185 | 1115 | 1 | 48.48% | 16 | 2300 | 1185 | 1115 | 1 | 48.48% | 16
17 | 2300 | 1185 | 1115 | 1 | 48.48% | 17 | 2300 | 1185 | 1115 | 1 | 48.48% | 17
18 | 2300 | 1185 | 1115 | 1 | 48.48% | 18 | 2300 | 1185 | 1115 | 1 | 48.48% | 18
19 | 2300 | 1185 | 1115 | 1 | 48.48% | 19 | 2300 | 1185 | 1115 | 1 | 48.48% | 19
20 | 2300 | 1185 | 1115 | 1 | 48.48% | 20 | 2300 | 1185 | 1115 | 1 | 48.48% | 20
21 | 2300 | 1185 | 1115 | 1 | 48.48% | 21 | 2300 | 1185 | 1115 | 1 | 48.48% | 21
22 | 2300 | 1185 | 1115 | 1 | 48.48% | 22 | 2300 | 1185 | 1115 | 1 | 48.48% | 22
23 | 2412 | 1185 | 1227 | 1.08 | 50.87% | 23 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 23
24 | 2412 | 1185 | 1227 | 1.08 | 50.87% | 24 | 2342 | 1185 | 1157 | 1.01 | 49.4% | 24
2024-10-01 | [5 empty] | 2024-11-01 | [5 empty] | 2024-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | [5 empty] | 1 | [5 empty] | 1
2 | [5 empty] | 2 | [5 empty] | 2
3 | [5 empty] | 3 | [5 empty] | 3
4 | [5 empty] | 4 | [5 empty] | 4
5 | [5 empty] | 5 | [5 empty] | 5
6 | [5 empty] | 6 | [5 empty] | 6
7 | [5 empty] | 7 | [5 empty] | 7
8 | [5 empty] | 8 | [5 empty] | 8
9 | [5 empty] | 9 | [5 empty] | 9
10 | [5 empty] | 10 | [5 empty] | 10
11 | [5 empty] | 11 | [5 empty] | 11
12 | [5 empty] | 12 | [5 empty] | 12
13 | [5 empty] | 13 | [5 empty] | 13
14 | [5 empty] | 14 | [5 empty] | 14
15 | [5 empty] | 15 | [5 empty] | 15
16 | [5 empty] | 16 | [5 empty] | 16
17 | [5 empty] | 17 | [5 empty] | 17
18 | [5 empty] | 18 | [5 empty] | 18
19 | [5 empty] | 19 | [5 empty] | 19
20 | [5 empty] | 20 | [5 empty] | 20
21 | [5 empty] | 21 | [5 empty] | 21
22 | [5 empty] | 22 | [5 empty] | 22
23 | [5 empty] | 23 | [5 empty] | 23
24 | [5 empty] | 24 | [5 empty] | 24

## Charts
Month | Date | Group | HE | Type | 2023 RRS | 2024 RRS | Month | Jul |  | Responsive Reserve Requirement Comparison for July
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3041 | 2998 | Type | RRS |  | Range: 2300 MW - 2491 MW; Avg: 2375 MW (208 MW decrease from prev year)
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3041 | 2998
Jan | 2018-01-01 | b. HE3-6 | 3 | RRS | 2991 | 2998 | Row Labels | 2023 RRS | 2024 RRS |  | min | 2300
Jan | 2018-01-01 | b. HE3-6 | 4 | RRS | 2991 | 2998 | a. HE1-2 & HE23-24 | 2517 | 2412 |  | max | 2491
Jan | 2018-01-01 | b. HE3-6 | 5 | RRS | 2991 | 2998 | b. HE3-6 | 2562 | 2491 |  | avg | 2375
Jan | 2018-01-01 | b. HE3-6 | 6 | RRS | 2991 | 2998 | c. HE7-10 | 2517 | 2444 |  | Change | -208
Jan | 2018-01-01 | c. HE7-10 | 7 | RRS | 2871 | 2916 | d. HE11-14 | 2300 | 2300
Jan | 2018-01-01 | c. HE7-10 | 8 | RRS | 2871 | 2916 | e. HE15-18 | 2800 | 2300
Jan | 2018-01-01 | c. HE7-10 | 9 | RRS | 2871 | 2916 | f. HE19-22 | 2800 | 2300
Jan | 2018-01-01 | c. HE7-10 | 10 | RRS | 2871 | 2916
Jan | 2018-01-01 | d. HE11-14 | 11 | RRS | 2949 | 2960
Jan | 2018-01-01 | d. HE11-14 | 12 | RRS | 2949 | 2960
Jan | 2018-01-01 | d. HE11-14 | 13 | RRS | 2949 | 2960
Jan | 2018-01-01 | d. HE11-14 | 14 | RRS | 2949 | 2960
Jan | 2018-01-01 | e. HE15-18 | 15 | RRS | 2991 | 2916
Jan | 2018-01-01 | e. HE15-18 | 16 | RRS | 2991 | 2916
Jan | 2018-01-01 | e. HE15-18 | 17 | RRS | 2991 | 2916
Jan | 2018-01-01 | e. HE15-18 | 18 | RRS | 2991 | 2916
Jan | 2018-01-01 | f. HE19-22 | 19 | RRS | 2949 | 2916
Jan | 2018-01-01 | f. HE19-22 | 20 | RRS | 2949 | 2916
Jan | 2018-01-01 | f. HE19-22 | 21 | RRS | 2949 | 2916
Jan | 2018-01-01 | f. HE19-22 | 22 | RRS | 2949 | 2916
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3041 | 2998
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3041 | 2998
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3079 | 2998
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3079 | 2998
Feb | 2018-02-01 | b. HE3-6 | 3 | RRS | 3041 | 2998
Feb | 2018-02-01 | b. HE3-6 | 4 | RRS | 3041 | 2998
Feb | 2018-02-01 | b. HE3-6 | 5 | RRS | 3041 | 2998 | Type | RRS |  |  |  | Hourly Average Responsive Reserve Requirement Comparison
Feb | 2018-02-01 | b. HE3-6 | 6 | RRS | 3041 | 2998 | [5 empty] | 2024 RRS: On avg. 162 MW decrease from prev year. Largest decrease is in Jul by 256 MW.
Feb | 2018-02-01 | c. HE7-10 | 7 | RRS | 2991 | 2916 | Row Labels | 2023 RRS | 2024 RRS
Feb | 2018-02-01 | c. HE7-10 | 8 | RRS | 2991 | 2916 | Jan | 2965.3333 | 2950.6667 | -14.6667 |  |  | min-change | -255.8333 | Jul
Feb | 2018-02-01 | c. HE7-10 | 9 | RRS | 2991 | 2916 | Feb | 3022.3333 | 2950.6667 | -71.6667 |  |  | max-change | 0 | #N/A
Feb | 2018-02-01 | c. HE7-10 | 10 | RRS | 2991 | 2916 | Mar | 3256.3333 | 3088 | -168.3333 |  |  | AVG-CHANGE | -161.7708
Feb | 2018-02-01 | d. HE11-14 | 11 | RRS | 3041 | 2960 | Apr | 3102.1667 | 3003.3333 | -98.8333
Feb | 2018-02-01 | d. HE11-14 | 12 | RRS | 3041 | 2960 | May | 2900.8333 | 2663.6667 | -237.1667
Feb | 2018-02-01 | d. HE11-14 | 13 | RRS | 3041 | 2960 | Jun | 2676.1667 | 2420.3333 | -255.8333
Feb | 2018-02-01 | d. HE11-14 | 14 | RRS | 3041 | 2960 | Jul | 2582.6667 | 2374.5 | -208.1667
Feb | 2018-02-01 | e. HE15-18 | 15 | RRS | 2991 | 2916 | Aug | 2565.6667 | 2326.1667 | -239.5
Feb | 2018-02-01 | e. HE15-18 | 16 | RRS | 2991 | 2916 | Sep | 2692.8333 | 0 | #N/A
Feb | 2018-02-01 | e. HE15-18 | 17 | RRS | 2991 | 2916 | Oct | 2949.5 | 0 | #N/A
Feb | 2018-02-01 | e. HE15-18 | 18 | RRS | 2991 | 2916 | Nov | 3075.6667 | 0 | #N/A
Feb | 2018-02-01 | f. HE19-22 | 19 | RRS | 2991 | 2916 | Dec | 3053.1667 | 0 | #N/A
Feb | 2018-02-01 | f. HE19-22 | 20 | RRS | 2991 | 2916
Feb | 2018-02-01 | f. HE19-22 | 21 | RRS | 2991 | 2916
Feb | 2018-02-01 | f. HE19-22 | 22 | RRS | 2991 | 2916
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3079 | 2998
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3079 | 2998
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3335 | 3178
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3335 | 3178
Mar | 2018-03-01 | b. HE3-6 | 3 | RRS | 3335 | 3178
Mar | 2018-03-01 | b. HE3-6 | 4 | RRS | 3335 | 3178
Mar | 2018-03-01 | b. HE3-6 | 5 | RRS | 3335 | 3178
Mar | 2018-03-01 | b. HE3-6 | 6 | RRS | 3335 | 3178
Mar | 2018-03-01 | c. HE7-10 | 7 | RRS | 3239 | 3128
Mar | 2018-03-01 | c. HE7-10 | 8 | RRS | 3239 | 3128
Mar | 2018-03-01 | c. HE7-10 | 9 | RRS | 3239 | 3128
Mar | 2018-03-01 | c. HE7-10 | 10 | RRS | 3239 | 3128
Mar | 2018-03-01 | d. HE11-14 | 11 | RRS | 3239 | 3086
Mar | 2018-03-01 | d. HE11-14 | 12 | RRS | 3239 | 3086
Mar | 2018-03-01 | d. HE11-14 | 13 | RRS | 3239 | 3086
Mar | 2018-03-01 | d. HE11-14 | 14 | RRS | 3239 | 3086
Mar | 2018-03-01 | e. HE15-18 | 15 | RRS | 3195 | 2998
Mar | 2018-03-01 | e. HE15-18 | 16 | RRS | 3195 | 2998
Mar | 2018-03-01 | e. HE15-18 | 17 | RRS | 3195 | 2998
Mar | 2018-03-01 | e. HE15-18 | 18 | RRS | 3195 | 2998
Mar | 2018-03-01 | f. HE19-22 | 19 | RRS | 3195 | 2960
Mar | 2018-03-01 | f. HE19-22 | 20 | RRS | 3195 | 2960
Mar | 2018-03-01 | f. HE19-22 | 21 | RRS | 3195 | 2960
Mar | 2018-03-01 | f. HE19-22 | 22 | RRS | 3195 | 2960
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3335 | 3178
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3335 | 3178
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3195 | 3086
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3195 | 3086
Apr | 2018-04-01 | b. HE3-6 | 3 | RRS | 3239 | 3128
Apr | 2018-04-01 | b. HE3-6 | 4 | RRS | 3239 | 3128
Apr | 2018-04-01 | b. HE3-6 | 5 | RRS | 3239 | 3128
Apr | 2018-04-01 | b. HE3-6 | 6 | RRS | 3239 | 3128
Apr | 2018-04-01 | c. HE7-10 | 7 | RRS | 3156 | 3086
Apr | 2018-04-01 | c. HE7-10 | 8 | RRS | 3156 | 3086
Apr | 2018-04-01 | c. HE7-10 | 9 | RRS | 3156 | 3086
Apr | 2018-04-01 | c. HE7-10 | 10 | RRS | 3156 | 3086
Apr | 2018-04-01 | d. HE11-14 | 11 | RRS | 3041 | 2960
Apr | 2018-04-01 | d. HE11-14 | 12 | RRS | 3041 | 2960
Apr | 2018-04-01 | d. HE11-14 | 13 | RRS | 3041 | 2960
Apr | 2018-04-01 | d. HE11-14 | 14 | RRS | 3041 | 2960
Apr | 2018-04-01 | e. HE15-18 | 15 | RRS | 2991 | 2880
Apr | 2018-04-01 | e. HE15-18 | 16 | RRS | 2991 | 2880
Apr | 2018-04-01 | e. HE15-18 | 17 | RRS | 2991 | 2880
Apr | 2018-04-01 | e. HE15-18 | 18 | RRS | 2991 | 2880
Apr | 2018-04-01 | f. HE19-22 | 19 | RRS | 2991 | 2880
Apr | 2018-04-01 | f. HE19-22 | 20 | RRS | 2991 | 2880
Apr | 2018-04-01 | f. HE19-22 | 21 | RRS | 2991 | 2880
Apr | 2018-04-01 | f. HE19-22 | 22 | RRS | 2991 | 2880
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3195 | 3086
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3195 | 3086
May | 2018-05-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3041 | 2808
May | 2018-05-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3041 | 2808
May | 2018-05-01 | b. HE3-6 | 3 | RRS | 3041 | 2916
May | 2018-05-01 | b. HE3-6 | 4 | RRS | 3041 | 2916
May | 2018-05-01 | b. HE3-6 | 5 | RRS | 3041 | 2916
May | 2018-05-01 | b. HE3-6 | 6 | RRS | 3041 | 2916
May | 2018-05-01 | c. HE7-10 | 7 | RRS | 2949 | 2716
May | 2018-05-01 | c. HE7-10 | 8 | RRS | 2949 | 2716
May | 2018-05-01 | c. HE7-10 | 9 | RRS | 2949 | 2716
May | 2018-05-01 | c. HE7-10 | 10 | RRS | 2949 | 2716
May | 2018-05-01 | d. HE11-14 | 11 | RRS | 2774 | 2560
May | 2018-05-01 | d. HE11-14 | 12 | RRS | 2774 | 2560
May | 2018-05-01 | d. HE11-14 | 13 | RRS | 2774 | 2560
May | 2018-05-01 | d. HE11-14 | 14 | RRS | 2774 | 2560
May | 2018-05-01 | e. HE15-18 | 15 | RRS | 2800 | 2491
May | 2018-05-01 | e. HE15-18 | 16 | RRS | 2800 | 2491
May | 2018-05-01 | e. HE15-18 | 17 | RRS | 2800 | 2491
May | 2018-05-01 | e. HE15-18 | 18 | RRS | 2800 | 2491
May | 2018-05-01 | f. HE19-22 | 19 | RRS | 2800 | 2491
May | 2018-05-01 | f. HE19-22 | 20 | RRS | 2800 | 2491
May | 2018-05-01 | f. HE19-22 | 21 | RRS | 2800 | 2491
May | 2018-05-01 | f. HE19-22 | 22 | RRS | 2800 | 2491
May | 2018-05-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3041 | 2808
May | 2018-05-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3041 | 2808
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2651 | 2491
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2651 | 2491
Jun | 2018-06-01 | b. HE3-6 | 3 | RRS | 2774 | 2560
Jun | 2018-06-01 | b. HE3-6 | 4 | RRS | 2774 | 2560
Jun | 2018-06-01 | b. HE3-6 | 5 | RRS | 2774 | 2560
Jun | 2018-06-01 | b. HE3-6 | 6 | RRS | 2774 | 2560
Jun | 2018-06-01 | c. HE7-10 | 7 | RRS | 2651 | 2529
Jun | 2018-06-01 | c. HE7-10 | 8 | RRS | 2651 | 2529
Jun | 2018-06-01 | c. HE7-10 | 9 | RRS | 2651 | 2529
Jun | 2018-06-01 | c. HE7-10 | 10 | RRS | 2651 | 2529
Jun | 2018-06-01 | d. HE11-14 | 11 | RRS | 2381 | 2342
Jun | 2018-06-01 | d. HE11-14 | 12 | RRS | 2381 | 2342
Jun | 2018-06-01 | d. HE11-14 | 13 | RRS | 2381 | 2342
Jun | 2018-06-01 | d. HE11-14 | 14 | RRS | 2381 | 2342
Jun | 2018-06-01 | e. HE15-18 | 15 | RRS | 2800 | 2300
Jun | 2018-06-01 | e. HE15-18 | 16 | RRS | 2800 | 2300
Jun | 2018-06-01 | e. HE15-18 | 17 | RRS | 2800 | 2300
Jun | 2018-06-01 | e. HE15-18 | 18 | RRS | 2800 | 2300
Jun | 2018-06-01 | f. HE19-22 | 19 | RRS | 2800 | 2300
Jun | 2018-06-01 | f. HE19-22 | 20 | RRS | 2800 | 2300
Jun | 2018-06-01 | f. HE19-22 | 21 | RRS | 2800 | 2300
Jun | 2018-06-01 | f. HE19-22 | 22 | RRS | 2800 | 2300
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2651 | 2491
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2651 | 2491
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2517 | 2412
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2517 | 2412
Jul | 2018-07-01 | b. HE3-6 | 3 | RRS | 2562 | 2491
Jul | 2018-07-01 | b. HE3-6 | 4 | RRS | 2562 | 2491
Jul | 2018-07-01 | b. HE3-6 | 5 | RRS | 2562 | 2491
Jul | 2018-07-01 | b. HE3-6 | 6 | RRS | 2562 | 2491
Jul | 2018-07-01 | c. HE7-10 | 7 | RRS | 2517 | 2444
Jul | 2018-07-01 | c. HE7-10 | 8 | RRS | 2517 | 2444
Jul | 2018-07-01 | c. HE7-10 | 9 | RRS | 2517 | 2444
Jul | 2018-07-01 | c. HE7-10 | 10 | RRS | 2517 | 2444
Jul | 2018-07-01 | d. HE11-14 | 11 | RRS | 2300 | 2300
Jul | 2018-07-01 | d. HE11-14 | 12 | RRS | 2300 | 2300
Jul | 2018-07-01 | d. HE11-14 | 13 | RRS | 2300 | 2300
Jul | 2018-07-01 | d. HE11-14 | 14 | RRS | 2300 | 2300
Jul | 2018-07-01 | e. HE15-18 | 15 | RRS | 2800 | 2300
Jul | 2018-07-01 | e. HE15-18 | 16 | RRS | 2800 | 2300
Jul | 2018-07-01 | e. HE15-18 | 17 | RRS | 2800 | 2300
Jul | 2018-07-01 | e. HE15-18 | 18 | RRS | 2800 | 2300
Jul | 2018-07-01 | f. HE19-22 | 19 | RRS | 2800 | 2300
Jul | 2018-07-01 | f. HE19-22 | 20 | RRS | 2800 | 2300
Jul | 2018-07-01 | f. HE19-22 | 21 | RRS | 2800 | 2300
Jul | 2018-07-01 | f. HE19-22 | 22 | RRS | 2800 | 2300
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2517 | 2412
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2517 | 2412
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2466 | 2342
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2466 | 2342
Aug | 2018-08-01 | b. HE3-6 | 3 | RRS | 2562 | 2373
Aug | 2018-08-01 | b. HE3-6 | 4 | RRS | 2562 | 2373
Aug | 2018-08-01 | b. HE3-6 | 5 | RRS | 2562 | 2373
Aug | 2018-08-01 | b. HE3-6 | 6 | RRS | 2562 | 2373
Aug | 2018-08-01 | c. HE7-10 | 7 | RRS | 2466 | 2342
Aug | 2018-08-01 | c. HE7-10 | 8 | RRS | 2466 | 2342
Aug | 2018-08-01 | c. HE7-10 | 9 | RRS | 2466 | 2342
Aug | 2018-08-01 | c. HE7-10 | 10 | RRS | 2466 | 2342
Aug | 2018-08-01 | d. HE11-14 | 11 | RRS | 2300 | 2300
Aug | 2018-08-01 | d. HE11-14 | 12 | RRS | 2300 | 2300
Aug | 2018-08-01 | d. HE11-14 | 13 | RRS | 2300 | 2300
Aug | 2018-08-01 | d. HE11-14 | 14 | RRS | 2300 | 2300
Aug | 2018-08-01 | e. HE15-18 | 15 | RRS | 2800 | 2300
Aug | 2018-08-01 | e. HE15-18 | 16 | RRS | 2800 | 2300
Aug | 2018-08-01 | e. HE15-18 | 17 | RRS | 2800 | 2300
Aug | 2018-08-01 | e. HE15-18 | 18 | RRS | 2800 | 2300
Aug | 2018-08-01 | f. HE19-22 | 19 | RRS | 2800 | 2300
Aug | 2018-08-01 | f. HE19-22 | 20 | RRS | 2800 | 2300
Aug | 2018-08-01 | f. HE19-22 | 21 | RRS | 2800 | 2300
Aug | 2018-08-01 | f. HE19-22 | 22 | RRS | 2800 | 2300
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2466 | 2342
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2466 | 2342
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2705 | 0
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2705 | 0
Sep | 2018-09-01 | b. HE3-6 | 3 | RRS | 2774 | 0
Sep | 2018-09-01 | b. HE3-6 | 4 | RRS | 2774 | 0
Sep | 2018-09-01 | b. HE3-6 | 5 | RRS | 2774 | 0
Sep | 2018-09-01 | b. HE3-6 | 6 | RRS | 2774 | 0
Sep | 2018-09-01 | c. HE7-10 | 7 | RRS | 2651 | 0
Sep | 2018-09-01 | c. HE7-10 | 8 | RRS | 2651 | 0
Sep | 2018-09-01 | c. HE7-10 | 9 | RRS | 2651 | 0
Sep | 2018-09-01 | c. HE7-10 | 10 | RRS | 2651 | 0
Sep | 2018-09-01 | d. HE11-14 | 11 | RRS | 2427 | 0
Sep | 2018-09-01 | d. HE11-14 | 12 | RRS | 2427 | 0
Sep | 2018-09-01 | d. HE11-14 | 13 | RRS | 2427 | 0
Sep | 2018-09-01 | d. HE11-14 | 14 | RRS | 2427 | 0
Sep | 2018-09-01 | e. HE15-18 | 15 | RRS | 2800 | 0
Sep | 2018-09-01 | e. HE15-18 | 16 | RRS | 2800 | 0
Sep | 2018-09-01 | e. HE15-18 | 17 | RRS | 2800 | 0
Sep | 2018-09-01 | e. HE15-18 | 18 | RRS | 2800 | 0
Sep | 2018-09-01 | f. HE19-22 | 19 | RRS | 2800 | 0
Sep | 2018-09-01 | f. HE19-22 | 20 | RRS | 2800 | 0
Sep | 2018-09-01 | f. HE19-22 | 21 | RRS | 2800 | 0
Sep | 2018-09-01 | f. HE19-22 | 22 | RRS | 2800 | 0
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2705 | 0
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2705 | 0
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3079 | 0
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3079 | 0
Oct | 2018-10-01 | b. HE3-6 | 3 | RRS | 3156 | 0
Oct | 2018-10-01 | b. HE3-6 | 4 | RRS | 3156 | 0
Oct | 2018-10-01 | b. HE3-6 | 5 | RRS | 3156 | 0
Oct | 2018-10-01 | b. HE3-6 | 6 | RRS | 3156 | 0
Oct | 2018-10-01 | c. HE7-10 | 7 | RRS | 2991 | 0
Oct | 2018-10-01 | c. HE7-10 | 8 | RRS | 2991 | 0
Oct | 2018-10-01 | c. HE7-10 | 9 | RRS | 2991 | 0
Oct | 2018-10-01 | c. HE7-10 | 10 | RRS | 2991 | 0
Oct | 2018-10-01 | d. HE11-14 | 11 | RRS | 2871 | 0
Oct | 2018-10-01 | d. HE11-14 | 12 | RRS | 2871 | 0
Oct | 2018-10-01 | d. HE11-14 | 13 | RRS | 2871 | 0
Oct | 2018-10-01 | d. HE11-14 | 14 | RRS | 2871 | 0
Oct | 2018-10-01 | e. HE15-18 | 15 | RRS | 2800 | 0
Oct | 2018-10-01 | e. HE15-18 | 16 | RRS | 2800 | 0
Oct | 2018-10-01 | e. HE15-18 | 17 | RRS | 2800 | 0
Oct | 2018-10-01 | e. HE15-18 | 18 | RRS | 2800 | 0
Oct | 2018-10-01 | f. HE19-22 | 19 | RRS | 2800 | 0
Oct | 2018-10-01 | f. HE19-22 | 20 | RRS | 2800 | 0
Oct | 2018-10-01 | f. HE19-22 | 21 | RRS | 2800 | 0
Oct | 2018-10-01 | f. HE19-22 | 22 | RRS | 2800 | 0
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3079 | 0
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3079 | 0
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3195 | 0
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3195 | 0
Nov | 2018-11-01 | b. HE3-6 | 3 | RRS | 3195 | 0
Nov | 2018-11-01 | b. HE3-6 | 4 | RRS | 3195 | 0
Nov | 2018-11-01 | b. HE3-6 | 5 | RRS | 3195 | 0
Nov | 2018-11-01 | b. HE3-6 | 6 | RRS | 3195 | 0
Nov | 2018-11-01 | c. HE7-10 | 7 | RRS | 3041 | 0
Nov | 2018-11-01 | c. HE7-10 | 8 | RRS | 3041 | 0
Nov | 2018-11-01 | c. HE7-10 | 9 | RRS | 3041 | 0
Nov | 2018-11-01 | c. HE7-10 | 10 | RRS | 3041 | 0
Nov | 2018-11-01 | d. HE11-14 | 11 | RRS | 3041 | 0
Nov | 2018-11-01 | d. HE11-14 | 12 | RRS | 3041 | 0
Nov | 2018-11-01 | d. HE11-14 | 13 | RRS | 3041 | 0
Nov | 2018-11-01 | d. HE11-14 | 14 | RRS | 3041 | 0
Nov | 2018-11-01 | e. HE15-18 | 15 | RRS | 2991 | 0
Nov | 2018-11-01 | e. HE15-18 | 16 | RRS | 2991 | 0
Nov | 2018-11-01 | e. HE15-18 | 17 | RRS | 2991 | 0
Nov | 2018-11-01 | e. HE15-18 | 18 | RRS | 2991 | 0
Nov | 2018-11-01 | f. HE19-22 | 19 | RRS | 2991 | 0
Nov | 2018-11-01 | f. HE19-22 | 20 | RRS | 2991 | 0
Nov | 2018-11-01 | f. HE19-22 | 21 | RRS | 2991 | 0
Nov | 2018-11-01 | f. HE19-22 | 22 | RRS | 2991 | 0
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3195 | 0
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3195 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3156 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3156 | 0
Dec | 2018-12-01 | b. HE3-6 | 3 | RRS | 3195 | 0
Dec | 2018-12-01 | b. HE3-6 | 4 | RRS | 3195 | 0
Dec | 2018-12-01 | b. HE3-6 | 5 | RRS | 3195 | 0
Dec | 2018-12-01 | b. HE3-6 | 6 | RRS | 3195 | 0
Dec | 2018-12-01 | c. HE7-10 | 7 | RRS | 3079 | 0
Dec | 2018-12-01 | c. HE7-10 | 8 | RRS | 3079 | 0
Dec | 2018-12-01 | c. HE7-10 | 9 | RRS | 3079 | 0
Dec | 2018-12-01 | c. HE7-10 | 10 | RRS | 3079 | 0
Dec | 2018-12-01 | d. HE11-14 | 11 | RRS | 2991 | 0
Dec | 2018-12-01 | d. HE11-14 | 12 | RRS | 2991 | 0
Dec | 2018-12-01 | d. HE11-14 | 13 | RRS | 2991 | 0
Dec | 2018-12-01 | d. HE11-14 | 14 | RRS | 2991 | 0
Dec | 2018-12-01 | e. HE15-18 | 15 | RRS | 2949 | 0
Dec | 2018-12-01 | e. HE15-18 | 16 | RRS | 2949 | 0
Dec | 2018-12-01 | e. HE15-18 | 17 | RRS | 2949 | 0
Dec | 2018-12-01 | e. HE15-18 | 18 | RRS | 2949 | 0
Dec | 2018-12-01 | f. HE19-22 | 19 | RRS | 2949 | 0
Dec | 2018-12-01 | f. HE19-22 | 20 | RRS | 2949 | 0
Dec | 2018-12-01 | f. HE19-22 | 21 | RRS | 2949 | 0
Dec | 2018-12-01 | f. HE19-22 | 22 | RRS | 2949 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3156 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3156 | 0