## Slide 1
October 6, 2023 WMWG
October 10, 2023 PDCWG
Balancing Operations Planning Staff
2024 Ancillary Service Methodology Discussion

## Slide 2: Discussion Scope for Today
This presentation will discuss the proposed methodology to determine Ancillary Service (A/S) quantities for 2024.
  ERCOT is not proposing any changes in the methodology used for computing Regulation Service. To better reflect the balancing needs from the hour, ERCOT has updated the Net Load variability calculation to include additional accounting based on accumulated Area Control Error (ACE).
  ERCOT is proposing one change in the methodology for computing Responsive Reserve Service (RRS). ERCOT is proposing to remove the 2,800 MW RRS floor that is applied to summer peak hours for 2024. A Minimum 2,300 MW of RRS will apply to all hours.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2024 assessment for ERCOT shows a decrease in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2024 will change to 1,185 MW.
  ERCOT is proposing three changes in the methodology used to compute ERCOT Contingency Reserve Service (ECRS) for 2024.
  ERCOT is proposing one change in the methodology used to compute Non-Spinning Reserve Service (Non-Spin).
  Note that, while the quantities of each AS are set based on an analysis of certain risks, these are not necessarily the only reasons why each AS is needed.
The Ancillary Service (A/S) quantities for 2024 contained in this presentation are based on the methodology that was approved in December 2022. The quantities for 2024 reflect moving forward the historic data on which these are based, unless otherwise noted.
Slides responding to comments from previous stakeholder meetings are included.
ERCOT is seeking stakeholder feedback on these proposes changes for the 2024 A/S Methodology.

## Slide 3: Regulation Service Feedback
Regulation Service
    Growth of solar resources in east regions and their impact on Regulation needs.
Response
  ERCOT understands that that solar variability in the east solar regions is different than west and that growth in solar capacity in the eastern regions may further increase solar variability. ERCOT notes that there is already a substantial growth in solar capacity in the eastern regions.
  An estimation of increased variability brought about by the growth of solar resources is already used in the methodology for computing Regulation requirements. In Real Time, ERCOT receives a 5-min resolution solar forecast every 5-mins. This forecast is used in tools that estimate the 5-min ahead, 10min ahead, 30min ahead net load forecasts and the available capability to meet those ramps. The projected 5-min ahead net load forecast is also used to preposition SCED Dispatchable resources in response to a net load ramp. Lastly, SCED can be executed manually (with or without an offset) if Regulation alone is not able to recover frequency. These tools in conjunction with Regulation are relied upon to respond to solar variability and balance frequency.
  Improved intra-hour forecasting is an essential feature in responding to weather driven solar variability during the day-time. That said, to ensure that the underlying data used in establishing Regulation quantities appropriately accounts for frequency control across an hour, ERCOT has updated the net load variability calculations to include the accumulated Area Control Error (ACE) across the hour in the calculation. Through this adjustment the Net Load variability calculation better reflects the historic balancing needs.

## Slide 4: Installed Solar Capacity by Region
The projected month over month growth in installed solar capacity in 2024 is lower in all months except December.
Most MWs are expected to be added in the East counties.
Installed solar capacity of at least 4 counties will increase by more than 800 MW.
  Wharton +1,295 MW | Swisher +1,125 MW |
  Lamar +972 MW | Webb +819 MW

## Slide 5: Growth of Solar Capacity by Region
Far East installed capacity has increased by ~2,000 MW in 2023 and may further increase by 1,500 MW for a total of 3,500 MW before year ends.
Far East installed capacity is projected to increase by ~6,000 MW in 2024.
Far East installed capacity has increased by ~2,000 MW in 2022.

## Slide 6: Mechanisms to respond to Solar variability
The Solar adjustment tables were developed to project increases in variability expected by growth in the solar fleet. This has been part of the regulation methodology since 2021. This underlying study has been updated for 2024.
Improve GTBD i.e. the target that SCED uses to dispatch SCED Dispatchable Resources.
  In Real Time the parameters in GTBD can be changed to improve the accounting forecasted solar ramp as the solar fleet grows.
  The solar ramp that is currently used in GTBD is estimated using hourly solar forecasts. This gives a conservative estimate of variability within the hour. This can be toggled to use the intra-hour solar forecast. Making this change can which will make GTBD much more reactive in sensing weather variability.
    ERCOT has been actively engaged with its forecast vendors to develop forecasting methodologies that will improve 5-min solar ramp/variability forecasts.
In Real Time SCED can be executed manually (with or without an offset) if Regulation alone is not able to recover frequency.

## Slide 7: New Technique for establishing PSRR Threshold in GTBD
Chart: Dynamic PSRR Threshold
 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 100 | 100 | 100 | 0 | 0 | 0
ERCOT started to apply a dynamic PSRR threshold in GTBD calculation on 6/12/2023
PSRR thresholds change with 4 pre-defined day periods - Night, Sunrise, Sunset and Other
ERCOT started with a threshold of 80MW/min for Sunrise and Sunset periods on 6/12 and subsequently increased it to 100MW/min on 6/15
ERCOT plans to update the thresholds and the definition of day periods seasonally* (4 times a year)
Night
* Seasons will be defined by shift in solar ramping patterns

## Slide 8: SCED Manual Offset and Reg Up Exhaustion

## Slide 9: Regulation Exhaustion
2023 Avg:1.6%
2022 Avg :2.0%
2023 Avg:3.8%
2022 Avg :5.1%

## Slide 10: Regulation Service Methodology
Regulation Service is reserved capacity that is deployed every 4 seconds to balance supply and demand and maintain frequency close to 60Hz between 5-minute SCED runs.
ERCOT is not proposing any changes to the methodology used to compute the minimum Regulation Service requirements in 2024.
  To better reflect the balancing needs from the hour, ERCOT has updated the Net Load variability calculation to include additional accounting based on accumulated Area Control Error (ACE).
The preliminary Regulation quantities for January 2024 through August 2024 in subsequent slides have been computed using current methodology (2022 and 2023 five-minute net load variability), updated Wind Adjustment tables and the updated Solar Adjustment tables.
Regulation

## Slide 11: 2024 Solar Adjustment Tables
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
 | Min (MW) | Max (MW) | Average (MW)
Reg Up | 0 | 18 | 7.8
Reg Down | 0 | 20 | 7.7

## Slide 12: 2024 Wind Adjustment Tables
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Chart: Reg-Up Adjustment per 1000 MW increase in Wind Installed Capacity
| Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec.
2023 Reg-Up Adj. | 1.3798 | 1.5039 | 1.8328 | 1.806 | 1.6997 | 1.3779 | 1.1206 | 1.1201 | 1.303 | 1.2479 | 1.2649 | 1.3286
2024 Reg-Up Adj. | 1.1913 | 1.0376 | 1.6649 | 1.3893 | 1.4639 | 1.2949 | 1.309 | 1.0183 | 0.91327 | 0.88836 | 0.9438 | 0.83143
Chart: Reg-Down Adjustment per 1000 MW increase in Wind Installed Capacity
| Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec.
2023 Reg Down Adj. | 1.1056 | 1.3234 | 1.7668 | 1.679 | 1.3874 | 0.99909 | 0.84149 | 0.92914 | 1.0592 | 1.0554 | 1.0593 | 1.2217
2024 Reg Down Adj. | 1.1913 | 1.0376 | 1.6649 | 1.3893 | 1.4639 | 1.2949 | 1.309 | 1.0183 | 0.91327 | 0.88836 | 0.9438 | 0.83143
Notes: Avg Reg Up adjustment for wind is 1.2MW
Avg Reg Down adjustment for wind is 1.2 MW

## Slide 13: Hourly Average Regulation Comparison

## Slide 14: Regulation Comparison January

## Slide 15: Regulation Comparison April

## Slide 16: Regulation Comparison August

## Slide 17: Responsive Reserve Service Feedback
Responsive Reserve Service
    Is any RRS adjustment needed for telemetry errors that may impact PRC?
Response
  The additional 500MW were included in 2022 AS Methodology RRS during peak hours to maintain sufficient level of PRC. In 2022 Q4 ERCOT implemented NPRR989 to improve accounting of PRC from Energy Storage Resources (ESRs).
    Specifically with this change ESRs can contribute higher capacity as long as it can be sustained for 15min into PRC based on their verified droop. Prior to this change, PRC from ESRs was limited to 20% of their capacity.
  With regards to telemetry errors, ERCOT is still in the process of conducting post event analysis of PRC to determine the primary causes of telemetry errors that impacted PRC during the September 6 EEA event, similar to the one conducted post Winter Storm Uri in 2021.
  The RRS studies use a 100mHz margin to account for differences between study setup and Real Time. Further, the analysis on RRS Limits that was shared by ERCOT and GE at April 6 Workshop is also relevant. Specifically, that analysis provides a methodology to establish limits on RRS provision based on impact of performance failures. ERCOT is reviewing the recommendations from this study and expects to file NPRR(s) to adopt these as appropriate.

## Slide 18: Responsive Reserve Service (RRS) Methodology
Responsive Reserve Service (RRS) is reserved capacity that is procured to respond to low frequency events typically triggered by generating unit trips.
ERCOT is proposing one change in the methodology used to compute RRS requirements in 2024.
  ERCOT is proposing to remove the 2,800 MW floor that is applied during summer peak hours. A minimum of 2,300 MW of RRS will continue to be procured in all hours.
Responsive
  The additional 500 MW RRS during Summer peak helped in maintaining sufficient amount of Physical Responsive Capability (PRC) during these hours. The implementation of NPRR 989 that improved accounting of PRC from Energy Storage Resources (ESRs) and the recent implementation of ERCOT Contingency Reserve Service (ECRS) are helping in maintaining PRC.
NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2024 assessment for ERCOT shows a decrease in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2024 will change to 1,185 MW.
The preliminary RRS quantities for January 2024 through August 2024 in subsequent slides have been computed using 2022 and 2023 system inertia conditions and updated RRS table.
  The RRS table tracks RRS requirements for different inertia conditions. This table was updated in 2024 to use a minimum RRS-PFR limit of 1,185 MW.
No change in slides 20 to 25 since last presentation. August data has been included in Slide 22.
Notes: OY2022 IFRO – 412 MW/0.1 Hz | Limit 1,240 MW
OY2023 IFRO – 463 MW/0.1 Hz | Limit 1,390 MW
OY2024 IFRO – 395 MW/0.1 Hz | Limit 1,185 MW

## Slide 19: 2024 RRS Table
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS Curr IFRO (MW) | 3335 | 3287 | 3239 | 3195 | 3156 | 3079 | 3041 | 2991 | 2949 | 2871 | 2774 | 2705
**RRS Upd IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2960 | 2916 | 2880 | 2808 | 2716 | 2654
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290*** | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2651 | 2600 | 2562 | 2517 | 2466 | 2427 | 2381 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2606 | 2560 | 2529 | 2491 | 2444 | 2412 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,390 MW.
**RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,185 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. RRS requirement during these is based on the applicable floor.
Notes: RRS quantity for 2024 decrease between 2 MW (320 GW.s case) and 61 MW (150 GW.s case)

## Slide 20: Hourly Average RRS Comparison

## Slide 21: RRS Comparison February

## Slide 22: RRS Comparison March

## Slide 23: RRS Comparison July

## Slide 24: ERCOT Contingency Reserve Service (ECRS) Feedback
ERCOT Contingency Reserve Service
    Review impacts of proposed approach during peak net load hours
  Response
    ERCOT has revisited the underlying analysis and the risk factors used to compute ECRS quantities during the peak net load hours. ERCOT is proposing to update the methodology such that during the peak net load hours at least 90th percentile risk is covered.

## Slide 25: ERCOT Contingency Reserve Service (ECRS) Methodology
ECRS is reserved capacity that can respond in 10 minutes to recover frequency, cover forecast errors or ramps and replace deployed reserves.
ECRS requirements are computed as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support net load forecast errors during sustained net load ramps.
For 2024, ERCOT is considering to make the following changes
  Adjust the risk coverage during sunset hours to be at least 90th percentile
  Adjust the frequency recovery portion such that it (a) uses 2 years of historic information and cover 60% of historic net load and inertia conditions; and (b) adjust the quantity to account for Regulation requirement in the hour.
The preliminary ECRS quantities for January 2024 through August 2024 in subsequent slides have been computed using current methodology (2021, 2022 and 2023 Intra-Hour Net load and Net load Forecast, 2022 and 2023 system inertia conditions ) and updated Intra-hour Solar Over-Forecast Error Adjustment table.
  Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Notes: (b) change was to recognize the fact that during ECRS deployments that are triggered by unit trips, initially both Regulation and ECRS will be relied on to recover frequency and then ECRS will be used to recover deployed Regulation.

## Slide 26: Cold Start-up Time of OFFNS Resources in 2023
Cold Start time of units that were providing Non-Spin using OFFNS status was analyzed at 5-min resolution.
80th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
2 – Feb | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
3 – Mar | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
4 – Apr | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
5 – May | 18 min | 18 min | 18 min | 18 min | 24 min | 24 min
6 – Jun | 18 min | 18 min | 18 min | 30 min | 30 min | 30 min
7 – Jul | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
8 – Aug | 15 min | 18 min | 18 min | 30 min | 30 min | 18 min
Aug 17, 25, 30 | 18 min | 18 min | 30 min | 30 min | 30 min | 30 min
95th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
2 – Feb | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
3 – Mar | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
4 – Apr | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
5 – May | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
6 – Jun | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
7 – Jul | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
8 – Aug | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Aug 17, 25, 30 | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Notes: Decker Removed

## Slide 27: 2024 Intra-Hour Solar Adjustment Table
Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in 30-min ahead solar over forecast error per 1000 MW increase in installed solar capacity.
 | HE 1-2, 23-24 | HE 3-6 | HE 7-10 | HE 11-14 | HE 15-18 | HE 19-22
Jan | 0 | 0 | 0 | 21 | 20 | 0
Feb | 0 | 0 | 0 | 33 | 20 | 0
Mar | 0 | 0 | 0 | 33 | 73 | 0
Apr | 0 | 0 | 0 | 30 | 55 | 0
May | 0 | 0 | 0 | 59 | 96 | 26
Jun | 0 | 0 | 0 | 17 | 41 | 37
Jul | 0 | 0 | 0 | 23 | 23 | 8
Aug | 0 | 0 | 0 | 45 | 53 | 4
Sep | 0 | 0 | 0 | 64 | 56 | 0
Oct | 0 | 0 | 0 | 26 | 37 | 0
Nov | 0 | 0 | 0 | 1 | 4 | 0
Dec | 0 | 0 | 0 | 3 | 0 | 0

## Slide 28: Comparison of 30Min Ahead Net Load Forecast Error

## Slide 29: Hourly Average ECRS Comparison

## Slide 30: ECRS Comparison Mar

## Slide 31: ECRS Comparison Jan

## Slide 32: ECRS Comparison July

## Slide 33: ECRS Comparison August

## Slide 34: Non-Spin Feedback from September
Non-Spinning Reserve Service
    Consider if the look ahead can be varied seasonally.
    Review if Non-Spin quantities in off peak hours reflect the risk appropriately.
    Since ECRS and Non-Spin are used similarly, reduce the quantities of Non-Spin by some amount of procured ECRS.
Response
  In reviewing the cold start time of RUC’ed units by season, 6HA is appropriate look ahead. Most of the units RUC’ed in Winter have cold start times are much larger than 6 Hours.
  Recognizing that during night-time hours the net load tends to be lower and online committed capacity margin tends to be higher in comparison to peak hours, ERCOT is proposing a change to the risk coverage that will be used to derive the Non-Spin quantities in the early morning hours.

## Slide 35: Non-Spinning Reserve Methodology
Non-Spin is reserved capacity that can be started in 30 minutes to cover forecast errors, ramps or forced outages and replace deployed reserves until additional resources can be committed.
ERCOT is proposing one change to the methodology used to compute the minimum Non-Spin requirements in 2024. Specifically,
  Non-Spin quantities for HE23 to HE02 in Winter and HE23 in to HE06 rest of the year will be computed using 68th percentile of 6 Hours Ahead hourly average net load forecast error.
  Non-Spin quantities during rest of the hours will be based on 75th to 95th percentile of 6 Hours Ahead (HA) hourly average net load forecast error to compute Non-Spin quantities. The percentile used will be based on risk of a net load up-ramp in these hours.
The preliminary Non-Spin quantities for January 2024 through August 2024 in subsequent slides have been computed using current methodology (2021, 2022 and 2023 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the updated Solar Over-Forecast Error Adjustment table.
  Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 36: 2023 RUCs by Startup Time

## Slide 37: 2024 Intra-day Outage Table
The Intra-day Outage table helps account for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 38: Wind Over-Forecast Error Adjustment Table 2024
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind capacity.
Max: 31 MW per 1000 MW additional Wind capacity
Mean: 25 MW per 1000 MW additional Wind capacity

## Slide 39: Solar Over-Forecast Error Adjustment Table 2024
Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Max: 48 MW per 1000 MW additional solar capacity
Mean: 13 MW per 1000 MW additional solar capacity
Mean (Day time): 20 MW per 1000 MW additional solar capacity

## Slide 40: Distribution of HSL Minus Gen 2023
Avg HSL Minus Gen
Min HSL Minus Gen

## Slide 41: Hourly Average Non-Spin Comparison

## Slide 42: Non-Spin Comparison January

## Slide 43: Non-Spin Comparison April

## Slide 44: Non-Spin Comparison August

## Slide 45: Summary
Based on the analysis ERCOT has conducted thus far,
  ERCOT is not proposing any changes in the methodology used to compute Regulation Service for 2024.
  ERCOT is considering changes in the methodologies used to compute Responsive Reserve Service, ERCOT Contingency Reserve Service and Non-Spinning Reserve requirements for 2024.
The proposed timeline for this review is included alongside.
Using feedback received from last year’s experience, to make the AS Methodology review process more efficient, this year, ERCOT plans to provide relevant details on the proposed methodology during the September/October working group discussions. Following these discussions ERCOT will present an abridged summary of the proposed changes during the November/December discussions.
2024 Methodology Review Timeline
September 20, 2023 – PDCWG
September 22, 2023 – WMWG
October 6, 2023 – WMWG (Proposed)
October 10, 2022 – PDCWG (Proposed)
October 19, 2023 – OWG (Proposed)
November 01, 2023 – WMS
November 02, 2023 – ROS
December 04, 2023 – TAC
December 19, 2023 – BoD
Please reach out to Nitika Mago if you have any additional feedback on the proposed 2024 AS Methodology following this meeting.

## Slide 46
Suggestions?

## Slide 47: Solar Region Hourly Forecast Performance

## Slide 48: Predicted Solar Ramp Rate (PSRR) Error
Performance Metric | Persistence Ramp* | SCED PSRR | PSRR, IHPPF | PSRR, STPPF
Monthly MAE (MW per 5 minutes) | 177 | 96 | 101 | 96
Monthly MAE when 5-Min. Solar Ramp > 100 MW | 285 | 121 | 125 | 121
* Persistence Ramp assumes a 0 MW solar ramp

## Slide 49: Load Damping Ratio
ERCOT has computed the effective load damping ratio for frequency events since Jan 1, 2017. Based on this analysis, 2% is a reasonable damping ratio for RRS studies.
For each frequency event, the load dampening ratio is calculated as the delta load percentage change/ delta frequency percentage change.
%
where : Event Start Time

## Slide 50: Adequacy of Non-Spin quantities in 2023
Between Jan 1, 2023 and Jul 31, 2023,
  ~5% of the time the 6 Hour Ahead (HA) net load forecast error based Non-Spin was not sufficient to cover the 6HA risk
  ~16% of the time the margin in the 6 Hour Ahead (HA) net load forecast error based Non-Spin to cover the 6HA risk was less than 1,430 MW.

## Slide 51: Non-Spinning Reserve Service (Non-Spin) Deployments in 2023-Q1
Chart: Non-Spin Responsibility
Between Jan 2023 and Mar 2023, there were 12 events that resulted in deployment of offline Non-Spin.
Note that, between Jun 2023 and Jul 2023, an average ~36 % of Non-Spin was provided using online capacity and by Quick Start Generation Resources. This type of Non-Spin is always available to SCED to dispatch (with an offer floor of $75) and no operator action is needed to deploy this capacity.
Deployment Start Time | Deployment End Time | Deployment Duration | Max Deployment (MW) | Reason
1/3/2023 17:21 | 1/3/2023 18:30 | 01:09:00 | 1134.8 | Available Headroom not sufficient for projected 30-minutes net load ramp
1/6/2023 16:53 | 1/6/2023 18:15 | 01:22:00 | 1214.5 | Projected Ramp Available
1/9/2023 17:26 | 1/9/2023 17:56 | 00:30:00 | 514 | Projected Ramp Available
1/17/2023 5:46 | 1/17/2023 7:25 | 01:39:00 | 468.4 | Projected Ramp Available
2/8/2023 18:07 | 2/8/2023 18:40 | 00:33:00 | 544 | 
3/21/2023 19:01 | 3/21/2023 19:50 | 00:49:00 | 544.6 | 
3/22/2023 19:01 | 3/22/2023 19:51 | 00:50:00 | 524.91 | 
3/24/2023 5:55 | 3/24/2023 7:19 | 01:24:00 | 1832 | 
3/24/2023 18:55 | 3/24/2023 19:33 | 00:38:00 | 976 | 
3/25/2023 18:44 | 3/25/2023 20:48 | 02:04:00 | 1828.7 | 
3/26/2023 18:35 | 3/26/2023 20:03 | 01:28:00 | 2241 | 
3/27/2023 18:32 | 3/27/2023 21:05 | 02:33:00 | 731 | 

## Slide 52: Non-Spinning Reserve Service (Non-Spin) Deployments in 2023-Q2
Chart: Non-Spin Responsibility
Between April 2023 and Jun 2023, there were 8 events that resulted in deployment of offline Non-Spin.
Note that, between Jun 2023 and Jul 2023, an average ~36 % of Non-Spin was provided using online capacity and by Quick Start Generation Resources. This type of Non-Spin is always available to SCED to dispatch (with an offer floor of $75) and no operator action is needed to deploy this capacity.
Deployment Start Time | Deployment End Time | Deployment Duration | Max Deployment (MW) | Reason
4/14/2023 19:15 | 4/14/2023 20:14 | 00:59:00 | 622.2 | Available Headroom not sufficient for projected 30-minutes net load ramp
4/21/2023 18:54 | 4/21/2023 20:56 | 02:02:00 | 690.4 | Projected Ramp Available
4/29/2023 19:39 | 4/29/2023 21:11 | 01:32:00 | 1182.5 | Projected Ramp Available
5/4/2023 19:50 | 5/4/2023 20:25 | 00:35:00 | 447 | Projected Ramp Available
5/11/2023 19:18 | 5/11/2023 21:18 | 02:00:00 | 1048.7 | 
6/10/2023 19:16 | 6/10/2023 20:32 | 01:16:00 | 328 | 
6/18/2023 19:36 | 6/18/2023 20:22 | 00:46:00 | 447.5 | 
6/20/2023 16:24 | 6/20/2023 21:09 | 04:45:00 | 378.7 | 

## Slide 53: Non-Spinning Reserve Service (Non-Spin) Deployments in 2023-Q3
Between Jul 2023 and Aug 2023, there were 15 events that resulted in deployment of offline Non-Spin.
Note that, between Jul 2023 and Aug 2023, an average ~43 % of Non-Spin was provided using online capacity and by Quick Start Generation Resources. This type of Non-Spin is always available to SCED to dispatch (with an offer floor of $75) and no operator action is needed to deploy this capacity.
Deployment Start Time | Deployment End Time | Deployment Duration | Max Deployment (MW) | Reason
7/10/2023 19:21 | 7/10/2023 20:23 | 01:02:00 | 1080.9 | Available Headroom not sufficient for projected 30-minutes net load ramp
8/4/2023 17:04 | 8/4/2023 20:43 | 3:39:22 | 123 | 
8/7/2023 16:58 | 8/7/2023 20:19 | 3:21:27 | 129.1 | 
8/10/2023 15:29 | 8/10/2023 20:23 | 4:53:33 | 116.9 | 
8/11/2023 18:34 | 8/11/2023 20:09 | 1:34:37 | 112 | 
8/12/2023 18:57 | 8/12/2023 20:13 | 1:16:18 | 244 | 
8/13/2023 19:02 | 8/13/2023 20:06 | 1:03:24 | 199.1 | 
8/15/2023 19:37 | 8/15/2023 20:43 | 1:05:37 | 1926 | 
8/17/2023 14:41 | 8/17/2023 20:58 | 6:16:58 | 2024 | 
8/20/2023 19:14 | 8/20/2023 21:17 | 2:03:02 | 267 | 
8/24/2023 16:09 | 8/24/2023 21:06 | 4:57:13 | 231.2 | 
8/25/2023 17:57 | 8/25/2023 21:02 | 3:04:42 | 158.2 | 
8/29/2023 18:24 | 8/29/2023 20:07 | 1:42:28 | 115.5 | 
8/30/2023 18:02 | 8/30/2023 20:50 | 2:47:59 | 170.7 | 
8/31/2023 18:26 | 8/31/2023 20:03 | 1:36:38 | 114 | 
Chart: Non-Spin Responsibility
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Jul-23 | Aug-23
NSRS-Offline | 1553.8846 | 1621.9249 | 1762.7945 | 1782.4102 | 1823.1138 | 1855.9452 | 2405.2676 | 2385.802 | 2355.013 | 2351.9233 | 1932.9861 | 1959.539 | 1668.6809 | 1536.513 | 1432.1027 | 1354.7871 | 1288.6913 | 1243.3173 | 1121.0135 | 1101.4805 | 1158.0517 | 1216.3497 | 1595.5468 | 1693.453 | 1165.3205 | 1224.4074 | 1237.4409 | 1268.88 | 1349.2412 | 1343.6613 | 1418.7085 | 1391.5656 | 1383.4594 | 1381.5171 | 1448.7748 | 1293.9944 | 957.9593 | 815.7163 | 558.1506 | 616.5282 | 602.5868 | 609.8443 | 532.9517 | 576.1229 | 681.3371 | 687.1453 | 881.8159 | 1051.6426
NSRS-Online | 271.6289 | 255.8724 | 312.4973 | 298.4694 | 297.9607 | 284.808 | 395.8029 | 423.4334 | 448.8354 | 443.5995 | 354.6356 | 390.1498 | 642.1352 | 756.8418 | 869.2077 | 885.8493 | 936.69 | 973.4698 | 866.1968 | 879.2047 | 816.3629 | 868.9835 | 457.0845 | 320.2601 | 214.7133 | 222.9922 | 252.0972 | 252.8968 | 252.5523 | 251.8524 | 259.1205 | 270.0238 | 276.637 | 274.211 | 352.0629 | 523.5143 | 761.6255 | 790.2686 | 662.6077 | 622.8094 | 633.0831 | 639.2853 | 614.3753 | 582.0762 | 513.4976 | 646.6528 | 548.6844 | 367.1052
NSRS-QSGR | 475.1381 | 421.2155 | 575.7048 | 570.1364 | 530.0029 | 511.779 | 665.4426 | 657.7229 | 671.4032 | 668.461 | 599.6558 | 537.5339 | 460.3258 | 481.9194 | 525.9574 | 590.8087 | 604.7639 | 609.4529 | 601.1055 | 609.1019 | 618.4436 | 479.2261 | 574.4384 | 615.3287 | 651.1094 | 580.3519 | 761.3842 | 742.2555 | 659.0226 | 658.4187 | 731.8161 | 758.4752 | 760.3455 | 765.9461 | 735.7768 | 712.93 | 694.5539 | 804.9278 | 787.9885 | 781.7753 | 783.5205 | 781.1318 | 758.5752 | 760.4704 | 715.7135 | 567.3326 | 645.8413 | 729.7729
Total NSRS Responsibility | 2300.3967 | 2299.0129 | 2650.9968 | 2651.0162 | 2651.0774 | 2652.5323 | 3466.5129 | 3466.5065 | 3467.0323 | 3463.8679 | 2885.7937 | 2886.0871 | 2771.1419 | 2768.4129 | 2827.2678 | 2831.4452 | 2829.6807 | 2822.6723 | 2588.3158 | 2581.2923 | 2587.0968 | 2563.2787 | 2626.9987 | 2629.042 | 2035.1271 | 2039.5258 | 2264.2803 | 2270.0968 | 2271.529 | 2271.2097 | 2429.2193 | 2432.9194 | 2434.5323 | 2441.4581 | 2548.4662 | 2540.3225 | 2426.7936 | 2416.9904 | 2022.65 | 2034.4064 | 2029.5903 | 2026.4355 | 1913.5378 | 1920.4216 | 1916.0451 | 1895.6242 | 2078.5739 | 2157.598

## Slide 54: Net Load Forecast Error Spread
Call out for July HE19

## Slide 55: Forecast Variability Process
ERCOT assess the netload forecast variability for Current Operation Day + 2 and may procure up to an additional 1,000 MW of Non-Spin for specific Operating Hours.
The approach for determining the additional increase will be updated such that the additional Non-Spin may be procured for Operating Hours that are
  identified as having an increased potential of high forecast variability,
  there is a risk that the actual net load during these Operating Hours could be higher than forecast (after making appropriate forecast model selection) AND
  the expected available capacity and expected reserves including the posted minimum Non-Spin requirements during these Operating Hours is not sufficient to cover the projected net load forecast uncertainty risk.
ERCOT procured additional Non-Spin for
  Jul 29, Aug 1, Aug 2, Aug 14, Aug 27, Aug 29, Aug 30, and Sep 3 and Sep 4 in 2021
  Jan. 2, Jan. 3, Jan. 20, Feb. 3, Feb. 4, May 22, May 23, May 24, June 1 in 2022.