## Slide 1: 2024 AS Methodology Recommendations
Presented at:
Wholesale Market Subcommittee
Carrie Bivens
ERCOT IMM
November 1, 2023

## Slide 2: 2024 AS Methodology Incremental Recommendations
    Change the non-spin 6-hour ahead error requirement to 4-hour ahead.
      ERCOT stated that the 6 hours is to address RUC start times.
      Additional MWs are self-committed between 6 hours and hour ahead.
      HRUC data from 2022 to Sep 2023 also shows start-up times at the time of the RUC instruction more in line with 4 hours.
    Use 10-minute ahead net load errors for ECRS methodology instead of 30-minute ahead.
      The defined net load ramp trigger conditions are using a 10-minute time horizon.

## Slide 3: 2022 to Sep 2023 COP Self-Committed Capacity Increase From 6 Hour-Ahead to 1 Hour-Ahead
Chart: Self-Commitment Capacity Increase From 6 Hour-Ahead COP (MW)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1HA 50th | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5 | 76.5 | 158.9 | 164.5 | 187.2 | 233.5 | 246.5 | 241 | 177.5 | 73 | 0 | 0 | 0
1HA 75th | 251 | 223.5 | 169.4 | 92 | 47.2 | 17 | 17 | 48 | 120 | 208 | 245 | 305.3 | 404.7 | 454 | 476.6 | 558 | 578 | 599.5 | 535 | 455.5 | 325.4 | 249 | 247 | 258
2HA 50th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 56.95 | 75 | 73 | 144 | 171 | 182.5 | 140.3 | 48.4 | 0 | 0 | 0
2HA 75th | 236 | 177.25 | 106 | 53 | 17 | 0 | 0 | 0 | 26 | 65 | 200 | 243 | 308 | 350 | 350 | 413 | 460 | 498 | 496.55 | 392 | 281 | 195 | 218.35 | 231
3HA 50th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 90 | 96.5 | 93.75 | 17 | 0 | 0 | 0
3HA 75th | 191 | 119 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 180 | 250 | 260 | 270 | 270 | 287 | 347.5 | 361 | 314.5 | 255 | 120 | 107.5 | 165
4HA 50th | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4HA 75th | 123.5 | 58.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 195 | 171 | 135 | 181.7 | 195 | 259 | 227 | 150 | 48.4 | 46 | 47.2

## Slide 4: 2022 to Sep 2023 HRUC Startup Times
Chart: Start-up Times (in Hours)
| EXTENSION | X <= 1 | X <= 2 | X <= 3 | X <= 4 | X <= 5 | X <= 6 | X <= 7 | X > 7
% of HRUC Startups | 0.075188 | 0.10048 | 0.22351 | 0.35133 | 0.5188 | 0.61928 | 0.76692 | 0.78674 | 1

## Slide 5: 2022 to Sep 2023 HRUC Startup Times Across the Commitment Block by Hour
Chart: Annual Startup Time Range % of HRUC MW
X <= 4 | 0.52829 | 0.5153 | 0.51043 | 0.51601 | 0.48024 | 0.5111 | 0.51323 | 0.52748 | 0.53748 | 0.56341 | 0.56694 | 0.61779 | 0.63658 | 0.61767 | 0.59549 | 0.58236 | 0.56929 | 0.54512 | 0.509 | 0.51967 | 0.50178 | 0.50392 | 0.45706 | 0.41778
X > 4 | 0.47171 | 0.4847 | 0.48957 | 0.48399 | 0.51976 | 0.4889 | 0.48677 | 0.47252 | 0.46252 | 0.43659 | 0.43306 | 0.38221 | 0.36342 | 0.38233 | 0.40451 | 0.41764 | 0.43071 | 0.45488 | 0.491 | 0.48033 | 0.49822 | 0.49608 | 0.54294 | 0.58222

## Slide 6: 2022 to Sep 2023 HRUC Startup Times Across the Commitment Block by Season & Hour
Chart: Spring (Mar-May)
X <= 4 | 0.67699 | 0.67724 | 0.68333 | 0.68322 | 0.68333 | 0.64915 | 0.80346 | 0.71796 | 0.74107 | 0.78365 | 0.81928 | 0.78954 | 0.63694 | 0.63747 | 0.57983 | 0.55657 | 0.54623 | 0.51748 | 0.44781 | 0.45243 | 0.45156 | 0.45541 | 0.49645 | 0.45789
X > 4 | 0.32301 | 0.32276 | 0.31667 | 0.31678 | 0.31667 | 0.35085 | 0.19654 | 0.28204 | 0.25893 | 0.21635 | 0.18072 | 0.21046 | 0.36306 | 0.36253 | 0.42017 | 0.44343 | 0.45377 | 0.48252 | 0.55219 | 0.54757 | 0.54844 | 0.54459 | 0.50355 | 0.54211
Chart: Summer (Jun-Aug)
X <= 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14917 | 0.23914 | 0.66373 | 0.77433 | 0.68228 | 0.65686 | 0.64696 | 0.64195 | 0.6599 | 0.64581 | 0.66961 | 0.66022 | 0.64623 | 0.35682 | 0.15904
X > 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85083 | 0.76086 | 0.33627 | 0.22567 | 0.31772 | 0.34314 | 0.35304 | 0.35805 | 0.3401 | 0.35419 | 0.33039 | 0.33978 | 0.35377 | 0.64318 | 0.84096
Chart: Winter (Dec-Feb)
X <= 4 | 0.58965 | 0.57916 | 0.569 | 0.57624 | 0.51395 | 0.53523 | 0.45814 | 0.47661 | 0.48475 | 0.51126 | 0.44158 | 0.5065 | 0.46485 | 0.4316 | 0.42734 | 0.39961 | 0.35957 | 0.33847 | 0.38068 | 0.38033 | 0.38039 | 0.4105 | 0.4139 | 0.40377
X > 4 | 0.41035 | 0.42084 | 0.431 | 0.42376 | 0.48605 | 0.46477 | 0.54186 | 0.52339 | 0.51525 | 0.48874 | 0.55842 | 0.4935 | 0.53515 | 0.5684 | 0.57266 | 0.60039 | 0.64043 | 0.66153 | 0.61932 | 0.61967 | 0.61961 | 0.5895 | 0.5861 | 0.59623
Chart: Fall (Sep-Nov)
X <= 4 | 0.26452 | 0.26483 | 0.26483 | 0.26483 | 0.26483 | 0.40643 | 0.47885 | 0.45542 | 0.4528 | 0.52361 | 0.56228 | 0.54798 | 0.56484 | 0.56484 | 0.54803 | 0.55265 | 0.54781 | 0.50879 | 0.49457 | 0.5015 | 0.45638 | 0.49229 | 0.49572 | 0.45906
X > 4 | 0.73548 | 0.73517 | 0.73517 | 0.73517 | 0.73517 | 0.59357 | 0.52115 | 0.54458 | 0.5472 | 0.47639 | 0.43772 | 0.45202 | 0.43516 | 0.43516 | 0.45197 | 0.44735 | 0.45219 | 0.49121 | 0.50543 | 0.4985 | 0.54362 | 0.50771 | 0.50428 | 0.54094

## Slide 7: 3 to 6 Hour-Ahead Net Load Forecast Error Percentile Comparison for Oct 2021 to Sep 2023
Chart: 
| 95 | 75 | 68 | 50
3ha offpeak | 0.0868 | 0.0327 | 0.0239 | 0.0041
3ha onpeak | 0.0751 | 0.0212 | 0.0121 | -0.0061
4ha offpeak | 0.1128 | 0.0414 | 0.03 | 0.0064
4ha onpeak | 0.0828 | 0.0204 | 0.0108 | -0.0094
5ha offpeak | 0.1289 | 0.0473 | 0.0336 | 0.0072
5ha onpeak | 0.0856 | 0.0199 | 0.0096 | -0.0119
6ha offpeak | 0.1419 | 0.0505 | 0.0365 | 0.0086
6ha onpeak | 0.0906 | 0.0188 | 0.0085 | -0.0138
*Positive indicates Under-Forecast
*Negative indicates Over-Forecast

## Slide 8: 4 & 6 Hour-Ahead Net Load Forecast Error Percentile Comparison for Oct 2021 to Sep 2023
*Positive indicates Under-Forecast
Chart: Winter (Dec-Feb)
p95_6ha | 0.1629 | 0.1934 | 0.1936 | 0.1778 | 0.1348 | 0.1094 | 0.1052 | 0.1064 | 0.1175 | 0.1472 | 0.1198 | 0.1074 | 0.1136 | 0.1087 | 0.1196 | 0.1713 | 0.1428 | 0.086 | 0.0985 | 0.0926 | 0.1201 | 0.1061 | 0.1139 | 0.1247
p75_6ha | 0.0552 | 0.0731 | 0.0776 | 0.0786 | 0.0632 | 0.0454 | 0.0275 | 0.0194 | 0.0159 | 0.043 | 0.0263 | 0.0188 | 0.0241 | 0.0252 | 0.0206 | 0.0358 | 0.0311 | 0.0272 | 0.0256 | 0.0171 | 0.0236 | 0.0297 | 0.0299 | 0.0421
p68_6ha | 0.0397 | 0.0555 | 0.0641 | 0.0631 | 0.0522 | 0.0309 | 0.0199 | 0.0303
p95_4ha | 0.1351 | 0.1564 | 0.1414 | 0.1188 | 0.1079 | 0.0995 | 0.0876 | 0.0905 | 0.09 | 0.1286 | 0.1024 | 0.1142 | 0.1116 | 0.1263 | 0.123 | 0.1329 | 0.1214 | 0.0741 | 0.0848 | 0.0917 | 0.0942 | 0.084 | 0.0932 | 0.1139
p75_4ha | 0.0514 | 0.0636 | 0.0677 | 0.06 | 0.0434 | 0.0371 | 0.0248 | 0.0227 | 0.0111 | 0.041 | 0.033 | 0.0266 | 0.0242 | 0.0346 | 0.0278 | 0.0306 | 0.0276 | 0.0237 | 0.0264 | 0.022 | 0.0149 | 0.0228 | 0.0372 | 0.0455
p68_4ha | 0.0382 | 0.0507 | 0.0436 | 0.0467 | 0.0352 | 0.0221 | 0.0216 | 0.0352
Chart: Spring (Mar-May)
p95_6ha | 0.1693 | 0.1986 | 0.2148 | 0.2402 | 0.2336 | 0.2118 | 0.1891 | 0.1715 | 0.1417 | 0.1781 | 0.1594 | 0.1019 | 0.1073 | 0.1348 | 0.1316 | 0.1127 | 0.1092 | 0.1083 | 0.0739 | 0.0453 | 0.0667 | 0.0776 | 0.094 | 0.1126
p75_6ha | 0.076 | 0.0873 | 0.1165 | 0.1284 | 0.0985 | 0.0965 | 0.0815 | 0.0735 | 0.0584 | 0.0514 | 0.046 | 0.0255 | 0.0177 | 0.0184 | 0.0339 | 0.0341 | 0.0304 | 0.0349 | 0.0222 | 0.0125 | 0.0217 | 0.0273 | 0.0456 | 0.0574
p68_6ha | 0.0601 | 0.067 | 0.0969 | 0.1077 | 0.0838 | 0.0717 | 0.0223 | 0.0394
p95_4ha | 0.1326 | 0.1685 | 0.1767 | 0.1714 | 0.1637 | 0.1552 | 0.1364 | 0.1311 | 0.1246 | 0.1606 | 0.1366 | 0.1075 | 0.1243 | 0.1556 | 0.1226 | 0.0848 | 0.0812 | 0.1038 | 0.072 | 0.0595 | 0.0724 | 0.0847 | 0.0816 | 0.0924
p75_4ha | 0.0582 | 0.0801 | 0.0788 | 0.0804 | 0.0723 | 0.0759 | 0.0621 | 0.0567 | 0.0551 | 0.046 | 0.045 | 0.0276 | 0.0349 | 0.0368 | 0.0321 | 0.0245 | 0.025 | 0.0341 | 0.0207 | 0.0055 | 0.0301 | 0.0297 | 0.0384 | 0.0378
p68_4ha | 0.0482 | 0.068 | 0.0684 | 0.0638 | 0.0572 | 0.0556 | 0.0282 | 0.0204
Chart: Summer (Jun-Aug)
p95_6ha | 0.062 | 0.0769 | 0.0993 | 0.1106 | 0.1059 | 0.0977 | 0.0887 | 0.0919 | 0.0993 | 0.0553 | 0.0323 | 0.015 | 0.0128 | 0.0093 | 0.0132 | 0.0139 | 0.0222 | 0.0335 | 0.0378 | 0.027 | 0.0367 | 0.046 | 0.0444 | 0.0516
p75_6ha | 0.0336 | 0.0304 | 0.0463 | 0.0501 | 0.0456 | 0.0458 | 0.0398 | 0.0439 | 0.045 | 0.0161 | -0.006 | -0.0122 | -0.0165 | -0.0202 | -0.0108 | -0.0068 | -0.0054 | 0.0055 | 0.01 | -0.0016 | 0.0104 | 0.0172 | 0.02 | 0.0184
p68_6ha | 0.0229 | 0.0215 | 0.0386 | 0.042 | 0.0401 | 0.0359 | 0.0133 | 0.0126
p95_4ha | 0.0618 | 0.0737 | 0.0853 | 0.0883 | 0.0777 | 0.0806 | 0.0756 | 0.0797 | 0.0994 | 0.0466 | 0.0259 | 0.0197 | 0.0271 | 0.0182 | 0.0085 | 0.0123 | 0.0218 | 0.034 | 0.035 | 0.0266 | 0.0353 | 0.0396 | 0.0526 | 0.0511
p75_4ha | 0.0284 | 0.0321 | 0.0364 | 0.0374 | 0.0341 | 0.0345 | 0.0337 | 0.0421 | 0.0432 | 0.0081 | -0.0044 | -0.0087 | -0.0003 | -0.0034 | -0.0081 | -0.011 | -0.0027 | 0.0071 | 0.0096 | 0.0027 | 0.0146 | 0.017 | 0.0241 | 0.0192
p68_4ha | 0.0212 | 0.0228 | 0.0291 | 0.0293 | 0.0262 | 0.0263 | 0.0188 | 0.0103
Chart: Fall (Sep-Nov)
p95_6ha | 0.0789 | 0.1032 | 0.1396 | 0.0981 | 0.0907 | 0.0792 | 0.0665 | 0.0774 | 0.0859 | 0.0801 | 0.0548 | 0.0573 | 0.064 | 0.0486 | 0.0374 | 0.0506 | 0.0478 | 0.0618 | 0.0675 | 0.0567 | 0.06 | 0.0745 | 0.0742 | 0.0777
p75_6ha | 0.022 | 0.0292 | 0.0454 | 0.0446 | 0.0338 | 0.0283 | 0.0241 | 0.0199 | 0.0127 | 0.0299 | 0.0183 | 0.0066 | 0.009 | 0.0019 | -0.001 | 0.0079 | 0.008 | 0.0146 | 0.0076 | 0.02 | 0.0166 | 0.0191 | 0.0159 | 0.0195
p68_6ha | 0.0136 | 0.0179 | 0.0327 | 0.0317 | 0.0262 | 0.0179 | 0.0082 | 0.0114
p95_4ha | 0.087 | 0.0934 | 0.0993 | 0.0718 | 0.0635 | 0.0656 | 0.0693 | 0.0727 | 0.0855 | 0.0828 | 0.0664 | 0.0588 | 0.0613 | 0.0722 | 0.0437 | 0.0393 | 0.0456 | 0.0713 | 0.0681 | 0.0514 | 0.0587 | 0.0507 | 0.0753 | 0.095
p75_4ha | 0.031 | 0.034 | 0.0363 | 0.0312 | 0.0284 | 0.0246 | 0.0236 | 0.0217 | 0.0176 | 0.033 | 0.0224 | 0.0142 | 0.0162 | 0.0178 | 0.0093 | 0.0041 | 0.0049 | 0.0187 | 0.0209 | 0.0252 | 0.0123 | 0.0125 | 0.0086 | 0.0197
p68_4ha | 0.0177 | 0.024 | 0.0292 | 0.0225 | 0.0184 | 0.0158 | 0.001 | 0.0107

## Slide 9: 10 to 30 Minute-Ahead Net Load Forecast Error Percentile Comparison for Oct 2021 to Sep 2023
Chart: 
| 95 | 90 | 85 | 50
10ma offpeak | 0.0216 | 0.0149 | 0.0112 | -0.002
10ma onpeak | 0.02 | 0.0137 | 0.0101 | -0.0018
15ma offpeak | 0.0264 | 0.0185 | 0.014 | -0.0021
15ma onpeak | 0.0247 | 0.017 | 0.0126 | -0.0019
20ma offpeak | 0.0308 | 0.0218 | 0.0167 | -0.002
20ma onpeak | 0.0291 | 0.02 | 0.015 | -0.002
30ma offpeak | 0.0392 | 0.0279 | 0.0216 | -0.0017
30ma onpeak | 0.0384 | 0.0263 | 0.0198 | -0.0019
*Positive indicates Under-Forecast
*Negative indicates Over-Forecast

## Slide 10: 10 & 30 Minute-Ahead Net Load Forecast Error Percentile Comparison for Oct 2021 to Sep 2023
Chart: 
p95_30ma | 0.0426 | 0.0481 | 0.0458 | 0.0446 | 0.0439 | 0.041 | 0.0448 | 0.0374 | 0.06 | 0.0596 | 0.0489 | 0.0464 | 0.0487 | 0.0476 | 0.0512 | 0.0482 | 0.0621 | 0.0448 | 0.0402 | 0.0201 | 0.0216 | 0.0313 | 0.0332 | 0.0386
p90_30ma | 0.0409 | 0.0355 | 0.0272 | 0.013
p85_30ma | 0.0245 | 0.0236 | 0.0274 | 0.0257 | 0.0255 | 0.0216 | 0.0258 | 0.023 | 0.037 | 0.0404 | 0.0227 | 0.0236 | 0.0221 | 0.0229 | 0.0243 | 0.0239 | 0.0323 | 0.0279 | 0.0182 | 0.0083 | 0.0104 | 0.0169 | 0.0182 | 0.0198
p95_10ma | 0.0249 | 0.0245 | 0.0246 | 0.0258 | 0.0236 | 0.0208 | 0.0239 | 0.0191 | 0.0283 | 0.0298 | 0.0222 | 0.0215 | 0.0234 | 0.0257 | 0.0261 | 0.0311 | 0.0372 | 0.0268 | 0.0201 | 0.0091 | 0.0115 | 0.0166 | 0.0179 | 0.0206
p90_10ma | 0.0222 | 0.02 | 0.013 | 0.0056
p85_10ma | 0.0123 | 0.011 | 0.0139 | 0.0145 | 0.0121 | 0.0096 | 0.0135 | 0.0113 | 0.0173 | 0.0175 | 0.0099 | 0.0107 | 0.0106 | 0.0117 | 0.0129 | 0.0144 | 0.017 | 0.0155 | 0.0084 | 0.0032 | 0.0046 | 0.0083 | 0.0094 | 0.0095
Chart: 
p95_30ma | 0.0484 | 0.0553 | 0.0543 | 0.0496 | 0.0566 | 0.0532 | 0.0484 | 0.0509 | 0.0704 | 0.0519 | 0.0399 | 0.049 | 0.0487 | 0.0411 | 0.0348 | 0.0278 | 0.0344 | 0.0431 | 0.0505 | 0.0425 | 0.0382 | 0.0271 | 0.0355 | 0.0479
p90_30ma | 0.0242 | 0.03 | 0.0367 | 0.03
p85_30ma | 0.0249 | 0.0302 | 0.0332 | 0.0325 | 0.0317 | 0.0284 | 0.0318 | 0.0315 | 0.0453 | 0.0253 | 0.0202 | 0.0288 | 0.0254 | 0.0217 | 0.0179 | 0.0137 | 0.0171 | 0.0224 | 0.0277 | 0.0215 | 0.0229 | 0.0116 | 0.019 | 0.0241
p95_10ma | 0.0274 | 0.0291 | 0.0323 | 0.0288 | 0.0317 | 0.0265 | 0.0289 | 0.0261 | 0.0339 | 0.0246 | 0.019 | 0.0244 | 0.0232 | 0.0211 | 0.0175 | 0.0177 | 0.0222 | 0.0283 | 0.0306 | 0.0242 | 0.0195 | 0.0153 | 0.0205 | 0.0275
p90_10ma | 0.0145 | 0.0191 | 0.0225 | 0.0174
p85_10ma | 0.013 | 0.0166 | 0.0161 | 0.0181 | 0.0164 | 0.0137 | 0.0174 | 0.0152 | 0.021 | 0.0111 | 0.0095 | 0.0136 | 0.0124 | 0.0109 | 0.0084 | 0.0078 | 0.0107 | 0.0142 | 0.0176 | 0.0133 | 0.0113 | 0.0067 | 0.0101 | 0.0139
Chart: 
p95_30ma | 0.0294 | 0.0338 | 0.0351 | 0.0331 | 0.0294 | 0.0334 | 0.0391 | 0.0284 | 0.0316 | 0.0167 | 0.0229 | 0.0237 | 0.0191 | 0.0187 | 0.0176 | 0.0158 | 0.0205 | 0.0208 | 0.0237 | 0.0246 | 0.023 | 0.0201 | 0.0183 | 0.0222
p90_30ma | 0.0142 | 0.0161 | 0.0185 | 0.0182
p85_30ma | 0.0178 | 0.0208 | 0.0201 | 0.0203 | 0.0183 | 0.0217 | 0.0279 | 0.0181 | 0.0176 | 0.004 | 0.0138 | 0.0163 | 0.013 | 0.0109 | 0.0098 | 0.0085 | 0.0111 | 0.0132 | 0.0149 | 0.0135 | 0.0162 | 0.0114 | 0.0084 | 0.0135
p95_10ma | 0.018 | 0.0198 | 0.0193 | 0.0194 | 0.016 | 0.0196 | 0.0204 | 0.0144 | 0.0141 | 0.0085 | 0.0128 | 0.0133 | 0.0109 | 0.0104 | 0.0092 | 0.01 | 0.0122 | 0.0127 | 0.0168 | 0.0149 | 0.0149 | 0.0112 | 0.0107 | 0.0129
p90_10ma | 0.0083 | 0.0097 | 0.0128 | 0.0115
p85_10ma | 0.0102 | 0.0114 | 0.011 | 0.0109 | 0.0096 | 0.0124 | 0.0139 | 0.0073 | 0.0056 | 0.0011 | 0.0068 | 0.0084 | 0.0065 | 0.0061 | 0.0053 | 0.0052 | 0.0063 | 0.0077 | 0.0103 | 0.0092 | 0.0101 | 0.0051 | 0.0047 | 0.0074
Chart: 
p95_30ma | 0.0304 | 0.0323 | 0.032 | 0.0356 | 0.0312 | 0.0362 | 0.0418 | 0.0392 | 0.0478 | 0.0554 | 0.0259 | 0.0351 | 0.0278 | 0.0249 | 0.0248 | 0.0284 | 0.036 | 0.0449 | 0.0352 | 0.0246 | 0.0186 | 0.0237 | 0.0264 | 0.0312
p90_30ma | 0.0255 | 0.0339 | 0.0286 | 0.0161
p85_30ma | 0.019 | 0.0192 | 0.0183 | 0.0215 | 0.0193 | 0.0187 | 0.0265 | 0.0226 | 0.0293 | 0.0356 | 0.0115 | 0.0191 | 0.0163 | 0.015 | 0.0136 | 0.0123 | 0.0196 | 0.0261 | 0.024 | 0.012 | 0.007 | 0.0118 | 0.0142 | 0.0189
p95_10ma | 0.0165 | 0.0188 | 0.0181 | 0.0205 | 0.0177 | 0.0188 | 0.0222 | 0.0191 | 0.0248 | 0.0269 | 0.0147 | 0.0174 | 0.0143 | 0.0138 | 0.0144 | 0.0164 | 0.0216 | 0.0262 | 0.0189 | 0.0123 | 0.0086 | 0.0126 | 0.0139 | 0.0166
p90_10ma | 0.0153 | 0.0192 | 0.0152 | 0.008
p85_10ma | 0.009 | 0.0101 | 0.0105 | 0.0118 | 0.0101 | 0.0093 | 0.0146 | 0.0103 | 0.0138 | 0.0142 | 0.0059 | 0.0094 | 0.0079 | 0.0073 | 0.0075 | 0.0075 | 0.0115 | 0.0151 | 0.0129 | 0.006 | 0.0025 | 0.0058 | 0.0072 | 0.0087
*Positive indicates Under-Forecast