- Summary of Nodal Operating Guide Revisions

- Effective:  November 1, 2023

Section 1:

NOGRR230 – WAN Participant Security

This Nodal Operating Guide Revision Request (NOGRR) ensures integrity of Wide Area Network (WAN) Data transmission by adding a requirement to share data in a way that prevents Denial of Service (DoS) and Distributed Denial of Service (DDoS) attacks.

Revised Subsection:  1.4

- Section 2:

NOGRR247 – Change UFLS Stages and Load Relief Amounts

This Nodal Operating Guide Revision Request (NOGRR) modifies the ERCOT automatic Under-Frequency Load Shed (UFLS) program by increasing the number of Load shed stages from three to five and changing the Transmission Operator (TO) Load relief amounts to uniformly increment by 5% for each stage, adds a UFLS minimum time delay of six cycles (0.1 seconds), and adds 59.1 Hz to the list of UFLS stages in paragraph (3) of Section 2.6.1, Automatic Firm Load Shedding, revises the grey-boxed language from NOGRR226, Addition of Supplemental UFLS Stages, in Section 2.6.1 to provide that the TO Load value used to determine the TO Load at each frequency threshold in Table 1, Standard UFLS Stage, will be the value of TO Load at the time frequency reaches 59.5 Hz, rather than the value of TO Load at the time of reaching each successive frequency threshold, consistent with the current method for determining TO Load in Table 1, and assigns an effective date of October 1, 2026 for both NOGRR226 and NOGRR247 grey-boxed language.

Revised Subsection:  2.6.1 [effective upon system implementation (and partially no earlier than October 1, 2026)]

NOGRR250 – Related to NPRR1171, Requirements for DGRs and DESRs on Circuits Subject to Load Shedding

This Nodal Operating Guide Revision Request (NOGRR) removes language that prohibits Distribution Service Providers (DSPs) from connecting Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs) to circuits included in an Under-Frequency Load Shed (UFLS) scheme to align with NPRR1171, Requirements for DGRs and DESRs on Circuits Subject to Load Shedding, and recognizes that some DGRs and DESRs may be connected to circuits that are subject to Load shed.

Revised Subsection:  2.6.1 [effective upon system implementation of NPRR1171]

- Section 3:

NOGRR249 – Communication of System Operating Limit Exceedances

This Nodal Operating Guide Revision Request (NOGRR) specifies the methods for Transmission Operators (TOs) to receive electronic communication of system operating limit exceedances from ERCOT.

Revised Subsection:  3.7 [effective on April 1, 2024]

- Section 4:

NOGRR252 – Related to NPRR1176, Update to EEA Trigger Levels

This Nodal Operating Guide Revision Request (NOGRR) aligns Nodal Operating Guide language with NPRR1176, Update to EEA Trigger Levels, which revises the Energy Emergency Alert (EEA) procedures to require a declaration of EEA Level 3 when Physical Responsive Capability (PRC) cannot be maintained above 1,500 MW and will require ERCOT to shed firm Load to recover 1,500 MW of reserves within 30 minutes, modifies the trigger levels for EEA Level 1 and EEA Level 2, changes the trigger for ERCOT’s consideration of alternative transmission ratings or configurations from Advisory to Watch when PRC drops below 3,000 MW, and restores a frequency trigger for the declaration of EEA Level 3 if the steady-state frequency drops below 59.8 Hz for any period of time.

Revised Subsections:  4.2.2, 4.5.3 and 4.5.3.1

- Section 7:

NOGRR230 – WAN Participant Security

See Section 1 above.

- Revised Subsection:  7.1.2

- Section 8:

NOGRR251 – Add Cold Weather Conditions to Template for Emergency Operations Plan

This Nodal Operating Guide Revision Request (NOGRR) aligns Section 8, Attachment L with North American Electric Reliability Corporation (NERC) Reliability Standard EOP-011-2, Emergency Preparedness and Operations, by adding cold weather conditions to the template used for the development of emergency operations plans.

- Revised Attachment:  L

NOGRR215 – Limit Use of Remedial Action Schemes

This Nodal Operating Guide Revision Request (NOGRR) allows new Remedial Action Schemes (RASs) to be used only to address an actual or anticipated violation of transmission security criteria when market tools are insufficient to address those violations, and clarifies the procedures for retiring RASs.

- Revised Attachment:  K

- Section 11:

NOGRR215 – Limit Use of Remedial Action Schemes

See Section 8 above.

- Revised Subsections:  11.1, 11.2 and 11.2.1 [effective upon system implementation (paragraph (3) of Section 11.1 and paragraph (1) of Section 11.2); and November 1, 2023 for all remaining language]

- Administrative Changes:

- Non-substantive administrative changes were made such as spelling corrections, formatting, and correcting Section numbering and references.

Revised Subsections:  2.3.1.2, 3.7, 7.1.1, 7.1.2, 8K, 8L and 11.2