## Slide 1
Balancing Operations Planning Staff
Proposed 2024 Ancillary Service Methodology
with Details

## Slide 2: Introduction
ERCOT has reviewed the methodology to determine minimum Ancillary Service (AS) requirements and is proposing the following changes for 2024.
  No changes in the methodology used for computing Regulation Service.
    To better reflect the balancing needs from the hour, ERCOT has updated the Net Load variability calculation to include additional accounting based on accumulated Area Control Error (ACE).
  Remove the 2,800 MW RRS floor that is applied to summer peak hours for 2024. A Minimum 2,300 MW of RRS will apply to all hours.
2024 Methodology Review Timeline
September 20, 2023 – PDCWG (link)
September 22, 2023 – WMWG (link)
October 6, 2023 – WMWG (Proposed)
October 10, 2022 – PDCWG (Proposed)
October 19, 2023 – OWG (Proposed)
November 01, 2023 – WMS
November 02, 2023 – ROS
December 04, 2023 – TAC
December 19, 2023 – BoD
  Change methodology for ERCOT Contingency Reserve Service (ECRS) to (1) Adjust the risk coverage during sunset hours to be at least 90th percentile, (2) Adjust the frequency recovery portion such that it (2)(a) uses 2 years of historic information and cover 60% of historic net load and inertia conditions; and (2)(b) accounts for Regulation requirement in the hour.
  Change methodology for Non-Spinning Reserve Service (Non-Spin) quantities specifically for HE23 to HE02 in Winter and HE23 in to HE06 rest of the year to be computed using 68th percentile of 6 Hours Ahead hourly average net load forecast error. Non-Spin quantities during rest of the hours will be based on 75th to 95th percentile of 6 Hours Ahead (HA) hourly average net load forecast error to compute Non-Spin quantities. The percentile used will be based on risk of a net load up-ramp in these hours.
Lastly, NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2024 assessment for ERCOT shows a decrease in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2024 will change to 1,185 MW.
Note that, while the quantities of each AS are set based on an analysis of certain risks, these are not necessarily the only reasons why each AS is needed.

## Slide 3: Thoughts on IMM AS Methodology Recommendation
 | IMM Recommendation | ERCOT Comments
RRS | Remove the 2,800 MW floor on RRS. | Agree with this recommendation.
ECRS | Reduce the frequency recovery MW procurement for ECRS. | ERCOT is proposing to adjust the frequency recovery portion such that it (a) uses 2 years of historic information and cover 60% of historic net load and inertia conditions; and (b) accounts for Regulation requirement in the hour. These changes overall reduce the frequency recovery MW portion of ECRS quantity.
 | Use 10-minute ahead net load errors for ECRS methodology. | 30 Minute Ahead net load forecast errors reflect the magnitude uncertainty that ECRS would be relied upon to cover till resources providing offline Non-Spin are online and ready for dispatch. Offline Non-Spin resources can have a cold start time of upto 30min.
 | Reduce ECRS duration requirement back to one hour – requiring that resources providing ECRS be able to deploy for at least two hours effectively reduced energy storage resource participation by half. | While this is not directly related to AS Methodology, it is worth noting that, the BoD approved version of NPRR1186 keeps the duration requirement for ECRS from a qualification perspective but specifies that the minimum State-Of-Charge needed to provide ECRS will be set per a 1-hour requirement. This change may influence a change in ESR participation for ECRS.
Non-Spin | Change the non-spin 6-hour ahead error requirement to 3-hour ahead. | 6 Hour Ahead net load forecast errors reflect the magnitude uncertainty that Non-Spin would be relied upon to cover till offline resources can be committed, are online and ready for dispatch. 6 hours reflects lead times of typical resources that are offline and available for commitment on tighter days.

## Slide 4: Regulation Service Methodology
Regulation Service is reserved capacity that is deployed every 4 seconds to balance supply and demand and maintain frequency close to 60Hz between 5-minute SCED runs.
ERCOT is not proposing any changes to the methodology used to compute the minimum Regulation Service requirements in 2024.
  To better reflect the balancing needs from the hour, ERCOT has updated the Net Load variability calculation to include additional accounting based on accumulated Area Control Error (ACE).
The preliminary Regulation quantities for January 2024 through August 2024 in subsequent slides have been computed using current methodology (2022 and 2023 five-minute net load variability), updated Wind Adjustment tables and the updated Solar Adjustment tables.
Regulation

## Slide 5: 2024 Wind Adjustment Tables
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Chart: Reg-Up Adjustment per 1000 MW increase in Wind Installed Capacity
| Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec.
2023 Reg-Up Adj. | 1.3798 | 1.5039 | 1.8328 | 1.806 | 1.6997 | 1.3779 | 1.1206 | 1.1201 | 1.303 | 1.2479 | 1.2649 | 1.3286
2024 Reg-Up Adj. | 1.1913 | 1.0376 | 1.6649 | 1.3893 | 1.4639 | 1.2949 | 1.309 | 1.0183 | 0.91327 | 0.88836 | 0.9438 | 0.83143
Chart: Reg-Down Adjustment per 1000 MW increase in Wind Installed Capacity
| Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec.
2023 Reg Down Adj. | 1.1056 | 1.3234 | 1.7668 | 1.679 | 1.3874 | 0.99909 | 0.84149 | 0.92914 | 1.0592 | 1.0554 | 1.0593 | 1.2217
2024 Reg Down Adj. | 1.1913 | 1.0376 | 1.6649 | 1.3893 | 1.4639 | 1.2949 | 1.309 | 1.0183 | 0.91327 | 0.88836 | 0.9438 | 0.83143
Notes: Avg Reg Up adjustment for wind is 1.2MW
Avg Reg Down adjustment for wind is 1.2 MW

## Slide 6: 2024 Solar Adjustment Tables
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
 | Min (MW) | Max (MW) | Average (MW)
Reg Up | 0 | 18 | 7.8
Reg Down | 0 | 20 | 7.7

## Slide 7: Mechanisms to respond to Solar variability
The Solar adjustment tables were developed to project increases in variability expected by growth in the solar fleet. This has been part of the regulation methodology since 2021. This underlying study has been updated for 2024.
Improve GTBD i.e. the target that SCED uses to dispatch SCED Dispatchable Resources.
  In Real Time the parameters in GTBD can be changed to improve the accounting forecasted solar ramp as the solar fleet grows.
  The solar ramp that is currently used in GTBD is estimated using hourly solar forecasts. This gives a conservative estimate of variability within the hour. This can be toggled to use the intra-hour solar forecast. Making this change can which will make GTBD much more reactive in sensing weather variability.
    ERCOT has been actively engaged with its forecast vendors to develop forecasting methodologies that will improve 5-min solar ramp/variability forecasts.
In Real Time SCED can be executed manually (with or without an offset) if Regulation alone is not able to recover frequency.

## Slide 8: Hourly Average Regulation Comparison

## Slide 9: Regulation Comparison January

## Slide 10: Regulation Comparison April

## Slide 11: Regulation Comparison August

## Slide 12: Responsive Reserve Service (RRS) Methodology
Responsive Reserve Service (RRS) is reserved capacity that is procured to respond to low frequency events typically triggered by generating unit trips.
ERCOT is proposing one change in the methodology used to compute RRS requirements in 2024.
  ERCOT is proposing to remove the 2,800 MW floor that is applied during summer peak hours. A minimum of 2,300 MW of RRS will continue to be procured in all hours.
Responsive
  The additional 500 MW RRS during Summer peak helped in maintaining sufficient amount of Physical Responsive Capability (PRC) during these hours. The implementation of NPRR 989 that improved accounting of PRC from Energy Storage Resources (ESRs) and the recent implementation of ERCOT Contingency Reserve Service (ECRS) are helping in maintaining PRC.
NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2024 assessment for ERCOT shows a decrease in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2024 will change to 1,185 MW.
The preliminary RRS quantities for January 2024 through August 2024 in subsequent slides have been computed using 2022 and 2023 system inertia conditions and updated RRS table.
  The RRS table tracks RRS requirements for different inertia conditions. This table was updated in 2024 to use a minimum RRS-PFR limit of 1,185 MW.
No change in slides 20 to 25 since last presentation. August data has been included in Slide 22.
Notes: OY2022 IFRO – 412 MW/0.1 Hz | Limit 1,240 MW
OY2023 IFRO – 463 MW/0.1 Hz | Limit 1,390 MW
OY2024 IFRO – 395 MW/0.1 Hz | Limit 1,185 MW

## Slide 13: 2024 RRS Table
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS Curr IFRO (MW) | 3335 | 3287 | 3239 | 3195 | 3156 | 3079 | 3041 | 2991 | 2949 | 2871 | 2774 | 2705
**RRS Upd IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2960 | 2916 | 2880 | 2808 | 2716 | 2654
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290*** | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2651 | 2600 | 2562 | 2517 | 2466 | 2427 | 2381 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2606 | 2560 | 2529 | 2491 | 2444 | 2412 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,390 MW.
**RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,185 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. RRS requirement during these is based on the applicable floor.
Notes: RRS quantity for 2024 decrease between 2 MW (320 GW.s case) and 61 MW (150 GW.s case)

## Slide 14: Hourly Average RRS Comparison

## Slide 15: RRS Comparison February

## Slide 16: RRS Comparison March

## Slide 17: RRS Comparison July

## Slide 18: ERCOT Contingency Reserve Service (ECRS) Methodology
ECRS is reserved capacity that can respond in 10 minutes to recover frequency, cover forecast errors or ramps and replace deployed reserves.
ECRS requirements are computed as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support net load forecast errors during sustained net load ramps.
For 2024, ERCOT is considering to make the following changes
  Adjust the risk coverage during sunset hours to be at least 90th percentile
  Adjust the frequency recovery portion such that it (a) uses 2 years of historic information and cover 60% of historic net load and inertia conditions; and (b) adjust the quantity to account for Regulation requirement in the hour.
The preliminary ECRS quantities for January 2024 through August 2024 in subsequent slides have been computed using current methodology (2021, 2022 and 2023 Intra-Hour Net load and Net load Forecast, 2022 and 2023 system inertia conditions ) and updated Intra-hour Solar Over-Forecast Error Adjustment table.
  Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Notes: (b) change was to recognize the fact that during ECRS deployments that are triggered by unit trips, initially both Regulation and ECRS will be relied on to recover frequency and then ECRS will be used to recover deployed Regulation.

## Slide 19: Cold Start-up Time of OFFNS Resources in 2023
Cold Start time of units that were providing Non-Spin using OFFNS status was analyzed at 5-min resolution.
80th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
2 – Feb | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
3 – Mar | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
4 – Apr | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
5 – May | 18 min | 18 min | 18 min | 18 min | 24 min | 24 min
6 – Jun | 18 min | 18 min | 18 min | 30 min | 30 min | 30 min
7 – Jul | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
8 – Aug | 15 min | 18 min | 18 min | 30 min | 30 min | 18 min
Aug 17, 25, 30 | 18 min | 18 min | 30 min | 30 min | 30 min | 30 min
95th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
2 – Feb | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
3 – Mar | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
4 – Apr | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
5 – May | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
6 – Jun | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
7 – Jul | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
8 – Aug | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Aug 17, 25, 30 | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Notes: Decker Removed

## Slide 20: 2024 Intra-Hour Solar Adjustment Table
Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in 30-min ahead solar over forecast error per 1000 MW increase in installed solar capacity.
 | HE 1-2, 23-24 | HE 3-6 | HE 7-10 | HE 11-14 | HE 15-18 | HE 19-22
Jan | 0 | 0 | 0 | 21 | 20 | 0
Feb | 0 | 0 | 0 | 33 | 20 | 0
Mar | 0 | 0 | 0 | 33 | 73 | 0
Apr | 0 | 0 | 0 | 30 | 55 | 0
May | 0 | 0 | 0 | 59 | 96 | 26
Jun | 0 | 0 | 0 | 17 | 41 | 37
Jul | 0 | 0 | 0 | 23 | 23 | 8
Aug | 0 | 0 | 0 | 45 | 53 | 4
Sep | 0 | 0 | 0 | 64 | 56 | 0
Oct | 0 | 0 | 0 | 26 | 37 | 0
Nov | 0 | 0 | 0 | 1 | 4 | 0
Dec | 0 | 0 | 0 | 3 | 0 | 0

## Slide 21: Hourly Average ECRS Comparison

## Slide 22: ECRS Comparison Apr

## Slide 23: ECRS Comparison May

## Slide 24: ECRS Comparison August

## Slide 25: Non-Spinning Reserve Methodology
Non-Spin is reserved capacity that can be started in 30 minutes to cover forecast errors, ramps or forced outages and replace deployed reserves until additional resources can be committed.
ERCOT is proposing one change to the methodology used to compute the minimum Non-Spin requirements in 2024. Specifically,
  Non-Spin quantities for HE23 to HE02 in Winter and HE23 in to HE06 rest of the year will be computed using 68th percentile of 6 Hours Ahead hourly average net load forecast error.
  Non-Spin quantities during rest of the hours will be based on 75th to 95th percentile of 6 Hours Ahead (HA) hourly average net load forecast error to compute Non-Spin quantities. The percentile used will be based on risk of a net load up-ramp in these hours.
The preliminary Non-Spin quantities for January 2024 through August 2024 in subsequent slides have been computed using current methodology (2021, 2022 and 2023 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the updated Solar Over-Forecast Error Adjustment table.
  Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 26: 2023 RUCs by Startup Time

## Slide 27: 2024 Intra-day Outage Table
The Intra-day Outage table helps account for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 28: Wind Over-Forecast Error Adjustment Table 2024
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind capacity.
Max: 31 MW per 1000 MW additional Wind capacity
Mean: 25 MW per 1000 MW additional Wind capacity

## Slide 29: Solar Over-Forecast Error Adjustment Table 2024
Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Max: 48 MW per 1000 MW additional solar capacity
Mean: 13 MW per 1000 MW additional solar capacity
Mean (Day time): 20 MW per 1000 MW additional solar capacity

## Slide 30: Hourly Average Non-Spin Comparison

## Slide 31: Non-Spin Comparison January

## Slide 32: Non-Spin Comparison April

## Slide 33: Non-Spin Comparison August

## Slide 34: Summary
Below is a summary of the proposed changes to the methodology used for computing minimum AS quantities for 2024,
  ERCOT is not proposing any changes in the methodology used to compute Regulation Service.
  ERCOT is proposing changes in the methodologies used to compute Responsive Reserve Service (one change), ERCOT Contingency Reserve Service (three changes) and Non-Spinning Reserve Service (one change) requirements.
Spreadsheets that contain the preliminary quantities from Jan to Sep 2024 and a redline version of the AS Methodology document have been posted on today’s meeting page.
ERCOT is seeking endorsement on ERCOT’s proposed methodology for computing minimum AS quantities for 2024.