## Slide 1
November 2, 2023 ROS
Balancing Operations Planning Staff
Proposed 2024 Ancillary Service Methodology

## Slide 2: Introduction
ERCOT has reviewed the methodology to determine minimum Ancillary Service (AS) requirements and is proposing the following changes for 2024.
  No changes in the methodology used for computing Regulation Service.
    To better reflect the balancing needs from the hour, ERCOT has updated the Net Load variability calculation to include additional accounting based on accumulated Area Control Error (ACE).
  Remove the 2,800 MW RRS floor that is applied to summer peak hours for 2024. A Minimum 2,300 MW of RRS will apply to all hours.
2024 Methodology Review Timeline
September 20, 2023 – PDCWG (link)
September 22, 2023 – WMWG (link)
October 6, 2023 – WMWG (Proposed)
October 10, 2022 – PDCWG (Proposed)
October 19, 2023 – OWG (Proposed)
November 01, 2023 – WMS
November 02, 2023 – ROS
December 04, 2023 – TAC
December 19, 2023 – BoD
  Change methodology for ERCOT Contingency Reserve Service (ECRS) to (1) Adjust the risk coverage during sunset hours to be at least 90th percentile, (2) Adjust the frequency recovery portion such that it (2)(a) uses 2 years of historic information and cover 60% of historic net load and inertia conditions; and (2)(b) accounts for Regulation requirement in the hour.
  Change methodology for Non-Spinning Reserve Service (Non-Spin) quantities specifically for HE23 to HE02 in Winter and HE23 in to HE06 rest of the year to be computed using 68th percentile of 6 Hours Ahead hourly average net load forecast error. Non-Spin quantities during rest of the hours will be based on 75th to 95th percentile of 6 Hours Ahead (HA) hourly average net load forecast error to compute Non-Spin quantities. The percentile used will be based on risk of a net load up-ramp in these hours.
Lastly, NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2024 assessment for ERCOT shows a decrease in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2024 will change to 1,185 MW.
Note that, while the quantities of each AS are set based on an analysis of certain risks, these are not necessarily the only reasons why each AS is needed.

## Slide 3: Thoughts on IMM AS Methodology Recommendation
 | IMM Recommendation | ERCOT Comments
RRS | Remove the 2,800 MW floor on RRS. | Agree with this recommendation.
ECRS | Reduce the frequency recovery MW procurement for ECRS. | ERCOT is proposing to adjust the frequency recovery portion such that it (a) uses 2 years of historic information and cover 60% of historic net load and inertia conditions; and (b) accounts for Regulation requirement in the hour. These changes overall reduce the frequency recovery MW portion of ECRS quantity.
 | Use 10-minute ahead net load errors for ECRS methodology. | 30 Minute Ahead net load forecast errors reflect the magnitude uncertainty that ECRS would be relied upon to cover till resources providing offline Non-Spin are online and ready for dispatch. Offline Non-Spin resources can have a cold start time of upto 30min.
 | Reduce ECRS duration requirement back to one hour – requiring that resources providing ECRS be able to deploy for at least two hours effectively reduced energy storage resource participation by half. | While this is not directly related to AS Methodology, it is worth noting that, the BoD approved version of NPRR1186 keeps the duration requirement for ECRS from a qualification perspective but specifies that the minimum State-Of-Charge needed to provide ECRS will be set per a 1-hour requirement. This change may influence a change in ESR participation for ECRS.
Non-Spin | Change the non-spin 6-hour ahead error requirement to 3-hour ahead. | 6 Hour Ahead net load forecast errors reflect the magnitude uncertainty that Non-Spin would be relied upon to cover till offline resources can be committed, are online and ready for dispatch. 6 hours reflects lead times of typical resources that are offline and available for commitment on tighter days.

## Slide 4: Hourly Average Regulation Comparison

## Slide 5: Hourly Average RRS Comparison

## Slide 6: Hourly Average ECRS Comparison

## Slide 7: Hourly Average Non-Spin Comparison (REVISED)

## Slide 8: Summary
Below is a summary of the proposed changes to the methodology used for computing minimum AS quantities for 2024,
  ERCOT is not proposing any changes in the methodology used to compute Regulation Service.
  ERCOT is proposing changes in the methodologies used to compute Responsive Reserve Service (one change), ERCOT Contingency Reserve Service (three changes) and Non-Spinning Reserve Service (one change) requirements.
Spreadsheets that contain the preliminary quantities from Jan to Sep 2024 and a redline version of the AS Methodology document have been posted on today’s meeting page.
ERCOT is seeking endorsement on ERCOT’s proposed methodology for computing minimum AS quantities for 2024.

## Slide 9
Appendix

## Slide 10: Cold Start-up Time of OFFNS Resources in 2023
Cold Start time of units that were providing Non-Spin using OFFNS status was analyzed at 5-min resolution.
80th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
2 – Feb | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
3 – Mar | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
4 – Apr | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
5 – May | 18 min | 18 min | 18 min | 18 min | 24 min | 24 min
6 – Jun | 18 min | 18 min | 18 min | 30 min | 30 min | 30 min
7 – Jul | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
8 – Aug | 15 min | 18 min | 18 min | 30 min | 30 min | 18 min
Aug 17, 25, 30 | 18 min | 18 min | 30 min | 30 min | 30 min | 30 min
95th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
2 – Feb | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
3 – Mar | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
4 – Apr | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
5 – May | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
6 – Jun | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
7 – Jul | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
8 – Aug | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Aug 17, 25, 30 | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Notes: Decker Removed

## Slide 11: 2023 RUCs by Startup Time