## Slide 1: Vestas Perspective on NOGRR-245
Miguel A. Cova Acosta
Power Plant Solutions

## Slide 2: Overview
IEEE – 2800 US Context
IEEE 2800
Guidance on test and verification procedures for IBR

## Slide 3: Overview
IEEE 2800
Guidance on test and verification procedures for IBR
NOGRR - 245
NOGRR-245 represents a “short” section of IEEE-2800 requirements based on ERCOT interpretation.
IEEE 2800
ERCOT Implementation and interpretation of requirements
NOGRR-245

## Slide 4: Overview
IEEE 2800
MISO Implementation and interpretation of requirements
IEEE 2800
IEEE 2800
ERCOT Implementation and interpretation of requirements
NOGRR-245
IEEE 2800
NYISO Implementation and interpretation of requirements
IEEE – 2800 US Future?

## Slide 5: IEEE 2800/ NOGR-245
Requirement Interpolation – PoI vs WTG
The following criteria are not defined at this stage by ERCOT / IEEE:
Evaluation Criteria
Operational Points
Loading Factor
Project specific control tuning
Project Specific Conditions that will affect the compliance outcome:
Grid Stiffness
Single Line Diagram/Reactive Compensation devices
PPC Configuration (Control strategy)
Nearby IBR plants
Others
Turbines
Project Specific Power Plant
Grid
OEM - RFI
NOGRR-245 / IEEE 2800
PoI
Isn't straightforward to translate requirements from PoI to WTG_

## Slide 6: Vestas Presence in ERCOT
Turbine Variants Installed
Type I - Direct-Connected Induction (Asynchronous) Generator: These are fixed-speed turbines with stall-regulated blades. They're directly connected to the grid and often include capacitors for reactive power compensation. They're robust but less efficient in energy capture.
Type II - Wound-Rotor Induction Generator with External Resistance Control: These turbines have a variable slip enabled by external resistors and pitch-regulated blades, allowing for a wider speed range.
Type III - Doubly-Fed Asynchronous Generator (DFAG): Also known as DFIG, these have a wound rotor induction generator with a power converter for vector control of the rotor circuit current, enhancing operational speed range and efficiency.
Type IV - Variable Speed Turbine with Full-Rated Power Converter: These employ a full-rated power converter for decoupling generator dynamics from the grid, enabling independent real and reactive power control, with either synchronous or induction generators.
Chart: Vestas Installed Capacity - ERCOT
| Type III | Type IV | Type I or II | Type III - Legacy | Type IV - Legacy
 | 4674.1 | 2885.65 | 209.28 | 459.07 | 300.3

## Slide 7: Vestas assessment of Installed fleet in ERCOT
 | Type 3 | Type 4 | Discontinued Type 3 & 4 | Type 1 and 2
2.6.2.1 (1) Frequency Ride Through curve |  |  |  | 
2.6.2.1(3) Protection System Coordination |  |  |  | 
2.6.2.1(3) Rate of Change of Frequency (RoCoF) |  |  |  | 
2.6.2.1 (4) Current injection settings |  |  |  | 
2.6.2.1 (5) Controls system coordination |  |  |  | 
2.6.2 (3) Filtered quantities/ time delay use |  |  |  | 
2.9.1.2 (1) Table A VRT Curves |  |  |  | 
2.9.1.2 (3) Protection System Coordination |  |  |  | 
2.9.1.2 (4) Current injection settings |  |  |  | 
2.9.1.2 (5) Controls system coordination |  |  |  | 
2.9.1.2 (6) Filtered quantities/ time delay use |  |  |  | 
2.9.1.2 (7) Multiple excursion FRT |  |  |  | 
2.9.1.2 (8) Phase Angle Jump |  |  |  | 
2.9.1.1 (1) Table A and C VRT Curves* |  |  |  | 
Pass
Not Assessed Fail
NOGRR-245
Vestas's evaluation of the requirements at turbine terminals indicates that the capabilities of most of our current installed fleet meets the specified requirements, as detailed in the accompanying table with no hardware changes required.

## Slide 8: NOGRR-245 – Voltage Requirement
Global Comparison
Chart: UVRT Global Profiles
| 1E-4 | 0.15 | 1.75 | 99999
AME-US-ONS-TSO-ERCOT Un [p.u.] | 0 | 0 | 0.9 | 0.9
AME-US-ALL-ALL-IEEE_PES-With_auxiliary_equip_limitation Un [p.u.] | 0.1 | 0.1 | 0.25 | 0.25 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9
APC-AU-ONS-TSO-AEMO-AAS_>100kV Un [p.u.] | 0 | 0 | 0.7 | 0.7 | 0.8 | 0.8 | 0.9 | 0.9
MED-ES-ONS-TSO-Peninsular-≥110kV Un [p.u.] | 0 | 0 | 0.85 | 0.85 | 0.9 | 0.9
MED-IT-ALL-TSO-220kV Un [p.u.] | 0 | 0 | 0.85 | 0.85 | 0.9 | 0.9
MED-IT-ALL-TSO-380kV Un [p.u.] | 0 | 0 | 0.85 | 0.85 | 0.9 | 0.9
NCE-DE-ONS-DSO-MV<110kV-asym Un [p.u.] | 0.15 | 0.15 | 0.75 | 0.85 | 0.85 | 0.9 | 0.9
NCE-DE-ONS-TSO-HV=110kV-sym Un [p.u.] | 0 | 0 | 0.85 | 0.85 | 0.8727 | 0.8727
NCE-DE-ONS-TSO-HV=110kV-asym Un [p.u.] | 0 | 0 | 0.75 | 0.85 | 0.85 | 0.8727 | 0.8727
NCE-DE-ALL-TSO-EHV>110kV-sym Un [p.u.] | 0 | 0 | 0.85 | 0.85 | 0.9 | 0.9
NCE-DK-ALL-TSO-Nordics SynArea-Type_D_≥110kV Un [p.u.] | 0 | 0 | 0.9 | 0.9

## Slide 9: NOGRR-245 – Frequency Requirement
Global Comparison
Chart: Frequency range
| 0.01 | 299 | 299 | 540 | 540 | 9999 | 9999 | 540 | 540 | 299 | 299 | 0.01
AME-US-ONS-TSO-ERCOT-draft | 0.95 | 0.95 | 0.97333 | 0.97333 | 0.98 | 0.98 | 1.02 | 1.02 | 1.0267 | 1.0267 | 1.03 | 1.03
APC-AU-ONS-TSO-WP-AAS | 0.94 | 0.94 | 0.95 | 0.95 | 0.98 | 0.98 | 1.02 | 1.02 | 1.03 | 1.03 | 1.04 | 1.04 | 1.05 | 1.05
APC-AU-ONS-TSO-WP-MAS | 0.94 | 0.94 | 0.95 | 0.95 | 0.96 | 0.96 | 0.98 | 0.98 | 1.02 | 1.02 | 1.04 | 1.04
APC-NZ-ONS-ALL-North | 0.94 | 0.94 | 0.942 | 0.942 | 0.946 | 0.946 | 0.95 | 0.95 | 0.95 | 0.95
EUR-GB-ALL-ALL | 0.94 | 0.94 | 0.95 | 0.95 | 0.98 | 0.98 | 1.02 | 1.02 | 1.03 | 1.03 | 1.04 | 1.04
LAT-BR-ONS-ALL | 0.93333 | 0.93333 | 0.975 | 0.975 | 1.0417 | 1.0417 | 1.05 | 1.05
NCE-UK-ALL-TSO | 0.94 | 0.94 | 0.95 | 0.95 | 0.97 | 0.97 | 0.98 | 0.98 | 1.02 | 1.02 | 1.03 | 1.03 | 1.04 | 1.04

## Slide 10: Plant Lifecycle
GI Studies
Mature Models
GI Studies
Plant Connection
PreliminaryModels
Compliant?
Compliant?
Due
Diligence
Commissioning
Plant Lifecycle
Plant is recurrently reconfigured to mitigate potential grid connection issues
Models are updated based on bug fixes or new features for real product
Constant monitoring of performance and usability for Grid Code Compliance
New Project
Beginning of model cycle release for a new potential sales project
Operational Project
Ending of lifecycle when project is energized and delivering full power to grid
Updated Models
Updated Models
Bug Fixes
Bug Fixes
Features
Active and Reactive Current Profile
LVRT Recovery timings
Control Bandwidths
PLL PI Control Constants
Reactive Controller Constants
Negative Sequence Support
Grid Harmonic Damping
Post Fault Support

## Slide 11: Multiple FRT
Power Recovery for Weak Grid Conditions
Voltage Stability
Multiple FRT Requirement
50% More Energy Dissipated in the Chopper for same fault
Strong Grid with 10pu/s recovery of Active Power
Weak Grid with 2pu/s recovery of Active Power
Multiple Fault Ride-Through (FRT) is essential for maintaining grid stability. However, requirements should consider exemptions for energy dissipation, depending on the specific configuration of the project.

## Slide 12: Phase Jump
PLL Tuning for Weak Grid Conditions
Control Stability
Phase Jump Requirement
Phase Jump Ride Through is beneficial for maintaining grid stability. However, requirements should consider exemptions for site specific PLL tuning to maintain control stability under very weak grid conditions.

## Slide 13: NOGRR-245 – Full Picture
Known
LVRT Requirements
OVRT Requirements
Multiple FRT
Phase Jump
ROCOF Requirements
Unknown
Compliance Evaluation and Evidence
Modeling vs HiL vs Field Test vs Plant Commissioning Operational Scenarios
Tolerances
Type Tests
Exemption Process
13
NOGRR-245

## Slide 14: Suggestions and Reflections
Wrap up
Will each Independent System Operator (ISO) interpret the IEEE-2800 standard on an individual basis, potentially resulting in multiple variants of 'IEEE-2800' within the United States?
Do ISOs have a definitive understanding of the evidence required by Generation Owners (GO) and Original Equipment Manufacturers (OEM) to demonstrate compliance with the IEEE-2800 requirements as of today?
Could site-specific parameters, which are designed to enhance the grid's stability, supersede NOGRR-245 or the IEEE-2800 standards?
…
Vestas requires clarification on the test conditions and deliverables for evaluating various requested features, such as attestations, simulation reports, and plant or turbine-level simulations.
While Vestas recognizes the importance of NOGRR-245 within the industry and its alignment with IEEE 2800 standards. However, its verification processes should also be in accordance with IEEE 2800.2.

## Slide 15: Thank you