## Slide 1
West Texas Synchronous Condenser Regional Planning Group Project
Sun Wook Kang
Manager, Grid Planning
Technical Advisory Committee Meeting
December 4, 2023

## Slide 2: Overview
  These are Tier 1 projects with a combined estimated cost of $ 892.2 Million
  Reduce the reliability risk and strengthen the West Texas system
WETT, LCRA TSC, and Oncor each submitted synchronous condenser projects for Regional Planning Group (RPG) review in September 2023

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
Inverter-Based Resources (IBRs) in West Texas have experienced rapid and continued growth. The total capacity of IBRs in West Texas is projected to surpass roughly 42 GW by end of 2025
Significant prevalence of IBRs coupled with the absence of conventional synchronous generation resources has further weaken the system and increased the likelihood of potential instability issues (e.g., Odessa events)
The purpose of the project is to reduce the reliability risk and strengthen the West Texas system

## Slide 5: Comparison of Project Options
Enhancing system resilience and strength in the West Texas region involves exploring options like incorporating conventional generators, synchronous condensers, and other technologies such as STATCOMs and grid-forming inverters
ERCOT considered adding synchronous condensers in the West Texas region as the only transmission upgrade option because the installation of synchronous condensers can provide the necessary characteristics for supporting the reliable operation of a system with a high penetration of IBRs

## Slide 6: West Texas Synchronous Condensers: Results and Benefits
Significant improvement in system responses for critical faults even under stressed system conditions in West Texas region:
  Average enhancement of 11% in the system strength (voltage stiffness, measured in the West Texas short circuit current level)
  Average reduction of 21% in the number of 345-kV and 138-kV buses and 22% in IBRs that encounter severe voltage dips (less than 0.85 p.u.) during major transmission faults in the West Texas region
Potential enhancements in the stability and GTCs within the West Texas region
  The McCamey GTC limit is expected to be improved by an average of 15% with the potential synchronous condensers
  No significant impact on the West Texas GTC limit
The six synchronous condensers would improve the reliability and resilience of the existing West Texas system and minimize unexpected events in real time
Adding more synchronous condensers (more than the proposed six) showed marginal improvement

## Slide 7: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted an SSO screening for the potential synchronous condensers. The results of the topology check indicated that all the synchronous condenser locations except at the Reiter 345-kV substation are considered to be potentially vulnerable to SSO. Therefore, a detailed SSO assessment is recommended, and the affected TSPs shall coordinate with ERCOT to perform and complete a detailed SSO assessment and provide any SSO Mitigation, if required, prior to energization of synchronous condensers

## Slide 8: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
No congestion analysis was conducted because synchronous condenser is the sole transmission option and a reactive support device.
ERCOT concluded that
  no potential future generation were found which may impact the project need
  the load scaling did not have a material impact on the project need

## Slide 9: ERCOT Recommendation:
Based on the review, ERCOT will recommend the Board endorse synchronous condenser installations at six 345-kV substations: Cottonwood, Bearkat, Tonkawa, Long Draw, Reiter, and Bakersfield to reduce the reliability risk and strengthen the West Texas system
The targeted in-service date for the project (based on the information from TSPs) is between May - October 2027
Estimated Capital Cost: $892.2 Million

## Slide 10: ERCOT Recommendation:
ERCOT recommends six synchronous condensers at the following 345 kV substations; Cottonwood, Tonkawa, Long Draw, Bearkat, Reiter, and Bakersfield
  Approximately 350 MVAr capacity at each location
  Around 3,600 Ampere (A) of three-phase fault current contribution to the 345-kV point of interconnection (POI)
  A combined total inertia of 2,000 MW-seconds (MW-s) or above at each location, incorporating synchronous condenser with flywheel for frequency support