## Slide 1
Review of Potential Real-Time Market Price Correction for October 22, 2023 Due to a Failure to Process Market Submissions
David Maggio
Principal, Market Design & Analytics
Technical Advisory Committee (TAC)
December 4, 2023

## Slide 2: Background
On October 22, 2023, ERCOT experienced market submission failures that impacted market submissions from the Market Management System (MMS) user interface and Application Programming Interface (API). This issue affected submissions to both the Real-Time Market (RTM) as well as the Day-Ahead Market (DAM).
  Security-Constrained Economic Dispatch (SCED) was not able to read Three Part Offers (TPOs) between 12:15 PM – 12:54 PM and Current Operating Plans (COPs) between 1:00 PM – 1:09 PM, resulting is SCED failing to produce valid prices during these windows. This issue initially started at 6:36 AM, however SCED was able to continue using existing offer submissions until 12:15 PM.
  The DAM deadlines were extended with results being published at 5:35 PM.
  Additional details regarding this issue were presented to the Wholesale Market Subcommittee (WMS) on November 1, 2023.
Market Notice M-B102423-01 was issued on October 24, 2023, notifying the market of the issue and ERCOT’s intent, upon completion of impact analysis, to seek ERCOT Board of Directors (Board) approval for price correction as specified by ERCOT Protocol Section 6.3(7)(b).
Market Notice M-B102423-02 was issued on November 3, 2023, notifying the market that files containing price correction data have been posted to the TAC meeting page for December 4, 2023.

## Slide 3: Timeline for SCED
12:15 PM – 12:54 PM : SCED was unable to process TPOs, resulting in proxy Energy Offer Curves (EOCs) being created for Resources. The EOCs were created in accordance with paragraph (4) of ERCOT Protocol Section 6.5.7.3.
  This drove the RTM System Lambda to ~$4,992/MWh for this entire window of time. System Lambda was $23.54/MWh for the SCED execution at 12:10 PM.
12:55 PM – 12:56 PM : SCED was able to process TPOs, resulting in valid SCED runs. In accordance with paragraph (2) of Protocol Section 6.5.9.2, a 15-minute price hold starts from the first good SCED run (12:55 PM) following resolution of the failure. The prices used in the hold are required to be from the last good SCED run before the issue began (12:10 PM)
1:00 PM – 1:05 PM : SCED failed to process COPs, resulting in additional SCED failure.
1:09 PM : SCED was able to process COPs and produce valid results. The 15-minute hold period for SCED failure resets, beginning at 1:09 PM and ending at 1:24 PM.
1:25 PM : 15-minute hold ends and current SCED results were published to the market.
  System Lambda was $23.29/MWh for the SCED execution at 1:25 PM.

## Slide 4: Settlements Impact Analysis
ERCOT Protocols Section 6.3(7)(b) requires that the absolute value impact to any single Counter-Party (CP) meet one of the following two criteria before seeking approval from the Board.
  2% and also greater than $20,000; or
  20% and also greater than $2,000.
With the large change in the Real-Time System Lambda, several CPs met these criteria.
Largest Absolute Value Impact to a CP | Largest Absolute Percent Impact to a CP
$8,414,409.32 | 650.63%
CPs meeting (i) | CPs meeting (ii) | CPs meeting both Criteria
141 | 172 | 140
Change in Statement Charges Due to ERCOT | Largest Absolute Percent Impact to a CP
$(62,266,419.44) | 79.14%

## Slide 5: Next Steps
ERCOT intends to seek an approval of correction to RTM prices for Operating Day October 22, 2023, for the impacted intervals, at the Reliability and Market Committee on December 18, 2023, and the ERCOT Board meeting on December 19, 2023.