## Slide 1
Silverleaf and Cowpen 345/138-kV Stations Regional Planning Group Project
Robert Golen
Manager, Regional Planning
Technical Advisory Committee Meeting
ERCOT Public
December 4, 2023

## Slide 2: Overview
TNMP submitted the Silverleaf and Cowpen 345/138-kV Stations Project for Regional Planning Group (RPG) review in May 2023
  This is a Tier 1 project that was estimated to cost $299.0 million
  Addresses the reliability need in the Reeves and Ward Counties in the Far West weather zone

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review indicated reliability planning criteria violations
System improvement is needed to meet reliability planning criteria

## Slide 5: Comparison of Project Options
ERCOT analyzed four options and short-listed two options
Among the short-listed two options, Option 1 improves long-term load serving capability, and operational flexibility
Option 1 is the preferred option
* Cost estimates were provided by Transmission Service Providers (TSPs)

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 1 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 1 did not cause any new congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse Option 1 to address the reliability need in the Reeves and Ward Counties in the Far West weather zone
TSP expects to implement the upgrades by June 2027
Estimated Capital Cost: $273.1 Million
ERCOT will recommend that the ERCOT Board designate Option 1 as critical to the reliability of the ERCOT System pursuant to PUCT Substantive Rule 25.101(b)(3)(D)

## Slide 9: ERCOT Recommendation: Option 1
Construct a new 345-kV New Substation 1 near the existing Cedarvale station, by cutting into the planned North McCamey – Sand Lake 345-kV double-circuit line
Construct a new 345/138-kV Silverleaf station near New Substation 1, with three 668/750-MVA transformers, connecting to New Substation 1 via three 1793-MVA 345-kV tie lines
Loop the existing Cedarvale – Pecos 138-kV line #1 and #2, and Cedarvale – Bone Springs 138-kV line into the new Silverleaf station, will require approximately 4.4 miles of new Rights of Way (ROW)

## Slide 10: ERCOT Recommendation: Option 1 (Continued)
Construct a new 345-kV New Substation 2, ~ 13 miles away from the existing Sand Lake station, by cutting into the existing Sand Lake – Solstice 345-kV double-circuit line
Construct a new 345/138-kV Cowpen station near New Substation 2, with two 668/750-MVA transformers, connecting to New Substation 2 via two 1793-MVA 345-kV tie lines
Loop the existing IH20 – Salt Draw 138-kV line and Birds of Prey Tap – Harpoon Tap 138-kV line into the new Cowpen station, will require approximately 14.2 miles of new ROW

## Slide 11: Option 1