## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS
Vice Chair: Vacant
ROS
December 7th, 2023

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs and IMFR
    0 FME in the month of October
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 11/15/2023
  2024 Leadership PDCWG
  ERCOT Analysis of Disturbances/Frequency Events
  ERCOT Frequency Control Metrics and Regulation Reports
  TRE Report

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 463 MW/0.1 Hz
IMFR Performance currently
1298.68 MW/0.1HZ

## Slide 6
Questions?

## Slide 7: Frequency Control Report
October 2023

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency
Notes: 14.60 mHz on avg for October 2023

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy
Notes: 35,628,256 MWh

## Slide 13: ERCOT Total Energy from Wind Generation
Notes:   8,770,987 MWH

## Slide 14: ERCOT % Energy from Wind Generation
Notes: 24.62%
of total energy was provided by wind generation

## Slide 15: ERCOT Total Energy from Solar Generation
Notes: 2,592,963 MWh

## Slide 16: ERCOT % Energy from Solar Generation
Notes: 7.28% of total
energy was provided by solar generation, which is highest solar penetration level so far.

## Slide 17: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia = 183,022 MW*s on 10/18/2023
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 227,814 MW*s
Max: 284,485 MW*s on October 5th
Min: 183,022 MW*s on October 18th

## Slide 18: ERCOT Inertia Trend
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.