## Slide 1
NOGRR 245
TAC
Stephen Solis – Principal, System Operations Improvement
December 4th, 2023

## Slide 2: Overview
Multiple events have occurred where Inverter Based Resources (IBRs) failed to ride-through
  Magnitudes have increased with more IBRs on ERCOT System
As proposed by ERCOT, Nodal Operating Guide Revision Request (NOGRR 245) would enhance clarity and specificity of IBR ride through requirements and align with most relevant parts of IEEE 2800-2022 and NERC Reliability Guidelines
ERCOT received over 50 public comments and multiple separate feedback meetings on NOGRR 245
FERC issued Order 901 directing NERC to address same risks that NOGRR245 addresses
ERCOT issued RFIs to OEMs and REs on ability to comply with ERCOT proposal and ROS-recommended versions of NOGRR
Presentation summarizes RFI results and proposed changes based on the information obtained through this RFI

## Slide 3: FERC Order 901 Key Takeaways
NERC must “develop new or modified Reliability Standards that require registered IBR generator owners and operators to use appropriate settings…to ride through frequency and voltage system disturbances….” (para 190)
  Must “permit IBR tripping only to protect …equipment in scenarios similar to when synchronous generation resources use tripping as protection from internal faults”
  Must “require registered IBRs to continue to inject current and perform frequency support during a [BPS] disturbance
  Must address FRT, VRT and “post-disturbance ramp rates, phase lock loop synchronization, and other known causes of IBR tripping or momentary cessation”
Must apply to new and existing IBRs (para 190)
NERC should determine whether existing IBRs that cannot be modified through software updates may receive limited exemption (para 193)
  Subset of existing IBRs unable to modify coordinated protection/control settings to meet VRT requirements w/o physical equipment modification until IBRs are replaced or upgraded (para 193)
  NERC must develop Reliability Standards requiring planners/operators to mitigate the reliability impacts resulting from such an exemption. (para 199)
Directed new standards for generator owners to install disturbance monitoring equipment and provide data to planners and operators (NOGRR 255) (para 85)
FERC comments indicate urgency based on future of IBR penetration levels (Comm Danly)
  FERC contemplated exemptions assuming time until levels reach a critical risk threshold that ERCOT is already encountering today

## Slide 4: RFI Results
OEM RFI and part of RE RFI asked if technically feasible to comply w/ requirements in ERCOT recommended language from 8/18/23 comments
Some RE responses may reflect late info from OEMs
Remainder of RE RFI asked if it was commercially reasonable to comply with requirements as captured in the ROS approved language from the September 14, 2023.
VRT curves are more stringent in ROS approved language
Key Takeaway: RFI results highlight most challenged requirements from OEM perspective and differences between OEM capabilities and RE assessments. ROS approved language would require much higher levels of exemptions and residual system risk.

## Slide 5: ERCOT Proposed Changes to NOGRR 245
Based on RFI results, ERCOT will be proposing revised comments (based on its 8/18/23 comments):
Allow exceptions for documented technical limitations to FRT and VRT curves for IBRs (and Type 1 and 2 WGRs) w/ SGIAs before 1/16/14
  Exceptions will be given based on ERCOT sole determination
  Must meet existing requirements, and substantially meet new requirements, with each plant's documented technical limitation level becoming the requirement for that plant
  Must maximize capability through use of parameterization, software upgrades and technically feasible upgrade kits (but major repowers/retrofits not required)
  Technical limitations must be accurately represented in all provided models
  ERCOT may apply operational restrictions for performance failures to the documented limitation that pose significant reliability risk that cannot be mitigated in reasonable time (e.g., 90 days)
  Must meet latest requirements upon reinvestment (e.g., repower/retrofit requiring GIM process)
Remove specificity and clarity requirements for legacy IBRs for RoCoF and Phase Angle Jump
  Return expectations around RoCoF and Phase Angle Jump requirements to status quo
    If voltage and frequency are within “no trip” zones, IBR must ride through
Modify multiple excursion requirement for legacy IBRs to maximize capability if they use a counter or can adjust parameters to ensure riding through normal TSP reclose schemes vs current alignment with IEEE 2800

## Slide 6: ERCOT Proposed Changes to NOGRR 245
Allow documented technical limitations to IEEE 2800 synchronized before 1/1/26
  Exceptions will be given based on ERCOT sole determination
  Must fully meet legacy requirements
  Must substantially meet preferred requirements with each plant’s documented technical limitations being the new specificity requirements for that plant.
  Must maximize capability through the use of parameterization, software upgrades and technically feasible upgrade kits (with allowed implementation timeframes)
  Technical limitation must be accurately represented in all provided models
  ERCOT may apply operational restrictions for performance failures to the documented limitation that pose significant reliability risk that cannot be mitigated in reasonable time (e.g., 90 days)
  Must meet latest requirements upon reinvestment (e.g., repower/retrofit requiring GIM process)
Revise operational restrictions expectations for performance failures that pose significant reliability risk and cannot be implemented in reasonable time
Other minor clarifications/exceptions
  Handling of active current reductions during fault
  SGIA modifications for load-only additions would not trigger requirement to meet IEEE 2800 requirements if IBR does not need physical modifications to meet other requirements
  Allow multiple excursion trips if energy dissipated exceeds certain thresholds
  Clarify RoCoF and Phase Angle Jump requirements to address differences between fault and non-fault timeframes

## Slide 7: Reliability Impact of ERCOT proposed exceptions
Can move forward w/ OEM-identified parameterization and upgrade kits available from OEMs but that owners are waiting to authorize and procure
"Technical Infeasibility" exemptions would not require consideration of very expensive upgrades such as repowers or converter replacements"
Allows IBRs w/ SGIA beyond 6/1/23 with challenges to immediately meeting IEEE 2800 requirements to have a feasible path forward
Reliability risk continues due to IBRs w/ exemptions
Modeled limitations may impact stability limits
  Generic Transmission Constraints and its limits (GTLs) may be updated or added as needed.
  Impact of exceeding some GTLs may qualify them as an IROL
  Additional transmission projects may need to be implemented
Some newly modeled limitations and repeated performance failures may require new credible contingencies (e.g., combined transmission and generator contingency) to be considered in both operations and planning
  May result in additional transmission congestion
  May create new voltage, cascading or instability conditions
Key Takeaway: Proposed exemptions should help faster adoption of available improvements and IEEE 2800 but at expense of continued reliability risk and its associated impacts

## Slide 8: Additional assumptions
IBR performance requirements are one part of overall solution to address risk
  IBR performance requirements (NOGRR 245) w/ appropriate enforcement
  System strength upgrades (e.g., 6 new synchronous condensers)
  Grid Forming capability adoption
  Modeling and testing improvements
  Disturbance monitoring equipment installs (NOGRR 255)
  Potential planning criteria adjustments
To offset risk, exemptions must be accompanied by:
  Clear expectations around potential operating restrictions for failures
  Models and contingencies accurately reflecting limitations
  Proper active and reactive power controls coordination
The actions required to offset the risk could lead to additional operation and planning impact such as congestion and system improvements.
Key Takeaway: Proposal assumes willingness to take on more reliability risk, that other risk offset activities will be adopted, and that other system cost impacts are acceptable to impacted entities.

## Slide 9: Proposed timeline for NOGRR 245 (i.e. Next steps)
Dec 4, 2023
TAC
Table
Jan 24, 2024
TAC
Vote
Feb 27, 2024
ERCOT Board
Vote
April 11, 2024
PUCT
Vote

## Slide 10
Questions?

## Slide 11
Appendix: RFI Results detailed comparison

## Slide 12: Frequency Ride Through Curve
8,200 of 8,797 MW are GE 1.x platform
  GE clarifies that can meet for WTGs sold > 2014
  GE is NOT planning to meet requirements by creating a retrofit OR repower solution for the 1.x platforms
Highlights more risk with the ROS approved version (16,261 MW) for commercially reasonable vs the ERCOT recommended version (9,891 MW) for technically feasible since curves are same
FERC Order 901 did not consider exemptions for frequency ride-through
Key Takeaway: Frequency ride through curves should be achievable for most legacy IBRs. Parameterization, software changes, and minor upgrade kits should be implemented. Limited, specific exemptions may be acceptable for infeasible or very expensive, major upgrades/retrofits.

## Slide 13: Frequency Protection System Coordination
OEM RFI responses show high percentage able to comply
Highlights more risk with the ROS approved version (16,557 MW) for commercially reasonable vs the ERCOT recommended version (8,903 MW) for technically feasible since same requirements
Most “No” responses from REs are due to insufficient information rather than a known limitation
Key Takeaway: Protection system coordination is critical and should be achievable with proper parameterization and software changes. ERCOT proposes to maintain requirements consistent with its August 18, 2023 comments.

## Slide 14: Rate of Change of Frequency (RoCoF)
A majority of “no” responses are due to lack of prior testing and verification rather than known limitation
Most IBRs do not actively monitor Rate of Change of Frequency (RoCoF)
Most “No” responses from OEMs and REs are due to insufficient information rather than a known limitation
Several recent technical discussions at various industry forums, including IBRWG highlight that IBRs should not trip off due for any level of RoCoF during fault conditions which is the current status quo for frequency ride-through requirements
Key Takeaway: Technical feasibility for legacy IBRs reflects challenges. ERCOT proposes to remove currently proposed language addressing RoCoF for legacy IBRs. ERCOT will maintain current requirements that when POIB is within frequency ride-through no trip zone, IBRs are not allowed to trip off or reduce output due to RoCoF.

## Slide 15: Frequency Current Injection settings
OEM RFI responses show high percentage able to comply
Highlights more risk with the ROS approved version (14,115 MW) for commercially reasonable vs the ERCOT recommended version (5,925 MW) for technically feasible since same requirements
Most “No” responses from REs are due to insufficient information rather than a known limitation
Key Takeaway: Frequency current injection settings should be achievable with proper parameterization and software changes for most legacy IBRs. ERCOT proposes to maintain requirements consistent with its August 18, 2023 comments.

## Slide 16: Frequency Controls System Coordination
OEM RFI responses show high percentage able to comply.
Highlights more risk with the ROS approved version (13,500 MW) for commercially reasonable vs the ERCOT recommended version (6,016 MW) for technically feasible since same requirements
Most “No” responses from REs are due to insufficient information rather than a known limitation
Key Takeaway: Frequency controls coordination is critical and should be achievable with proper parameterization and software changes. ERCOT proposes to maintain requirements consistent with its August 18, 2023 comments.

## Slide 17: Frequency Filtered quantities/time delay use
OEM RFI responses show high percentage able to comply.
Highlights more risk with the ROS approved version (15,013 MW) for commercially reasonable vs the ERCOT recommended version (6,977 MW) for technically feasible since same requirements
Most “No” responses from REs are due to insufficient information rather than a known limitation
Key Takeaway: Using filtered voltage measurements and using a time delay for any frequency trip settings should be achievable with proper parameterization and software changes for most legacy IBRs. ERCOT proposes to maintain requirements consistent with its August 18, 2023 comments.

## Slide 18: Voltage Ride Through (VRT) Curves
8,200 of 9,077 MW are GE 1.x platform
  GE clarifies that can meet for WTGs sold > 2014
  GE is NOT planning to meet requirements by creating a retrofit OR repower solution for the 1.x platforms
Highlights more risk with the ROS approved version (30,963 MW) for commercially reasonable with more stringent VRT curves vs the ERCOT recommended version (15,394 MW) for technically feasible with current VRT curves
Table C VRT curves in ROS approved version would be very challenged for legacy IBRs
FERC Order 901 does consider limited and documented exemptions for older IBRs who cannot meet VRT requirements until replaced
Key Takeaway: Voltage ride through curves should be achievable for most legacy IBRs. Parameterization, software changes, and minor upgrade kits should be implemented. Limited, specific exemptions may be acceptable for infeasible or very expensive, major upgrades/retrofits.

## Slide 19: Voltage Protection System Coordination
OEM RFI responses show high percentage able to comply
Highlights more risk with the ROS approved version (20,867 MW) for commercially reasonable vs the ERCOT recommended version (13,303 MW) for technically feasible since same requirements
Most “No” responses from REs are due to insufficient information rather than a known limitation
Key Takeaway: Protection system coordination is critical and should be achievable with proper parameterization and software changes. ERCOT proposes to maintain requirements consistent with its August 18, 2023 comments.

## Slide 20: Voltage Current Injection settings
OEM RFI responses show high percentage able to comply.
ERCOT in conversation with one OEM who detailed 3,000 MW of capacity that would potentially be non-compliant with current VRT curves.
Highlights more risk with the ROS approved version (22,443 MW) for commercially reasonable vs the ERCOT recommended version (13,999 MW) for technically feasible since same requirements
Most “No” responses from REs are due to insufficient information rather than a known limitation
Key Takeaway: Voltage current injection settings should be achievable with proper parameterization and software changes for most legacy IBRs. ERCOT proposes to maintain requirements consistent with its August 18, 2023 comments with some variations to account for GE comments .

## Slide 21: Voltage Controls System Coordination
OEM RFI responses show high percentage able to comply.
Highlights more risk with the ROS approved version (15,875 MW) for commercially reasonable vs the ERCOT recommended version (7,167 MW) for technically feasible since same requirements
Most “No” responses from REs are due to insufficient information rather than a known limitation
Key Takeaway: Voltage controls coordination is critical and should be achievable with proper parameterization and software changes. ERCOT proposes to maintain requirements consistent with its August 18, 2023 comments.

## Slide 22: Voltage Filtered quantities/time delay use
OEM RFI responses show high percentage able to comply.
Highlights more risk with the ROS approved version (14,574 MW) for commercially reasonable vs the ERCOT recommended version (7,940 MW) for technically feasible since same requirements
Most “No” responses from REs are due to insufficient information rather than a known limitation
Key Takeaway: Using filtered voltage measurements and using a time delay for any voltage trip settings should be achievable with proper parameterization and software changes for most legacy IBRs. ERCOT proposes to maintain requirements consistent with its August 18, 2023 comments.

## Slide 23: Multiple excursion requirements
A majority of “no” responses are due to lack of prior testing and verification rather than verified limitation
Most IBRs do not actively monitor multiple excursions as a protection
Recent IBRWG meetings and commenters highlight that legacy wind turbines in particular are limited by dc chopper heat dissipation capabilities or other mechanical limitations.
Key Takeaway: Technical feasibility for legacy IBRs reflects challenges. ERCOT proposes to reduce currently proposed language addressing multiple excursions to account for local TSP reclose schemes at a minimum for legacy IBRs and maximize parameterization if it actively monitors. ERCOT will also propose additional clarification for new IBRs that recognizes energy dissipation characteristics due to recovery time after a fault.

## Slide 24: Phase Angle Jump requirements
A majority of “No” responses are due to lack of prior testing and verification rather than known limitation for OEMs and REs
Most IBRs do not actively monitor phase angle jump for tripping
Several recent technical discussions at various industry forums, including IBRWG highlight that IBRs should not trip off due for any level of phase angle jump during fault conditions which is the current status quo for voltage ride-through requirements
Key Takeaway: Technical feasibility for legacy IBRs reflects challenges. ERCOT proposes to remove currently proposed language addressing phase angle jump for legacy IBRs. ERCOT will maintain current requirements that when POIB is within VRT no trip zone, that IBRs are not allowed to trip off or reduce output due to phase angle jump.