ERCOT Nodal Operating Guide

- Table of Contents

- January 1, 2024

1	Overview	1

1.1	Document Purpose	1

1.2	Document Relationship	1

1.3	Process for Nodal Operating Guide Revision	1

1.3.1 Introduction	1

1.3.2 Submission of a Nodal Operating Guide Revision Request	3

1.3.3 Nodal Operating Guide Revision Procedure	3

1.3.3.1 Review and Posting of Nodal Operating Guide Revision Requests	 3

1.3.3.2 Withdrawal of a Nodal Operating Guide Revision Request	 4

1.3.3.3 ROS Review and Action	 5

1.3.3.4 Comments to teh ROS Report	 6

1.3.3.5 Nodal Operating Guide Revision Request Impact Analysis	 6

1.3.3.6 ROS Review of Impact Analysis	 7

1.3.3.7 ERCOT Impact Analysis Based on ROS Report	 7

1.3.3.8 PRS Review of Project Prioritization	 7

1.3.3.9 Technical Advisory Committee Vote	 7

1.3.3.10 ERCOT Board Vote	 9

1.3.3.11 PUCT Approval of Revision Requests…………………..   		            9

1.3.3.12 Appeal of Action	 10

1.3.4 Urgent Requests	10

1.3.5 Nodal Operating Guide Revision Implementation	11

1.4	Definitions	11

1.5	Operational Training	17

1.5.1 System Operator Training Objectives	17

1.5.2 System Operator Training Requirements	17

1.5.3 ERCOT Operations Training Seminar	18

1.5.4 ERCOT Severe Weather Drill	18

1.5.5 Training Practices	19

1.5.6 ERCOT Operator Certification Program	19

2	System Operations and Control Requirements	1

2.1	Operational Duties	1

2.2	System Monitoring and Control	3

2.2.1 Overview	3

2.2.2 Security Criteria	5

2.2.3 Response to Transient Voltage Disturbance	5

2.2.4 Load Frequency Control	5

2.2.4.1 Maintenance and Verification	 6

2.2.4.2 Regulation Provider Loss of AGC	6

2.2.4.3 ERCOT Loss of AGC	7

2.2.5 Automatic Voltage Regulators	7

2.2.6 Power System Stabilizers	10

2.2.7 Turbine Speed Governors	12

2.2.8 Performance/Disturbance/Compliance Analysis	13

2.2.9 Time Error and Time Synchronization	14

2.2.9.1 Time Error	 14

2.2.9.2 Time Synchronization	14

2.2.10 Generation Resource and Energy Storage Resource Response Time Requirements	15

2.3	Ancillary Services	18

2.3.1 Responsive Reserve	26

2.3.1.1 Obligation	26

2.3.1.2 Additional Operational Details for Responsive Reserve Provders	26

2.3.1.2.1 Limit on Generation Resources and Controllable Load Resources Providing RRS	32

2.3.2 Non-Spinning Reserve Service	33

2.3.2.1 Additional Operational Details for Non-Spinning Reserve Service Providers	33

2.4	Outage Coordination	37

2.5	Reliability Unit Commitment	38

2.5.1 Criteria for Removing Contingencies from the RUC Analyses	38

2.6	Requirements for Under-Frequency and Over- Frequency Relaying	38

2.6.1 Automatic Firm Load Shedding	38

2.6.2 Generators and Energy Storage Resources	42

2.6.2.1 Frequency Ride-Through Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs)	43

2.6.3 Frequency Ride-Through Requirements for Direct Current Ties (DC Ties)	44

2.7	System Voltage Profile and Operational Voltage Control	44

2.7.1 Introduction	44

2.7.2 Maintaining Voltage Profile	45

2.7.3 Real-Time Operational Voltage Control	47

2.7.3.1 Operational Guidelines	47

2.7.3.2 ERCOT Responsibilities	49

2.7.3.3 TO/TSP Responsibilities	51

2.7.3.4 QSE Responsibilities	53

2.7.3.5 Resource Entity Responsibilities and Generation Resource Requirements	55

2.7.4 Special Consideration for Nuclear Power Plants	58

2.7.5 Parameters for Standard Reactor and Capacitor Switching Plan	58

2.7.6 Unit Dispatch Beyond the Corrected Unit Reactive Limit or Unit Reactive Limit	59

2.8	Operation of Direct Current Ties	59

2.8.1 Inadvertent Energy Management	60

2.9	Voltage Ride-Through Requirements For Generation Resources	60

2.9.1 Voltage Ride-Through Requirements for Intermittent Renewable Resources Connected to the ERCOT Transmission Grid	63

2.9.2 Voltage Ride-Through Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs)	69

2.10	Voltage Ride-Through Requirements For DC Ties	69

3 	ERCOT AND MARKET PARTICIPANT RESPONSIBILITIES	1

3.1	System Control Interfaces with ERCOT	1

3.1.1 Introduction	1

3.1.2 Compliance with Dispatch Instructions	1

3.1.3 Dispatch Instructions	1

3.2	Qualified Scheduling Entities	3

3.2.1 Operating Obligations	3

3.2.2 Changes in Resource Status	4

3.2.3 Regulatory Required Incident and Disturbance Reports	4

3.2.4 Ancillary Service Qualification and Testing Program	5

3.3	Resource Entities	6

3.3.1 Unit Capability Requirements	9

3.3.2 Unit Reactive Capability Requirements	10

3.3.3 Resource Entity Responsibilities for Equipment Ratings	17

3.4	Load Resource Testing Requirement	18

3.5	ERCOT Implementation	18

3.6	Transmission Service Providers	19

3.7  	Transmission Operators	19

3.7.1 Transmission Owner Responsibility for a Vegetation Management Program	22

3.7.2 Trasmission Service Provider Responsibilities for Equipment Ratings	22

3.8  	Requirements for Reporting Sabotage Information	24

4	Emergency Operations	2

4.1	Introduction	2

4.2	Communication Under Emergency Conditions	2

4.2.1 Operating Condition Notice	2

4.2.2 Advisory	3

4.2.3 Watch	4

4.2.4 Emergency Notice	5

4.3	Operation to Maintain Transmission System Security	5

4.3.1 Real-Time and Short Term Planning	6

4.4	Block Load Transfers between ERCOT and Non-ERCOT System	6

4.5	Energy Emergency Alert (EEA)	6

4.5.1 General	6

4.5.2 Operating Procedures	7

4.5.3 Implementation	9

4.5.3.1 General Procedures Prior to EEA Operations	 11

4.5.3.2 General Procedures During EEA Operations	14

4.5.3.3 EEA Levels	15

4.5.3.4 Load Shed Obligation………………………………………………………………..20

4.5.3.5 EEA Termination…………………………………………...……………………….21

4.6	Black Start Service	21

4.6.1 Principles	22

4.6.2 Strategies	22

4.6.3 Priorities	23

4.6.4 Responsibilities	24

4.6.5 Black Start Emergency Back Up Communication Facilities Criteria	27

4.7	Geomagnetic Disturbance Operating Plan	28

4.7.1 Monitoring and Dissemination of Space Weather Information	28

4.7.2 Development and Submission of TO GMD Operating Procedures or Processes	28

4.7.3 ERCOT’s GMD Operating Plan and ERCOT Review of TO GMD Operating Procedures or Processes	29

4.8	Responsive Reserve Service During Scarcity Conditions…………………………………………29

4.8.1 Responsive Reserve Service Manual Deployment…………………………………………..30

4.8.2 Responsive Reserve Service Manual Recall…….……….………….………………………30

5	Network Operations Modeling Requirements	1

5.1	System Modeling Information	1

6	Disturbance Monitoring and System Protection	1

6.1	Disturbance Monitoring Requirements	1

6.1.1 Introduction	1

6.1.2 Fault Recording and Sequence of Events Recording Equipment	1

6.1.2.1 Fault Recording Requirements	 2

6.1.2.2 Fault Recording and Sequence of Events Recording Equipment Location Requirements	 2

6.1.2.3 Fault Recording and Sequence of Events Recording Data Requirements	 3

6.1.2.4 Fault Recording and Sequence of Events Recording Data Retention and Reporting Requirements	4

6.1.3 Phasor Measurement Recording Equipment Including Dynamic Disturbance Recording Equipment	4

6.1.3.1 Recording and Triggering Requirements	 4

6.1.3.2 Location Requirements	 5

6.1.3.3 Data Recording and Redundancy Requirements	 6

6.1.3.4 Data Retention and Data Reporting Requirements	 7

6.1.4 Maintenance and Testing Requirements	8

6.1.5 Equipment Reporting Requirements	8

6.1.5.1 Geomagnetic Disturbance (GMD) Measurement Data Processes	 8

6.1.6 Review Process	8

6.2	System Protective Relaying	9

6.2.1 Introduction	9

6.2.1.1 Applicability	 9

6.2.2 Design and Operating Requirements for ERCOT System Facilities	10

6.2.3 Performance Analysis Requirements for ERCOT System Facilities	11

6.2.4 Protective Relay System Failure Response	13

6.2.5 Maintenance and Testing Requirements for ERCOT System Facilities	14

6.2.6 Requirements and Recommendations for ERCOT System Facilities	15

6.2.6.1 General Protection Criteria	 15

6.2.6.1.1 Dependability	 15

6.2.6.1.2 Security	 15

6.2.6.1.3 Dependability and Security	 15

6.2.6.1.4 Operating Time	 16

6.2.6.1.5 Testing and Maintenance	 16

6.2.6.1.6 Analysis of System Performance and Associated Protection Systems	 17

6.2.6.2 Equipment and Design Considerations	 18

6.2.6.2.1 Current Transformers	 18

6.2.6.2.2 Voltage Transformers and Potential Devices	 19

6.2.6.2.3 Batteries and Direct Current Supply	 20

6.2.6.2.4 AC Auxiliary Power	 21

6.2.6.2.5 Circuit Breakers	 21

6.2.6.2.6 Communication Channels	 21

6.2.6.2.7 Control Cables and Wiring	 22

6.2.6.2.8 Environment	 23

6.2.6.3 Specific Application Considerations	 23

6.2.6.3.1 Transmission Line Protection	 23

6.2.6.3.2 Transmission Station Protection	 24

6.2.6.3.3 Breaker Failure Protection	 25

6.2.6.3.4 Generator Protection and Relay Requirements	 26

6.2.6.3.5 Automatic Under-Frequency Load Shedding Protection Systems	 28

6.2.6.3.6 Automatic Under-Voltage Load Shedding Protection Systems	 28

7	Telemetry and Communication	1

7.1  	ERCOT Wide Area Network	1

7.1.1 ERCOT Responsibilities	2

7.1.2 WAN Participation Responsibilities	2

7.1.3 Joint Responsibilities (Maintenance and Restoration)	11

7.2	ERCOT ICCP Interface	11

7.2.1 Quality Codes	11

7.2.2 Metric of Availability	12

7.3	Telemetry	12

7.3.1 Data from ERCOT to QSEs	13

7.3.2 Data from ERCOT to TSP	13

7.3.3 Data from WAN Participants to ERCOT	14

7.3.4 Resolving Real-Time Data Issues that affect ERCOT Network Security Analysis	15

7.3.5 TSP and QSE Telemetry Restoration	16

7.3.6 General Telemetry Performance Criterion..............................................................................16

7.4	Calibration and Testing of Telemetry Responsibilities	16

7.5	Competitive Renewable Energy Zone Circuits and Stations	17

8	Attachments

8A Black Start Info

8B Protection System Misoperation Report

8C Turbine Governor Speed Tests

8D Seasonal Unit Net Real Power Capability Verification

8E Black Start Plan Template

8F Seasonal Hydro Responsive Reserve Net Capability Verification

8G Load Resource Tests

8H Unit Alternative Fuel Capability

8I Black Start Resource Availabiity Test Form

8J Initial and Sustained Measurements for Primary Frequency Response

8K Remedial Action Scheme (RAS) Template

8L Emergency Operations Plan

8M Selecting Buses for Capturing Sequence of Events Recording and Fault Recording Data

9	Monitoring Programs	1

9.1	QSE and Resource Monitoring Program	1

9.1.1 Real-Time Data	1

9.1.2 Compliance with Valid Dispatch Instructions	1

9.1.3 Resource Outage Reporting	2

9.1.4 Current Operating Plan Metrics for QSEs	2

9.2	TSP Monitoring Program	2

9.2.1 Intentionally Left Blank	3

9.2.2 Real-Time Data Monitor	3

9.2.3 Transmission Outage Reporting	3

9.3	ERCOT Monitoring Program	4

9.3.1 Transmission Control	4

9.3.2 System and Resource Control	5

9.3.3 Computer and Communication Systems Real-Time Availability and Systems Security	5

9.4	Ancillary Services Monitoring Program	5

9.4.1 Hydro Responsive Testing	5

9.4.2 Resource-Specific Responsive Reserve Performance	6

9.4.3 Resource-specific Non-Spinning Reserve	6

10	Market Data Transparency	1

10.1	Direct Current Tie Outage Information	1

11	Constraint Management Plans and Remedial Action Schemes	1

11.1	Introduction	1

11.2	Remedial Action Schemes	2

11.2.1 Reporting of RAS Operations	7

11.3	Automatic Mitigation Plans	8

11.4	Remedial Action Plan	10

11.4.1 Remedial Action Plan Process	11

11.5	Mitigation Plan	11

11.6	Pre-Contingency Action Plans	12

11.6.1 Pre-Contingency Action Plan Process	13

11.7	Temporary Outage Action Plan	13