## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS
Vice Chair: Chad Mulholland, NRG
ROS
January 8th, 2024

## Slide 2: Meeting Minutes
PDCWG Meeting 12/20/2023
  2024 Leadership PDCWG
  2024 PDCWG Calendar Review
  High Level Review of September 6, 2023 Frequency Event
  ERCOT Analysis of Disturbances/Frequency Events
  ERCOT Frequency Control Metrics and Regulation Reports
  TRE Report

## Slide 3: Frequency Measurable Events Performance

## Slide 4: Frequency Measurable Events
There was 1 FME in November
  11/9/2023 12:37:36
  Loss of 512 MW of Generation
    Interconnection Frequency Response: 1422 MW/0.1 Hz
    102 Resources were evaluated. These includes,
      30 Generation Resources
      3 Controllable Load Resources
      69 Energy Storage Resources
    14 of 102 Evaluated Resources had less than 75% of their expected Initial Primary Frequency Response.
    11 of 102 Evaluated Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 5: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 463 MW/0.1 Hz
IMFR Performance currently
1362.18 MW/0.1HZ

## Slide 6
Questions?

## Slide 7: Frequency Control Report
October 2023

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency
Notes: 14.82 mHz on avg for November 2023

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy
Notes: 31,531,973 MWh

## Slide 13: ERCOT Total Energy from Wind Generation
Notes:   7,779,271 MWH

## Slide 14: ERCOT % Energy from Wind Generation
Notes: 24.67%
of total energy was provided by wind generation

## Slide 15: ERCOT Total Energy from Solar Generation
Notes: 1,916,520 MWh

## Slide 16: ERCOT % Energy from Solar Generation
Notes: 6.08% of total energy was provided by solar generation.

## Slide 17: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia = 157,095 MW*s on 11/21/2023
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 197,289 MW*s
Max: 264,808 MW*s on November 28th
Min: 157,095 MW*s on November 21st

## Slide 18: ERCOT Inertia Trend
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.