## Start
ERCOT Distribution Loss Factor Estimates for 2024 (Mar - Dec)
1. Using the Spreadsheet to Calculate/Estimate Distribution Loss Factors
This spreadsheet calculates distribution loss factors (DLF) for all Distribution Service Providers (DSP) at various levels of ERCOT system load. From the "Inputs - Single DSP View" Tab, the user will select the DSP-DLF code and ERCOT load level of interest and the spreadsheet will calculate the resulting distribution loss factor. The graph displays the DSP loss factors at various ERCOT load levels as well as the level specified.
The "Inputs - Multiple DSP View" tab operates similar to the "Inputs - Single DSP View" tab and displays graphically all DSPs' DLF curves.
2. Examining the Calculations
This spreadsheet calculates the distribution loss factors for a selected TDSP based on the following formula:
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where: i = Interval
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval ERCOT Load (ERCOT Day Ahead Forecasted MW Load divided by 4)
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = ERCOT Annual interval Average Load (ERCOT will use 12,450 MWh for year 2024 calculations)
AAL = Annual Total System MWh / (Number of settlement intervals in the year)
Distribution Loss Factor Methodologies
Pursuant to Protocol Section 13.3 ERCOT is required to post annual Distribution Loss Factor (DLF) Methodologies submitted by TDSPs participating in the competitive retail electric market. DLF Methodologies are submitted to ERCOT prior to October 30 for review, approval, and posting by January 1st of the following year. DLF Methodogies changed outside of the annual process must be submitted two months prior to any update. These DLF Methodologies provide the ERCOT market with insight into the derivations that each TDSP uses for the Annual Distribution Loss Factor and Coefficients derived from regression analysis of the the TDSP loss study results.
The table below contains DLF Methodologies for the calendar year 2024 from April through December.
DSP | DLF Methodology
AEP-TCC/AEP-TNC | Methodology is referenced in PDFs AEP TCC TNC SILF 2020 and AEP_SILF 2020 included in this zip file.
CenterPoint | Methodology is referenced in Excel file CenterPoint Energy Distribution Loss Factor 2024 included in this zip file.
LP&L | Methodology is referenced in PDF LPL Distribution Loss Factor and Methodology V2 included in this zip file.
Nueces EC | Methodology is referenced in PDF NEC TDSP 2023 included in this zip file.
TNMP | Methodology is referenced in PDF TNMP DLF Summary V1.0 included in this zip file.
Oncor | Methodology is referenced in PDF 2017 Study of Oncor Electric Delivery Distribution Loss Factors included in this zip file.

## Inputs - Single DSP View
DSP DLF Code to Graph
Input ERCOT Load |  | AEP - TCC A | 1 | 5 | AEP - TCC A
|  | AEP - TCC B | 2 | 6 | AEP - TCC B
ERCOT MW Load | 49798 | AEP - TNC A | 3 | 7 | AEP - TNC A
|  | AEP - TNC B | 4 | 8 | AEP - TNC B | 1 | Oncor B
|  | CenterPoint D | 5 | 9 | CenterPoint D | 1 | AEP - TCC A
|  | CenterPoint E | 6 | 10 | CenterPoint E
DLF for DSP Selected to Graph |  | LP&L A | 7 | 11 | LP&L A
|  | LP&L B | 8 | 12 | LP&L B
AEP - TCC A | 5.49% | Nueces EC A | 9 | 13 | Nueces EC A
|  | Nueces EC B | 10 | 14 | Nueces EC B
|  | TNMP A | 11 | 15 | TNMP A
|  | TNMP B | 12 | 16 | TNMP B
|  | TNMP C | 13 | 17 | TNMP C
|  | TNMP D | 14 | 18 | TNMP D
All DSP Distribution Loss Factors |  | TNMP E | 15 | 19 | TNMP E
|  | Oncor A | 16 | 20 | Oncor A
AEP - TCC A | 5.49% | Oncor B | 17 | 21 | Oncor B
AEP - TCC B | 2.838%
AEP - TNC A | 6.006%
AEP - TNC B | 2.187%
CenterPoint D | 3.969%
CenterPoint E | 1.337%
LP&L A | 5.79%
LP&L B | 12.03%
Nueces EC A | 2.366%
Nueces EC B | 5.072%
TNMP A | 3.8%
TNMP B | 5.05%
TNMP C | 3.85%
TNMP D | 6.34%
TNMP E | 3.95%
Oncor A | 3.278%
Oncor B | 1.646%

## Inputs - Multiple DSP View
DSP DLF Code to Graph
Input ERCOT Load |  | AEP - TCC A | 1 | 5 | AEP - TCC A
|  | AEP - TCC B | 2 | 6 | AEP - TCC B
ERCOT MW Load | 49798 | AEP - TNC A | 3 | 7 | AEP - TNC A
|  | AEP - TNC B | 4 | 8 | AEP - TNC B | 1 | Oncor B
|  | CenterPoint D | 5 | 9 | CenterPoint D
|  | CenterPoint E | 6 | 10 | CenterPoint E | 1 | AEP - TCC A
DLF for DSP Selected |  | LP&L A | 7 | 11 | LP&L A
|  | LP&L B | 8 | 12 | LP&L B
AEP - TCC A | 5.49% | Nueces EC A | 9 | 13 | Nueces EC A
|  | Nueces EC B | 10 | 14 | Nueces EC B
|  | TNMP A | 11 | 15 | TNMP A
All DSP Distribution Loss Factors |  | TNMP B | 12 | 16 | TNMP B
|  | TNMP C | 13 | 17 | TNMP C
AEP - TCC A | 5.49% | TNMP D | 14 | 18 | TNMP D
AEP - TCC B | 2.838% | TNMP E | 15 | 19 | TNMP E
AEP - TNC A | 6.006% | Oncor A | 16 | 20 | Oncor A
AEP - TNC B | 2.187% | Oncor B | 17 | 21 | Oncor B
CenterPoint D | 3.969%
CenterPoint E | 1.337%
LP&L A | 5.79%
LP&L B | 12.03%
Nueces EC A | 2.366%
Nueces EC B | 5.072%
TNMP A | 3.8%
TNMP B | 5.05%
TNMP C | 3.85%
TNMP D | 6.34%
TNMP E | 3.95%
Oncor A | 3.278%
Oncor B | 1.646%

## TDSP and ERCOT Variables
ERCOT |  |  |  | DSP = | AEP - TCC | AEP - TCC | AEP - TNC | AEP - TNC | CenterPoint | CenterPoint | LP&L | LP&L | Nueces EC | Nueces EC | TNMP | TNMP | TNMP | TNMP | TNMP | Oncor | Oncor
September 01, 2022 to August 31, 2023 |  |  |  | DLF Code = | A | B | A | B | D | E | A | B | A | B | A | B | C | D | E | A | B
Annual MWh | 436232829 |  |  | F1 = | 0.02502 | 0.01872 | 0.02386 | 0.00622 | 0.022 | 0.0161 | 0.0322 | 0.0361 | 0.0234 | 0.0256 | 0.0172 | 0.0225 | 0.01 | 0.0217 | 0.0126 | 0.017 | 0.01147
Interval Count | 35040 |  |  | F2 = | 0 | 0 | 0 | 0 | -0.00615 | -0.0051 | 0.000302 | 0.000926 | 0.000141 | 0.00012 | 0.0004 | 0.0008 | 0 | -0.0007 | 0 | -0.002 | -0.00031
ERCOT AAL | 12449.567 | MWh |  | F3 = | 0.02988 | 0.00966 | 0.0362 | 0.01565 | 0.02384 | 0.002375 | 0.0254 | 0.083278 | 0.00012 | 0.025 | 0.0204 | 0.0272 | 0.0285 | 0.0424 | 0.0269 | 0.01778 | 0.0053
ERCOT Peak MW | 85579 | MW
| Hourly |  | Per Interval |  | AEP - TCC | AEP - TCC | AEP - TNC | AEP - TNC | CenterPoint | CenterPoint | LP&L | LP&L | Nueces EC | Nueces EC | TNMP | TNMP | TNMP | TNMP | TNMP | Oncor | Oncor
| MW Load |  | MWh |  | A | B | A | B | D | E | A | B | A | B | A | B | C | D | E | A | B
Example | 15000 |  | 3750 |  | 10.67% | 3.771% | 12.74% | 5.383% | 7.962% | 0.7634% | 9.433% | 28.83% | 0.7588% | 9.083% | 7.331% | 9.788% | 9.763% | 14.66% | 9.31% | 6.215% | 2.074%
Results: | 20000 |  | 5000 |  | 8.445% | 3.157% | 9.972% | 4.147% | 6.205% | 0.728% | 7.648% | 22.28% | 0.9838% | 7.265% | 5.81% | 7.756% | 7.498% | 11.36% | 7.204% | 4.91% | 1.749%
| 25000 |  | 6250 |  | 7.208% | 2.864% | 8.409% | 3.43% | 5.238% | 0.7713% | 6.706% | 18.49% | 1.213% | 6.277% | 4.967% | 6.628% | 6.179% | 9.465% | 5.991% | 4.195% | 1.601%
| 30000 |  | 7500 |  | 6.467% | 2.731% | 7.446% | 2.973% | 4.668% | 0.8541% | 6.186% | 16.09% | 1.444% | 5.704% | 4.462% | 5.951% | 5.333% | 8.275% | 5.224% | 3.776% | 1.54%
| 35000 |  | 8750 |  | 6.01% | 2.69% | 6.828% | 2.664% | 4.323% | 0.9595% | 5.907% | 14.48% | 1.676% | 5.368% | 4.151% | 5.531% | 4.758% | 7.488% | 4.713% | 3.525% | 1.529%
| 45000 |  | 11250 |  | 5.568% | 2.761% | 6.162% | 2.294% | 4.011% | 1.208% | 5.751% | 12.57% | 2.142% | 5.092% | 3.852% | 5.123% | 4.058% | 6.583% | 4.115% | 3.304% | 1.592%
at ERCOT AAL | 49798.2682 |  | 12449.567 |  | 5.49% | 2.838% | 6.006% | 2.187% | 3.969% | 1.337% | 5.79% | 12.03% | 2.366% | 5.072% | 3.8% | 5.05% | 3.85% | 6.34% | 3.95% | 3.278% | 1.646%
| 50000 |  | 12500 |  | 5.488% | 2.842% | 6.001% | 2.183% | 3.968% | 1.343% | 5.793% | 12.01% | 2.376% | 5.072% | 3.799% | 5.048% | 3.843% | 6.332% | 3.944% | 3.278% | 1.649%
| 55000 |  | 13750 |  | 5.469% | 2.942% | 5.913% | 2.104% | 3.973% | 1.483% | 5.886% | 11.62% | 2.609% | 5.103% | 3.787% | 5.028% | 3.685% | 6.166% | 3.827% | 3.287% | 1.716%
| 60000 |  | 15000 |  | 5.495% | 3.057% | 5.879% | 2.048% | 4.014% | 1.627% | 6.018% | 11.35% | 2.843% | 5.171% | 3.806% | 5.048% | 3.57% | 6.064% | 3.751% | 3.324% | 1.791%
| 65000 |  | 16250 |  | 5.555% | 3.184% | 5.888% | 2.011% | 4.083% | 1.773% | 6.179% | 11.18% | 3.078% | 5.269% | 3.848% | 5.101% | 3.489% | 6.011% | 3.706% | 3.381% | 1.872%
| 70000 |  | 17500 |  | 5.643% | 3.319% | 5.929% | 1.988% | 4.173% | 1.922% | 6.363% | 11.09% | 3.312% | 5.389% | 3.909% | 5.178% | 3.433% | 5.997% | 3.685% | 3.455% | 1.958%
| 75000 |  | 18750 |  | 5.752% | 3.461% | 5.997% | 1.976% | 4.281% | 2.072% | 6.566% | 11.06% | 3.546% | 5.527% | 3.985% | 5.275% | 3.398% | 6.013% | 3.684% | 3.541% | 2.048%
| 85000 |  | 21250 |  | 6.021% | 3.761% | 6.193% | 1.979% | 4.537% | 2.377% | 7.014% | 11.13% | 4.015% | 5.846% | 4.171% | 5.514% | 3.377% | 6.118% | 3.727% | 3.743% | 2.237%
at ERCOT peak | 85579 |  | 21394.75 |  | 6.038% | 3.779% | 6.207% | 1.98% | 4.553% | 2.395% | 7.042% | 11.14% | 4.042% | 5.866% | 4.183% | 5.529% | 3.377% | 6.126% | 3.731% | 3.756% | 2.249%
| 90000 |  | 22500 |  | 6.175% | 3.918% | 6.315% | 1.99% | 4.68% | 2.531% | 7.255% | 11.22% | 4.25% | 6.022% | 4.277% | 5.651% | 3.384% | 6.198% | 3.766% | 3.856% | 2.335%

## Calculations for Graph (hidden)
ERCOT | [5 empty] | DSP = | AEP - TCC | AEP - TCC | AEP - TNC | AEP - TNC | CenterPoint | CenterPoint | LP&L | LPL&L | Nueces EC | Nueces EC | TNMP | TNMP | TNMP | TNMP | TNMP | Oncor | Oncor
September 01, 2022 to August 31, 2023 | [5 empty] | DLF Code = | A | B | A | B | D | E | A | B | A | B | A | B | C | D | E | A | B
Annual MWH | 436232829 |  |  |  |  | F1 = | 0.02502 | 0.01872 | 0.02386 | 0.00622 | 0.022 | 0.0161 | 0.0322 | 0.0361 | 0.0234 | 0.0256 | 0.0172 | 0.0225 | 0.01 | 0.0217 | 0.0126 | 0.017 | 0.01147
Interval Count | 35040 |  |  |  |  | F2 = | 0 | 0 | 0 | 0 | -0.00615 | -0.0051 | 0.000302 | 0.000926 | 0.000141 | 0.00012 | 0.0004 | 0.0008 | 0 | -0.0007 | 0 | -0.002 | -0.00031
ERCOT AAL | 12449.567 | MWhs |  |  |  | F3 = | 0.02988 | 0.00966 | 0.0362 | 0.01565 | 0.02384 | 0.002375 | 0.0254 | 0.083278 | 0.00012 | 0.025 | 0.0204 | 0.0272 | 0.0285 | 0.0424 | 0.0269 | 0.01778 | 0.0053
ERCOT Peak MW | 85579 | MW
| Multi-Graph | 49798 | 0% |  |  | Multi-Graph | A: 49798; B: 5.49%
| ERCOT MW | 49798 | 20% |  |  | ERCOT Load | bar: B
| Hourly |  | Per Interval |  |  | Single DSP | A: Multiple DSP View
meter | MW Load |  | MWHs |  |  | View
Example | 15000 |  | 3750 | 0% | 0% | 10.67% | 10.67% | 3.771% | 12.74% | 5.383% | 7.962% | 0.7634% | 9.433% | 28.83% | 0.7588% | 9.083% | 7.331% | 9.788% | 9.763% | 14.66% | 9.31% | 6.215% | 2.074%
Results: | 20000 |  | 5000 | 0% | 0% | 8.445% | 8.445% | 3.157% | 9.972% | 4.147% | 6.205% | 0.728% | 7.648% | 22.28% | 0.9838% | 7.265% | 5.81% | 7.756% | 7.498% | 11.36% | 7.204% | 4.91% | 1.749%
| 25000 |  | 6250 | 0% | 0% | 7.208% | 7.208% | 2.864% | 8.409% | 3.43% | 5.238% | 0.7713% | 6.706% | 18.49% | 1.213% | 6.277% | 4.967% | 6.628% | 6.179% | 9.465% | 5.991% | 4.195% | 1.601%
| 30000 |  | 7500 | 0% | 0% | 6.467% | 6.467% | 2.731% | 7.446% | 2.973% | 4.668% | 0.8541% | 6.186% | 16.09% | 1.444% | 5.704% | 4.462% | 5.951% | 5.333% | 8.275% | 5.224% | 3.776% | 1.54%
| 35000 |  | 8750 | 0% | 0% | 6.01% | 6.01% | 2.69% | 6.828% | 2.664% | 4.323% | 0.9595% | 5.907% | 14.48% | 1.676% | 5.368% | 4.151% | 5.531% | 4.758% | 7.488% | 4.713% | 3.525% | 1.529%
| 45000 |  | 11250 | 0% | 0% | 5.568% | 5.568% | 2.761% | 6.162% | 2.294% | 4.011% | 1.208% | 5.751% | 12.57% | 2.142% | 5.092% | 3.852% | 5.123% | 4.058% | 6.583% | 4.115% | 3.304% | 1.592%
at ERCOT AAL | 49798.2682 |  | 12449.567 | 0% | 0% | 5.49% | 5.49% | 2.838% | 6.006% | 2.187% | 3.969% | 1.337% | 5.79% | 12.03% | 2.366% | 5.072% | 3.8% | 5.05% | 3.85% | 6.34% | 3.95% | 3.278% | 1.646%
| 50000 |  | 12500 | 0% | 0% | 5.488% | 5.488% | 2.842% | 6.001% | 2.183% | 3.968% | 1.343% | 5.793% | 12.01% | 2.376% | 5.072% | 3.799% | 5.048% | 3.843% | 6.332% | 3.944% | 3.278% | 1.649%
| 55000 |  | 13750 | 0% | 0% | 5.469% | 5.469% | 2.942% | 5.913% | 2.104% | 3.973% | 1.483% | 5.886% | 11.62% | 2.609% | 5.103% | 3.787% | 5.028% | 3.685% | 6.166% | 3.827% | 3.287% | 1.716%
| 60000 |  | 15000 | 0% | 0% | 5.495% | 5.495% | 3.057% | 5.879% | 2.048% | 4.014% | 1.627% | 6.018% | 11.35% | 2.843% | 5.171% | 3.806% | 5.048% | 3.57% | 6.064% | 3.751% | 3.324% | 1.791%
| 65000 |  | 16250 | 0% | 0% | 5.555% | 5.555% | 3.184% | 5.888% | 2.011% | 4.083% | 1.773% | 6.179% | 11.18% | 3.078% | 5.269% | 3.848% | 5.101% | 3.489% | 6.011% | 3.706% | 3.381% | 1.872%
| 70000 |  | 17500 | 0% | 0% | 5.643% | 5.643% | 3.319% | 5.929% | 1.988% | 4.173% | 1.922% | 6.363% | 11.09% | 3.312% | 5.389% | 3.909% | 5.178% | 3.433% | 5.997% | 3.685% | 3.455% | 1.958%
| 75000 |  | 18750 | 0% | 0% | 5.752% | 5.752% | 3.461% | 5.997% | 1.976% | 4.281% | 2.072% | 6.566% | 11.06% | 3.546% | 5.527% | 3.985% | 5.275% | 3.398% | 6.013% | 3.684% | 3.541% | 2.048%
| 85000 |  | 21250 | 0% | 0% | 6.021% | 6.021% | 3.761% | 6.193% | 1.979% | 4.537% | 2.377% | 7.014% | 11.13% | 4.015% | 5.846% | 4.171% | 5.514% | 3.377% | 6.118% | 3.727% | 3.743% | 2.237%
at ERCOT peak | 85579 |  | 21394.75 | 0% | 0% | 6.038% | 6.038% | 3.779% | 6.207% | 1.98% | 4.553% | 2.395% | 7.042% | 11.14% | 4.042% | 5.866% | 4.183% | 5.529% | 3.377% | 6.126% | 3.731% | 3.756% | 2.249%
| 90000 |  | 22500 | 0% | 0% | 6.175% | 6.175% | 3.918% | 6.315% | 1.99% | 4.68% | 2.531% | 7.255% | 11.22% | 4.25% | 6.022% | 4.277% | 5.651% | 3.384% | 6.198% | 3.766% | 3.856% | 2.335%
Single DSP View | 49798 |  | 12449.5 | 0% | 0% | 5.49% | 5.49% | 2.838% | 6.006% | 2.187% | 3.969% | 1.337% | 5.79% | 12.03% | 2.366% | 5.072% | 3.8% | 5.05% | 3.85% | 6.34% | 3.95% | 3.278% | 1.646%
Multiple DSP View | 49798 |  | 12449.5 | 0% | 0% | 5.49% | 5.49% | 2.838% | 6.006% | 2.187% | 3.969% | 1.337% | 5.79% | 12.03% | 2.366% | 5.072% | 3.8% | 5.05% | 3.85% | 6.34% | 3.95% | 3.278% | 1.646%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
Note on B4: Donald Maul: Updated as needed based on leap years