## 1) General Information
CenterPoint Energy Distribution Loss Factor for |  |  |  |  | 2024
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was updated on September 1, 2016. See following
protocol link: http://www.ercot.com/mktrules/nprotocols/current
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load (15 minute basis)
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
AAL value for use in 2024 = 12,450 MWH
AAL value for use in 2023 = 12,069 MWH
AAL value for use in 2022 = 11,048 MWH
AAL value for use in 2021 = 10,968 MWH
AAL value for use in 2020 = 10,740 MWH
AAL value for use in 2019 = 10,708 MWH
AAL value for use in 2018 = 10,190 MWH
AAL value for use in 2017 = 9,898 MWH
AAL value for use in 2016 = 9,940 MWH
AAL value for use in 2015 = 9,741 MWH
AAL value for use in 2014 = 9,290 MWH
AAL value for use in 2013 = 9,304 MWH
AAL value for use in 2012 = 9,463 MWH
AAL value for use in 2011 = 9,034 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = |  | 0.022
F2 = |  | -0.00615
F3 = |  | 0.02384
AAL for ERCOT (15 mins) = 10,708 |  | 12450
For "E" Primary Customers
F1 = |  | 0.0161
F2 = |  | -0.0051
F3 = |  | 0.002375
AAL for ERCOT (15 mins) = 10,708 |  | 12450
Assumptions
1. Assume AAL for CNP corresponds to AAL for ERCOT
2. However, the peak for CNP is proportionately greater than the peak for ERCOT relative to AAL.
Ratio of Peak to AAL
|  | CNP | ERCOT
Ratio of Peak to AAL for CNP is not proportional to ERCOT |  | 2.1285 | 1.7185
2021 for use in 2022 |  |  | 2022 for use in 2023 |  | 2023 for use in 2024
| 15 mins | 1 hour | 15 mins | 1 hour | 15 mins | 1 hour
CNP Peak | 3835 | 15340 | 4110.5 | 16442 | 4422 | 17688
CNP AAL | 1917 | 7668 | 2043.25 | 8173 | 2077.5 | 8310
ERCOT Peak | 18446.5 | 73786 | 20058.25 | 80233 | 21394.75 | 85579
ERCOT AAL | 11048 | 44192 | 12069 | 48276 | 12450 | 49800
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak, so that when ERCOT hits peak, % losses will correspond to CNP peak.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 3 - Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2018 for use as follows:
1. Substation Transformer Losses - The A B constants for substation transformers were updated for | [7 empty] | 2024
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
This database contains test data for every substation transformer.
| The total no-load losses are |  | 18.835 | MW.
Also, the database provided the total "Load" losses for the transformers on the system at rated trf load.
| This value is | 64.591 | MW at | 18.835 | MW load level.
| This results in a total of |  | 83.426 | MW of substation transformer losses at approximately |  |  |  | 20710.4 | MVA at CNP (Sub Trf nameplate rating)
The constants in the system loss equations were adjusted to match this result. See Tab 3.
2. Primary Conductor Losses (No change in the A B constants for primary conductor)
The primary conductor losses for 2007 were considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
| For | 2024 | there is no further change in the system loss equations.
3. Distribution Transformer Losses - The A B constants for distribution transformers were updated for | [7 empty] | 2024
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses.
Since the no-load losses used in the TLM program were based on older/higher values from 1985 and the GIS spreadsheet
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for "no-load" losses for a distribution system that has both old and new transformers.
The "load losses" from both methods were very close, so the load losses from GIS were used.
See Tab 3 for the updated A B constants for distribution transformers.
4. Secondary Conductor Losses - No change in the A B constants for secondary conductor for | [6 empty] | 2024
The constant in the system loss equation for secondary losses is same as used in previous years.
5. AAL for ERCOT
| The AAL for ERCOT was updated based on information from ERCOT. The new value is | [5 empty] | 12450 | MWH for 15 minutes.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were adjusted to get a curve fit in the most critical areas. See spreadsheet and graphs in Tab 2 - Loss Analysis.
The F1, F2, and F3 coefficients for D secondary customers and E primary metered customers for 2017 are shown above.
Overall results:
For "E" Primary Customers |  |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 for 2024
|  | DLF at AAL | 1.286% | 1.3% | 1.27% | 1.286% | 1.252% | 1.334% | 1.338%
|  | DLF at ERCOT Peak | 2.107% | 2.155% | 2.157% | 2.18% | 2.131% | 2.262% | 2.395%
For "D" Secondary Customers |  |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 for 2024
|  | DLF at AAL | 3.791% | 3.816% | 3.838% | 3.837% | 3.87% | 3.802% | 3.969%
|  | DLF at ERCOT Peak | 4.213% | 4.259% | 4.289% | 4.303% | 4.24% | 4.367% | 4.553%
Questions:
If you have any questions, please call Robert Pitcel at 713-207-7621, Michael Blum 713-207-6598, or Brian Clowe 713-207-6287.
Email Robert Pitcel at robert.pitcel@centerpointenergy.com, michael.blum@centerpointenergy.com, or Brian Clowe at brian.clowe@centerpointenergy.com

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 2) Loss Analysis
|  | CenterPoint Energy Distribution Loss Factor | [12 empty] | No Scaling | With Scaling | Using F1, F2 & F3 Coefficients |  | No Scaling | With Scaling
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  |  | Secondary | [5 empty] | Total |  | Adjustment for % Losses |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL | [15 empty] | 0% |  |  |  | 0%
|  |  |  | 50 | 18.8354 | 31.1646 | 0.0011066 | 18.8365 | 37.67% | 31.1635 | 170.5454 | -139.3818 | 0.0068862 | 189.3887 | 378.8% | 378.8%
|  |  |  | 135 | 18.8377 | 116.1623 | 0.015375 | 18.8531 | 13.97% | 116.1469 | 170.5499 | -54.403 | 0.0010491 | 189.4041 | 140.3% | 140.3%
|  |  |  | 500 | 18.8726 | 481.1274 | 0.26375 | 19.1364 | 3.827% | 480.8636 | 170.6291 | 310.2345 | 0.034115 | 189.7996 | 37.96% | 37.96%
1498.1949 | 5992.7798 |  | 250 | 1000 | 18.9856 | 981.0144 | 1.0965 | 20.0821 | 2.008% | 979.9179 | 170.8941 | 809.0237 | 0.232 | 191.2083 | 19.12% | 19.12%
3595.6679 | 14382.6715 | 1 | 600 | 2400 | 19.7024 | 2380.2976 | 6.4556 | 26.158 | 1.09% | 2373.842 | 172.5939 | 2201.2481 | 1.7175 | 200.4694 | 8.353% | 8.353% | 8.275% | 0.7773% | 1.09% | 1.09% |  |  | 26.158 | 200.4694
4194.9458 | 16779.7834 | 2 | 700 | 2800 | 20.0156 | 2779.9844 | 8.8056 | 28.8212 | 1.029% | 2771.1788 | 173.3372 | 2597.8416 | 2.3922 | 204.5506 | 7.305% | 7.305% | 7.202% | 0.7373% | 1.029% | 1.029% |  |  | 28.8212 | 204.5506
4794.2238 | 19176.8953 | 3 | 800 | 3200 | 20.377 | 3179.623 | 11.5192 | 31.8963 | 0.9968% | 3168.1037 | 174.1944 | 2993.9093 | 3.1772 | 209.2679 | 6.54% | 6.54% | 6.423% | 0.7267% | 0.9968% | 0.9968% |  |  | 31.8963 | 209.2679
5393.5018 | 21574.0072 | 4 | 900 | 3600 | 20.7866 | 3579.2134 | 14.5965 | 35.3831 | 0.9829% | 3564.6169 | 175.1651 | 3389.4518 | 4.0722 | 214.6203 | 5.962% | 5.962% | 5.841% | 0.7357% | 0.9829% | 0.9829% |  |  | 35.3831 | 214.6203
5992.7798 | 23971.1191 | 5 | 1000 | 4000 | 21.2444 | 3978.7556 | 18.0371 | 39.2815 | 0.982% | 3960.7185 | 176.2489 | 3784.4696 | 5.0767 | 220.6071 | 5.515% | 5.515% | 5.397% | 0.7584% | 0.982% | 0.982% |  |  | 39.2815 | 220.6071
6592.0578 | 26368.231 | 6 | 1100 | 4400 | 21.7504 | 4378.2496 | 21.841 | 43.5915 | 0.9907% | 4356.4085 | 177.4455 | 4178.963 | 6.1902 | 227.2272 | 5.164% | 5.164% | 5.052% | 0.791% | 0.9907% | 0.9907% |  |  | 43.5915 | 227.2272
7191.3357 | 28765.343 | 7 | 1200 | 4800 | 22.3046 | 4777.6954 | 26.0081 | 48.3127 | 1.007% | 4751.6873 | 178.7545 | 4572.9327 | 7.4124 | 234.4796 | 4.885% | 4.885% | 4.783% | 0.8311% | 1.007% | 1.007% |  |  | 48.3127 | 234.4796
7790.6137 | 31162.4549 | 8 | 1300 | 5200 | 22.907 | 5177.093 | 30.5383 | 53.4452 | 1.028% | 5146.5548 | 180.1757 | 4966.3791 | 8.7427 | 242.3636 | 4.661% | 4.661% | 4.571% | 0.877% | 1.028% | 1.028% |  |  | 53.4452 | 242.3636
8389.8917 | 33559.5668 | 9 | 1400 | 5600 | 23.5575 | 5576.4425 | 35.4313 | 58.9888 | 1.053% | 5541.0112 | 181.7085 | 5359.3027 | 10.1808 | 250.8781 | 4.48% | 4.48% | 4.405% | 0.9274% | 1.053% | 1.053% |  |  | 58.9888 | 250.8781
8989.1697 | 35956.6787 | 10 | 1500 | 6000 | 24.2562 | 5975.7438 | 40.6871 | 64.9433 | 1.082% | 5935.0567 | 183.3527 | 5751.704 | 11.7263 | 260.0223 | 4.334% | 4.334% | 4.275% | 0.9814% | 1.082% | 1.082% |  |  | 64.9433 | 260.0223
9588.4477 | 38353.7906 | 11 | 1600 | 6400 | 25.0032 | 6374.9968 | 46.3055 | 71.3086 | 1.114% | 6328.6914 | 185.108 | 6143.5834 | 13.3786 | 269.7952 | 4.216% | 4.216% | 4.175% | 1.038% | 1.114% | 1.114% |  |  | 71.3086 | 269.7952
10187.7256 | 40750.9025 | 12 | 1700 | 6800 | 25.7983 | 6774.2017 | 52.2864 | 78.0847 | 1.148% | 6721.9153 | 186.9739 | 6534.9414 | 15.1374 | 280.196 | 4.121% | 4.121% | 4.099% | 1.098% | 1.148% | 1.148% |  |  | 78.0847 | 280.196
10787.0036 | 43148.0144 | 13 | 1800 | 7200 | 26.6416 | 7173.3584 | 58.6297 | 85.2713 | 1.184% | 7114.7287 | 188.9502 | 6925.7786 | 17.0022 | 291.2236 | 4.045% | 4.045% | 4.043% | 1.159% | 1.184% | 1.184% |  |  | 85.2713 | 291.2236
11386.2816 | 45545.1264 | 14 | 1900 | 7600 | 27.5331 | 7572.4669 | 65.3352 | 92.8683 | 1.222% | 7507.1317 | 191.0364 | 7316.0954 | 18.9726 | 302.8772 | 3.985% | 3.985% | 4.004% | 1.222% | 1.222% | 1.222% | 0 | 0 | 92.8683 | 302.8772
11985.5596 | 47942.2383 | 15 | 2000 | 8000 | 28.4728 | 7971.5272 | 72.4028 | 100.8756 | 1.261% | 7899.1244 | 193.2322 | 7705.8922 | 21.0481 | 315.1559 | 3.939% | 3.964% | 3.979% | 1.287% | 1.261% | 1.287% | 1 | 1 | 102.9451 | 317.1385
12584.8375 | 50339.3502 | 16 | 2100 | 8400 | 29.4606 | 8370.5394 | 79.8324 | 109.293 | 1.301% | 8290.707 | 195.5373 | 8095.1697 | 23.2284 | 328.0587 | 3.905% | 3.955% | 3.967% | 1.352% | 1.301% | 1.353% | 2 | 2 | 113.6391 | 332.2222
13184.1155 | 52736.4621 | 17 | 2200 | 8800 | 30.4967 | 8769.5033 | 87.6239 | 118.1206 | 1.342% | 8681.8794 | 197.9513 | 8483.9282 | 25.513 | 341.5848 | 3.882% | 3.956% | 3.966% | 1.419% | 1.342% | 1.42% | 3 | 3 | 124.9501 | 348.1274
13783.3935 | 55133.574 | 18 | 2300 | 9200 | 31.5809 | 9168.4191 | 95.777 | 127.358 | 1.384% | 9072.642 | 200.4739 | 8872.1682 | 27.9014 | 355.7333 | 3.867% | 3.966% | 3.974% | 1.487% | 1.384% | 1.488% | 4 | 4 | 136.878 | 364.8533
14382.6715 | 57530.6859 | 19 | 2400 | 9600 | 32.7134 | 9567.2866 | 104.2918 | 137.0051 | 1.427% | 9462.9949 | 203.1047 | 9259.8902 | 30.3934 | 370.5032 | 3.859% | 3.983% | 3.99% | 1.556% | 1.427% | 1.556% | 5 | 5 | 149.4225 | 382.3988
14981.9495 | 59927.7978 | 20 | 2500 | 10000 | 33.894 | 9966.106 | 113.1679 | 147.0619 | 1.471% | 9852.9381 | 205.8433 | 9647.0947 | 32.9883 | 385.8936 | 3.859% | 4.008% | 4.014% | 1.625% | 1.471% | 1.626% | 6 | 6 | 162.5837 | 400.7632
15581.2274 | 62324.9097 | 21 | 2600 | 10400 | 35.1228 | 10364.8772 | 122.4054 | 157.5283 | 1.515% | 10242.4717 | 208.6895 | 10033.7822 | 35.6859 | 401.9037 | 3.864% | 4.038% | 4.043% | 1.695% | 1.515% | 1.696% | 7 | 7 | 176.3613 | 419.9454
16180.5054 | 64722.0217 | 22 | 2700 | 10800 | 36.3998 | 10763.6002 | 132.0041 | 168.4039 | 1.559% | 10631.5961 | 211.6429 | 10419.9532 | 38.4856 | 418.5325 | 3.875% | 4.074% | 4.079% | 1.765% | 1.559% | 1.766% | 8 | 8 | 190.7553 | 439.9447
16779.7834 | 67119.1336 | 23 | 2800 | 11200 | 37.725 | 11162.275 | 141.9639 | 179.6889 | 1.604% | 11020.3111 | 214.7031 | 10805.608 | 41.3872 | 435.7791 | 3.891% | 4.114% | 4.119% | 1.836% | 1.604% | 1.837% | 9 | 9 | 205.7654 | 460.76
17379.0614 | 69516.2455 | 24 | 2900 | 11600 | 39.0984 | 11560.9016 | 152.2845 | 191.3829 | 1.65% | 11408.6171 | 217.8698 | 11190.7473 | 44.39 | 453.6427 | 3.911% | 4.159% | 4.164% | 1.908% | 1.65% | 1.909% | 10 | 10 | 221.3916 | 482.3906
17978.3394 | 71913.3574 | 25 | 3000 | 12000 | 40.52 | 11959.48 | 162.966 | 203.486 | 1.696% | 11796.514 | 221.1426 | 11575.3714 | 47.4938 | 472.1224 | 3.934% | 4.207% | 4.213% | 1.979% | 1.696% | 1.98% | 11 | 11 | 237.6338 | 504.8354
18577.6173 | 74310.4693 | 26 | 3100 | 12400 | 41.9897 | 12358.0103 | 174.0081 | 215.9978 | 1.742% | 12184.0022 | 224.5212 | 11959.4809 | 50.6981 | 491.2172 | 3.961% | 4.259% | 4.265% | 2.052% | 1.742% | 2.052% | 12 | 12 | 254.4917 | 528.0937
19176.8953 | 76707.5812 | 27 | 3200 | 12800 | 43.5077 | 12756.4923 | 185.4108 | 228.9184 | 1.788% | 12571.0816 | 228.0053 | 12343.0763 | 54.0025 | 510.9263 | 3.992% | 4.314% | 4.321% | 2.124% | 1.788% | 2.125% | 13 | 13 | 271.9654 | 552.1645
19776.1733 | 79104.6931 | 28 | 3300 | 13200 | 45.0738 | 13154.9262 | 197.1738 | 242.2476 | 1.835% | 12957.7524 | 231.5945 | 12726.1579 | 57.4066 | 531.2487 | 4.025% | 4.372% | 4.38% | 2.197% | 1.835% | 2.197% | 14 | 14 | 290.0546 | 577.047
20375.4513 | 81501.8051 | 29 | 3400 | 13600 | 46.6881 | 13553.3119 | 209.2971 | 255.9853 | 1.882% | 13344.0147 | 235.2884 | 13108.7263 | 60.9099 | 552.1836 | 4.06% | 4.432% | 4.442% | 2.27% | 1.882% | 2.27% | 15 | 15 | 308.7592 | 602.7402
20974.7292 | 83898.917 | 30 | 3500 | 14000 | 48.3506 | 13951.6494 | 221.7806 | 270.1312 | 1.93% | 13729.8688 | 239.0868 | 13490.782 | 64.5121 | 573.7302 | 4.098% | 4.495% | 4.506% | 2.343% | 1.93% | 2.343% | 16 | 16 | 328.079 | 629.2432
21574.0072 | 86296.0289 | 31 | 3600 | 14400 | 50.0613 | 14349.9387 | 234.624 | 284.6854 | 1.977% | 14115.3146 | 242.9892 | 13872.3254 | 68.2128 | 595.8874 | 4.138% | 4.559% | 4.573% | 2.417% | 1.977% | 2.417% | 17 | 17 | 348.0141 | 656.5552
22173.2852 | 88693.1408 | 32 | 3700 | 14800 | 51.8202 | 14748.1798 | 247.8274 | 299.6476 | 2.025% | 14500.3524 | 246.9954 | 14253.357 | 72.0115 | 618.6544 | 4.18% | 4.626% | 4.642% | 2.491% | 2.025% | 2.49% | 18 | 18 | 368.5641 | 684.6753
22772.5632 | 91090.2527 | 33 | 3800 | 15200 | 53.6273 | 15146.3727 | 261.3904 | 315.0177 | 2.072% | 14884.9823 | 251.105 | 14633.8773 | 75.9077 | 642.0305 | 4.224% | 4.695% | 4.712% | 2.565% | 2.072% | 2.564% | 19 | 19 | 389.729 | 713.6026
23371.8412 | 93487.3646 | 34 | 3900 | 15600 | 55.4826 | 15544.5174 | 275.3131 | 330.7957 | 2.12% | 15269.2043 | 255.3176 | 15013.8867 | 79.9012 | 666.0145 | 4.269% | 4.765% | 4.785% | 2.639% | 2.12% | 2.638% | 20 | 20 | 411.5087 | 743.3363
23971.1191 | 95884.4765 | 35 | 4000 | 16000 | 57.386 | 15942.614 | 289.5953 | 346.9813 | 2.169% | 15653.0187 | 259.6329 | 15393.3858 | 83.9915 | 690.6058 | 4.316% | 4.837% | 4.859% | 2.713% | 2.169% | 2.712% | 21 | 21 | 433.903 | 773.8753
25019.8556 | 100079.4224 | 36 | 4175 | 16700 | 60.833 | 16639.167 | 315.4537 | 376.2867 | 2.253% | 16323.7133 | 267.4309 | 16056.2824 | 91.3813 | 735.0989 | 4.402% | 4.947% | 4.992% | 2.844% | 2.253% | 2.822% | 22 | 22 | 471.3315 | 826.1502
25619.1336 | 102476.5343 | 37 | 4275 | 17100 | 62.869 | 17037.131 | 330.7237 | 393.5927 | 2.302% | 16706.4073 | 272.027 | 16434.3803 | 95.7357 | 761.3554 | 4.452% | 5.022% | 5.071% | 2.918% | 2.302% | 2.897% | 23 | 23 | 495.3377 | 858.8254
26218.4116 | 104873.6462 | 38 | 4375 | 17500 | 64.9532 | 17435.0468 | 346.3527 | 411.3059 | 2.35% | 17088.6941 | 276.7244 | 16811.9696 | 100.1854 | 788.2158 | 4.504% | 5.099% | 5.15% | 2.993% | 2.35% | 2.971% | 24 | 24 | 519.9581 | 892.3027
26817.6895 | 107270.7581 | 39 | 4475 | 17900 | 67.0855 | 17832.9145 | 362.3406 | 429.4262 | 2.399% | 17470.5738 | 281.523 | 17189.0508 | 104.73 | 815.6792 | 4.557% | 5.176% | 5.231% | 3.068% | 2.399% | 3.046% | 25 | 25 | 545.1925 | 926.5814
27416.9675 | 109667.87 | 40 | 4575 | 18300 | 69.2661 | 18230.7339 | 378.6873 | 447.9534 | 2.448% | 17852.0466 | 286.4224 | 17565.6243 | 109.369 | 843.7448 | 4.611% | 5.255% | 5.312% | 3.143% | 2.448% | 3.12% | 26 | 26 | 571.0407 | 961.6604
28016.2455 | 112064.9819 | 41 | 4675 | 18700 | 71.4948 | 18628.5052 | 395.3925 | 466.8873 | 2.497% | 18233.1127 | 291.4222 | 17941.6905 | 114.1022 | 872.4117 | 4.665% | 5.334% | 5.395% | 3.219% | 2.497% | 3.195% | 27 | 27 | 597.5027 | 997.5391
28615.5235 | 114462.0939 | 42 | 4775 | 19100 | 73.7717 | 19026.2283 | 412.4562 | 486.2279 | 2.546% | 18613.7721 | 296.5221 | 18317.25 | 118.929 | 901.679 | 4.721% | 5.415% | 5.479% | 3.294% | 2.546% | 3.27% | 28 | 28 | 624.5783 | 1034.2164
15 min | ERCOT |  | 15 min | CNP | [12 empty] | Secondary | Primary | CNP
12450 | 49800 | AAL | 2077.5 | 8310 | 29.2342 | 8280.7658 | 78.1292 | 107.3634 | 1.292% | 8202.6366 | 195.0091 | 8007.6275 | 22.7287 | 325.1012 | 3.912% |  | 3.969% | 1.337% | At ERCOT AAL
21394.75 | 85579 | Peak | 4438.5 | 17754 | 66.3016 | 17688 | 356.4756 | 422.7773 | 2.381% | 17331.5244 | 279.7635 | 17051.7609 | 103.0637 | 805.6045 | 4.538% |  | 4.553% | 2.395% | At ERCOT Peak
| 1.7185 |  |  | 2.1365
17754.3016
AAL for CNP ( | 8280.7658 | MW) is measured at the Dist Fdr Bkr (PELCAR, Column G) so this value is increased | [6 empty] | 29.2342 | MW (Cell F50 ) for the high side of the sub trfs
Peak for CNP ( | 17688 | MW) is measured at the Dist Fdr Bkr (PELCAR, Column G) so this value is increased 60 MW (Cell F51) for the high side of the sub trfs | [12 empty] | Secondary (Adjusted) |  | Primary (Adjusted)
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % Losses above AAL are scaled proportionately.
(When ERCOT is at peak, CNP is 4.5 intervals below peak, so % losses at ERCOT peak are scaled up to match % losses at CNP peak.) | [14 empty] | ERCOT Peak | 4.54 | ERCOT Peak | 2.38
[15 empty] | CNP Peak | 4.54 | CNP Peak | 2.38
[15 empty] | Scaling for % Losses |  |  | 2024
[15 empty] | Secondary | Primary |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor |  |  | 0.57% | 0.595% |  | For Primary Distribution Customers "E"
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant |  |  |  | Primary Constants
|  | 2023 Values ----> |  | 18.835 | 1.5059e-07 | 0 | 1.1394e-06 |  |  | 170.545 | 3.636e-07 | 0 | 3.5446e-07 | <----2023 Values
|  | 2022 Values ----> |  | 18.691 | 1.7876e-07 | 0 | 1.1394e-06 |  |  | 166.812 | 3.7274e-07 | 0 | 3.5446e-07 | <----2022 Values
|  | 2021 Values ----> |  | 18.826 | 1.819e-07 | 0 | 1.1394e-06 |  |  | 164.118 | 3.8579e-07 | 0 | 3.5446e-07 | <----2021 Values |  |  | F1 = | 0.0161 | right
|  | 2020 Values ----> |  | 18.728 | 1.8618e-07 | 0 | 1.1394e-06 |  |  | 162.105 | 3.8581e-07 | 0 | 3.5446e-07 | <----2020 Values |  |  | F2 = | -0.0051 | middle
|  | 2019 Values ----> |  | 18.008 | 1.8612e-07 | 0 | 1.1394e-06 |  |  | 159.986 | 3.9124e-07 | 0 | 3.5446e-07 | <----2019 Values |  |  | F3 = | 0.002375 | left
|  | 2018 Values ----> |  | 18.569 | 1.7242e-07 | 0 | 1.1394e-06 |  |  | 156.724 | 4.0053e-07 | 0 | 3.5446e-07 | <----2018 Values
|  | 2017 Values ----> |  | 18.268 | 1.7762e-07 | 0 | 1.1394e-06 |  |  | 152.212 | 4.0973e-07 | 0 | 3.5446e-07 | <--- 2017 Values
|  | 2016 Values ----> |  | 20.6354 | 1.8059e-07 | 0 | 1.1394e-06 |  |  | 149.175 | 4.2041e-07 | 0 | 3.5446e-07 | <--- 2016 Values |  |  |  | Secondary Constants
|  | 2015 Values ----> |  | 20.867 | 1.7797e-07 | 0 | 1.1394e-06 |  |  | 145.39 | 4.3561e-07 | 0 | 3.5446e-07 | <--- 2015 Values
|  | 2014 Values ----> |  | 19.863 | 1.893e-07 | 0 | 1.1394e-06 |  |  | 142.346 | 4.4856e-07 | 0 | 3.5446e-07 | <--- 2014 Values
|  | 2013 Values ----> |  | 19.473 | 1.9548e-07 | 0 | 1.1394e-06 |  |  | 137.751 | 4.7391e-07 | 0 | 3.5446e-07 | <--- 2013 Values |  |  | F1 = | 0.022 | right
|  | 2012 Values ----> |  | 21.1118 | 1.8286e-07 | 0 | 1.1394e-06 |  |  | 133.986 | 5.0407e-07 | 0 | 3.5446e-07 | <--- 2012 Values |  |  | F2 = | -0.00615 | middle
|  | 2009 Values ----> |  | 20.312 | 1.9194e-07 | 0 | 1.1394e-06 |  |  | 130.794 | 5.041e-07 | 0 | 3.5446e-07 | <--- 2009 Values |  |  | F3 = | 0.02384 | left
|  | 2008 Values ----> |  | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values
|  | 2007 Values ----> |  | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | <--- 1995 |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2001 |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2004/2006 |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Start Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Start Value
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review.
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 10,740 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
(See graphs below)
Primary Constants
F1 = | 0.0161 | right
F2 = | -0.0051 | middle
F3 = | 0.002375 | left
Secondary Constants
F1 = | 0.022 | right
F2 = | -0.00615 | middle
F3 = | 0.02384 | left
Calculated Losses as per ERCOT Protocol
DLF = F1*(SIEL/AAL) + F2 + F3/(SIEL/AAL)
F1 = .016100
F2 = -.005100
F3 = .002375
Calculated Losses as per ERCOT Protocol
DLF = F1*(SIEL/AAL) + F2 + F3/(SIEL/AAL)
F1 = .022000
F2 = -.006150
F3 = .023840
ERCOT AAL (15 mins) = 12,450
ERCOT AAL (15 mins) = 12,450
ERCOT Peak (15 mins) = 21,394
ERCOT Peak (15 mins) = 21,394

## 3) Loss Equations
System Loss Equations For CenterPoint Energy
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
Calculations/Formulas
83.426 | = | A * (TRF name plate*TRF name plate) + (No load losses+1%)
| A = | 1.5059e-07
| B = | 18.835
Variables
| 2023 | for use in | 2024
Total No Load Losses for Substation Transformers +1% [MW]: |  |  |  | 18.835
Total Load Losses at Trf base name plate rating +1% [MW]: |  |  |  | 64.591
Total Losses [MW]: |  |  |  | 83.426
Trf base name plate rating [MVA]: |  |  |  | 20710.4
Distribution Transformers
Calculations/Formulas
279.745 | = | A * (Distribution Input*Distribution Input) + No load losses
| A = | 3.6356e-07
| B = | 170.545
Variables
| 2023 | for use in | 2024
Total No-Load Loss Average For Distribution Transformer[MW]: |  |  |  | 170.545
Total Load Losses at input to Distribution Transformers [MW]: |  |  |  | 109.2
Total Losses [MW]: |  |  |  | 279.745
Distribution Input [MW]: |  |  |  | 17331
Conductors
Primary Conductor
| A = | 1.1394e-06
| B = | 0
Secondary Conductor
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified